Kentucky Transportation Cabinet

# Spill Prevention Control and Countermeasures Plan Template

112.1	Applicability and General Requirements

The Kentucky Transportation Cabinet (KTC) owns numerous facilities around the State.  The ______(District name and number)____, is located at __________(address)_________ in _______(city)________, Kentucky, _(zip code)__.  The site consists of  _______-acres.  Ongoing activities at this facility include _______________________________________(describe what activities take place at this location, i.e. vehicle maintenance, sign shop, etc.)            ___________.

Because the facility has aboveground storage capacity in excess of 1,320 gallons of petroleum products, it is subject to the requirements of 40 CFR Part 112, which mandates the preparation and implementation of a Spill Prevention, Control, and Countermeasure (SPCC) Plan.  The purpose of the SPCC Plan is to establish procedures, methods, and equipment to prevent and/or mitigate the discharge of oil from non-transportation-related onshore and offshore facilities into or upon the navigable waters of the United States.  This plan has been prepared in accordance with sound engineering practices.  A copy of the regulation is in Appendix 1.

112.3	Implementation

(A facility in operation on or before August 16, 2002 must implement this Plan as soon as possible, but not later than August 18, 2002.  KTC should select a date for implementation of all measures included in the Plan.)

112.5	Amendment of SPCC PLAN

The SPCC plan must be amended when there is a change in facility design, construction, operation, or maintenance that materially affects the potential for a discharge as described in 40 CFR Part 112(b).  Examples of changes that may require amendment of the plan include but are not limited to:  commissioning or decommissioning containers; replacement, reconstruction or movement of containers; reconstruction, replacement, or installation of piping systems; construction or demolition that might alter secondary containment structures; changes of product or service; or revision of standard operation or maintenance procedures at a facility.  Amendments must be made within six months and implementation as soon as possible but no later than six months following the preparation of the amendment.

A complete review and evaluation of the SPCC plan must be performed at least once every five years from the date of the last review.  As a result of the review, the District will amend the plan within six months of the review to include more effective prevention and control technology if the technology has been field proven at the time of the review and will significantly reduce the likelihood of a discharge as described in 40 CFR Part 112(b).  The District will document the review and evaluation, and sign a statement as to whether the District will amend the plan.  Appendix 2 contains the statement to be signed after the five-year review.

112.7(a)(3)	Facility Characteristics / Description of Facility

(Describe the physical layout of the property, and include a facility diagram. Figure 1 can be the facility diagram.  It can be hand drawn or CADD, doesn’t matter.  The diagram must show the location and contents of each container subject to the regulation.  Can refer to a Table as referenced in the next section listing the products.  Show underground storage tanks also. Containers subject to the regulation include mobile and stationary petroleum containers of 55-gallons and greater in size.  For mobile containers, if they are stored in a certain area, mark that area on the diagram.)

112.7(a)(3)(i)	Above Ground Storage Tanks

(A list of the storage capacity of the container, type of oil in each container, and secondary containment for each container.  Can include the capacity of the secondary containment.  This can be in a narrative form or a Table.  An example Table 1 is attached.)

112.7(a)(3)(ii)	Discharge Prevention Measures

(Encompasses secondary containment and other discharge prevention measures.  Include procedures for routine handling of products, such as loading and unloading, VCR’s, etc.)

Example language:

As described above, the aboveground storage tanks, drums and containers that are located in the building all have secondary containment, capable of containing 100% of the tank contents.  Additionally, all tanks and drums are located in a corner of the building where no vehicle traffic takes place.  There are no forklifts or tow motors currently in use within the building. Spill kits are present in the drum storage and handling areas, and in the event of a major spill, shall be used to contain and recover spilled materials.

Additionally, the stationary tanks located outside have secondary containment equal to 110% of the tank contents.

Monthly inspections will check the condition of the tanks, valves, and piping of each tank (include overhead pipes if any), along with the drainpipes.

Loading and unloading procedures have also been developed to prevent discharges from the transfer of petroleum products and are found in 112.7(h).

Mobile containers are usually parked ___(describe location)______ where there is (describe secondary containment or drainage, etc)_________________ to contain a spill from the vehicles.

112.7(a)(3)(iii)	Discharge Controls

(Means spill controls and secondary containment.  Describe secondary containment or drainage controls around the containers, and other structures, equipment, and procedures for the control of a discharge.  Can also refer to Table 1 for information about secondary containment structures.)

Some example language to include: Procedures to control a discharge include shutting off the power supply to the tank, turning off any valves to the tank, and using booms or socks to contain the material.

112.7(a)(3)(iv)	Countermeasures for Discovery,

Notification, Response, and Cleanup

(The facility’s and contractor’s capabilities for discharge discovery, response and cleanup.  Includes personnel, equipment, and contractor.)

Example language:

District employees will be the first responders to all oil spills at the facility.  Upon discovery of a discharge of oil the first step will be to stop the flow through closing of valves, turning off power, or using sorbent materials for the containment of the spill.  Contacting other employees for assistance is also important.  In all instances the District Operations Manager (this is the main person you want notified) should be notified.

The following is an inventory of spill response equipment, which is kept on site in the event of a spill or leak of petroleum products.  (List materials on site such as oil dry, booms, socks, pads, spill kits, shovels, brooms, etc.).  Spill cleanup equipment is located (where? in which buildings? and near what equipment?).

112.7(a)(3)(v)	Disposal of Recovered Material

(Methods of disposal, may include recycling)

All spill material and debris will be managed in a manner that fully complies with applicable local, state, and federal laws regarding recycling or disposal of wastes.

112.7(a)(3)(vi)	Contact List

(Who to contact in the event of a spill inside and outside KTC.  Usually the same as contact list required per OSHA’s emergency response plans with the addition of ERT, EPA, and a cleanup contractor. A table works well so it can be posted by all phones.  An example is attached in Table 2.   If a cleanup contractor is listed it should be one the facility has an agreement with for response that ensures availability of personnel and equipment within appropriate response times.  Formal written agreements are not needed, but if one exists it must be addressed in the plan.)

Example language: A contact list for appropriate District personnel, contractors and government agencies is in Table 2.  In the event of a spill or discharge as described in 112. 1(b), i.e. discharge oil in any quantity that may be harmful, or a gasoline or diesel fuel spill per the state of Kentucky regulations, the appropriate persons and agencies on the contact list shall be called.

112.7(a)(4)	Spill Reporting Information

(Provide information and procedures for a person reporting a discharge to relate appropriate information.  The example language below includes all required information.  A form is a good way to make sure all data is gathered.  An example form is in Table 3, attached.  The information below also includes when written reports are required.)

Example language:

To assist in the reporting of a discharge described in 112.1(b), the appropriated information shall be collected and recorded on the Spill Notification Data Sheet in Table 3.  The information to be collected and written on the form should accurately describe the discharge occurrence.  The District Manager or designee should fill out this form.  Information to be recorded includes the exact address or location and phone number of the facility; the date and time of the discharge; the type of material discharged; estimates of the total quantity discharged; estimates of the quantity discharged as described in 112.1(b); the source of the discharge; a description of all affected media; the cause of the discharge; any damages or injuries caused by the discharge; actions being used to stop, remove, and mitigate the effects of the discharge; whether an evacuation may be needed; and the names of individuals and/or organizations who have also been contacted.

Whenever the facility has discharged more than 1000 gallons of oil in a single discharge as described in 112.1(b), or discharged more than 42 gallons of oil in each of two discharges occurring within any twelve month period the following information must be sent to EPA Region 4 within 60 days:

- Name of the facility;

- Name(s) of the owner or operator of the facility;

- Location of the facility;

- Maximum storage or handling capacity of the facility and normal daily throughput;

- The corrective actions and/or countermeasures taken, including an adequate description of equipment repairs and/or replacements;

- An adequate description of the facility, including maps, flow diagrams, and topographical maps;

- The cause of such discharge as described in 112.1(b), including a failure analysis of system or subsystem in which the failure occurred;

- Additional preventive measures Rumpke has taken or contemplated to minimize the possibility of recurrence;

Such other information as the Regional Administrator may reasonably require pertinent to the Plan or discharge.

A copy of the report will also be sent to the KDEP, Division of Water, 14 Reilly Road, Frankfort, Kentucky  40601.

112.7(a)(5)	Emergency Procedures

(Procedures to be used when a discharge occurs.  KTC may already have emergency response procedures to use here.)

Example language:

In the event of a release of release of oil at the facility the District Manager shall be notified immediately and the following steps shall be taken:

I.	Assessment of Hazard

- Upon notification of a petroleum-related spill, the first responder will determine the hazard potential of a spill response by determining at least the following factors:

- The substance spilled and its hazard potential

- The amount of the spill and the extent of spreading

- The source of the leakage/spill

- If a spill is determined to be of such a magnitude that it cannot be safely and effectively controlled by facility personnel, then the District Manager shall promptly notify outside emergency response agencies to implement control and cleanup.

II.	Securing Spill Response Equipment

- Upon determining the hazard potential for the planned response action, the District Manager shall direct those who will respond to the spill to obtain the appropriate response equipment and personal protective equipment.  A list of the spill response and personal protective equipment for this facility is provided in Section 112.7(a)(3)(iv).

III.	Containment and Elimination of Spill Source

- Upon obtaining the proper spill response tools and PPE, the spill responder(s) shall first attempt to contain the spill so as to prevent its entry into a storm sewer, a ditch, or any conveyance that eventually discharges to the waters of the United States.

- At the same time as containment is being performed or as soon as possible after the containment, the spill responder(s) shall attempt to seal or otherwise stop the source of the spill.  Common methods of eliminating a spill source include closing valves, leak stopping compound for pinhole leaks, drum overpacks, deactivating pumps, and diverting flow to another pathway as long as this pathway does not allow the spill to enter a navigable water course.

IV.	Spill Cleanup

- Once the spill is contained and the source eliminated, the spill responder(s) shall collect the spilled material by the appropriate manner and place the material into secure containers.

- The area or surface in contact with the spilled material shall be decontaminated by an appropriate method that is permissible under local, state, and federal laws.  The specific method used will depend upon the substance; the availability of permitted sewer discharge to a POTW, regulatory standards applicable to hazardous and toxic wastes, and other factors.  The responder will select the appropriate decontamination method after determining the applicable facts and by conferring either with the regulators or an expert in the subject of spill response.

- All spill material and debris will be managed in a manner that fully complies with applicable local, state, and federal laws regarding recycling or disposal of wastes.  The preferred method is to recycle or reclaim materials from spills in an effort to minimize waste generation.  Where this is not feasible or allowed, then disposal will be carried out in accordance with applicable local, state, or federal rules.

112.7(b)	Fault Analysis

(This is information concerning the potential consequences of equipment failure.  The plan must only discuss potential failure situations that might result in a discharge, not any failure situation.  Where experience dictates a reasonable potential for equipment failure, i.e. loading or unloading, tank overflow, rupture, leakage, include a prediction of the direction, rate of flow, and total quantity of oil which could be discharged from the facility as a result of each type of major equipment failure.  Experience means experience from the facility or the industry in general.  Address a major equipment failure, one that could cause a discharge as described in 112.1(b) not minor possibilities.  Spill pathways depends on the geographic characteristics of the facility and possibility for discharge.  Focus on the obvious.  Can refer to facility diagram for flow directions.)

112.7(c(	Containment

(Provide appropriate containment or diversionary structures or equipment to prevent a discharge as described in 112(b).  Must be capable of containing oil, and constructed so the any discharge will not escape the containment system before cleanup occurs.  At a minimum, must use one of the following dikes, berms, retaining walls, curbing, culverting, gutters or other drainage systems, weirs, booms or other barriers, spill diversion ponds, retention ponds or sorbent materials.  If dikes, berms, retaining walls, or anything earthen is used it must be sufficiently impervious to prevent a discharge before cleanup occurs.  The same is true for container floors or bottoms.  Liners are not required.  The plan must address how the secondary containment is designed to meet the requirements.  A description of how earthen structures were made sufficiently impervious is required such as removing vegetation, type of material used, repairing excavations

If you determine based on space or geographic constraints, not financial, that secondary containment is not practicable, you must complete the next section.  If you can provide secondary containment then skip the next section.)

112.7(d)	Contingency Planning

(This section requires the preparation of an Oil Spill Contingency Plan if the requirements of section 112.7(c(, 112.7(h)(1), 112.8(c((2), or 112.8(c((11) cannot be met.  If you determine it is not practicable to comply with the above list, you must clearly explain why the measure is not practicable, and conduct both periodic integrity testing of the containers and periodic integrity and leak testing of the valves and piping, and unless you have filed a response plan per 112.20, provide in your plan an oil spill contingency plan per 40 CFR Part 109 and a written commitment of manpower, equipment, and materials to expeditiously control and remove any quantity of oil discharged that may be harmful.)

112.7(e)	Inspections, Tests and Records

(Develop inspection procedures, perform inspections. Keep records of inspections and tests for three years.  Inspection form must be signed.  Records of tests and inspections can be kept under usual and customary business practices will suffice.  Inspections and tests mean schedules, evaluations, examinations, descriptions, inspections, and tests. Records can be kept electronically.)

Example language:

At least once a month an inspection will be made to thoroughly inspect all storage tanks, drums, mobile containers, piping, and containment areas.  An inspection form is provided in Appendix 3.  If any discrepancies are noted, corrective actions will be taken immediately.  Inspection records will be maintained for a minimum of three years.

The District has developed recordkeeping and internal reporting procedures to document the effective implementation of this SPCC Plan.  These include procedures for recording and maintaining records of inspections, maintenance activities, employee training, and spills and leaks that have the potential to reach navigable waters.

Reports of spills and leaks that have the potential to reach navigable waters will be maintained with the facility records.  Documents to be kept include the Spill Notification Data Sheet (Table 3) as well as a follow-up report describing the incident in detail, the effect on storm water quality, spill response actions taken, and recommended revisions to the plan to prevent a recurrence of the incident.

112.7(f)	Personnel Training and Discharge Prevention Procedures

(This section addresses the minimum training requirements.  The example language addresses all aspects of the rule in a generic format.)

Example language:

Training in discharge prevention is required of all oil handling personnel.  Oil handling personnel include anyone who is involved in the use of and loading and unloading of oil products.  At a minimum oil handling personnel shall be trained in the operation and maintenance of equipment to prevent oil discharges, discharge procedures protocols, applicable pollution control laws, rules and regulations, general facility operations, and the contents of the facility SPCC plan.  New employees shall be trained if their job involved possible handling of oil.  Any employee involved in the transfer of oil will be trained in loading and unloading procedures, response and cleanup, and notification procedures.

A person will be designated at each facility who is accountable for discharge prevention and who reports to facility/Cabinet management.

At least once a year the District will conduct discharge prevention briefings, or training sessions, to assure adequate understanding of the SPCC Plan.  The annual briefing must also include known discharges or failures, malfunctions, and any recently developed precautionary measures. Training records will be retained for a minimum of three years.

112.7(g)	Security

(The requirements of this section are options provided equivalent environmental protection by some other means of spill prevention, control or countermeasure.  You must state reason for nonconformance and describe in detail alternate methods and how you achieve equivalent environmental protection.  Requirement of this section include fencing, locking master control valve, locking starter controls on each oil pump in off position when not operating or standby, cap or blank flange the loading/unloading connections, and provide facility lighting.

Fences should be designed to deter vandalism.

Master flow and drain valves and any other valve permitting outward flow from the container have adequate security measures.  Manual locks, electronic or automatic locks, or whatever technology allows may be used.

Lock starter control or the building it’s located in.

Secure or blank flange loading/unloading connections, quick disconnect fittings can be used.  A secure cap is one that can be locked or some other method to deter vandalism.

List where keys are stored and who has keys.)

112.7(h)	Tank Truck Loading / Unloading

((1) This applies to loading or unloading of oil from a tank truck or tank car.  Secondary containment can be provided by dikes, berms, retaining walls, curbing, culverting, gutters, drainage systems, weirs, booms, other barriers, spill diversion ponds, retention ponds, or sorbent materials.  Must provide containment where loading/unloading area does not flow to catch basin or treatment facility. Design containment system to hold maximum capacity of any single compartment of the tank truck.

(2) Some kind of alarm or warning can be provided by interlocked warning light or physical barrier system, warning signs, wheel chocks, vehicle break interlock system to prevent vehicle from departing until complete disconnection is made.  This is an option but equivalent environmental protection must be provided.

(3) An inspection of lowermost drains and outlets of delivery trucks prior to filling or departure to prevent a discharge while in transit must be done.  Cannot just pass on to vendor, owner’s responsibility.  This is an option and can provide equivalent environmental protection.

You must state reasons for nonconformance (2) and (3) and describe in detail alternate methods and how you achieve equivalent environmental protection.)

Example of alternate procedures for (2) and (3): Can post them, give to vendors to sign, have employees check each delivery. Vehicle fueling and tank truck unloading has the potential for spills.  The following practices are suggested to reduce the potential for a spill:

- Make sure all vehicles are properly braked prior to fueling or unloading

- Keep the tanker trucker truck within the unloading containment zone during unloading of fuel or oil products

- Inspect all connections between the offloading truck and the tanks for leaks and tightness prior to unloading and prior to departure.

- Ascertain product level in tank prior to filling.  Fueling or unloading should be constantly monitored.  The tank should not be left unattended during any portion of the process.

- Drain the delivery hose of product prior to disconnection from the AST.

- Make sure all valves are closed.

- Upon fuel delivery, the tank installation and the area around the tank will be inspected for signs of product leakage and/or release.

- The driver must inspect his vehicle while still on the site for any discharges.  Prevent liquid discharge in transit by inspecting lowermost drains, connections, hoses etc.

112.7(i)	Brittle Fracture

(Evaluate “field constructed” tanks whenever tanks undergoes repairs, alterations, reconstruction, or change in service that might affect the risk of a discharge or failure due to brittle fracture or other catastrophe. Evaluate the container for risk of discharge and take appropriate action if necessary.  “Field constructed,” means a container that is assembled or reassembled outside the factory at the location of its intended use. “Catastrophic failures” are failures that result from events such as lighting strikes, dangerous seismic activity, etc.  “Repair” means any work to maintain or restore the container to a condition suitable for safe operation.  Repair includes the removal and replacement of material, re-leveling or jacking, repair of flaws, etc.   “Alteration” involves cutting, burning, welding, or heating operations that change changes the physical dimensions or configuration of the container.

The requirement of this section is an option provided equivalent environmental protection by some other means of spill prevention, control or countermeasure.  You must state reason for nonconformance and describe in detail alternate methods and how you achieve equivalent environmental protection.  Does the District have field constructed tanks?)

112.7(j)	Conformance with State Rules

(Include in the plan a complete discussion of conformance with applicable requirements of discharge prevention and containment procedures listed in this part or any more stringent State rules, regulations, and guidelines.)

Example language:

Kentucky environmental law, KRS 224.01-400(11), provides that any petroleum or petroleum product release, except diesel fuel, in excess of 25 gallons over a 24-hour period, must be reported.  The reportable quantity for diesel fuel is 75 gallons over a 24-hour period.  However any release that causes a visible sheen, or that violates any provision of Section 311 of the Clean Water Act must be reported.

Any release falling within the above categories should be reported immediately to the Environmental Response Team (ERT) of the Kentucky Natural Resources Cabinet.  The ERT phone number is listed on the Contact List in Table 2 and will be posted throughout the facility.  A written follow up report may be required by the Cabinet, and must be submitted within seven days of the Cabinet’s demand.  The report must contain the following information: precise location of the release; name, address, and phone number of person in charge at the time of the release, name and address of persons having knowledge of facts surrounding the release; the concentration and quantity of the release; circumstances and causes of the release; efforts taken to control and mitigate the release; any harmful effects of the release; transportation characteristics of the medium or matrix into which the material was released; current or proposed corrective action; and any other information that my assist in the response at the site.

112.8	Specific Requirements for Onshore Facilities

(Onshore facilities must also meet these specific discharge prevention and containment procedures.   Your plan may deviate from the requirements of this section except 112.8(c((2) and 112.8(c((11), if you provide equivalent environmental protection by some other means of spill prevention, control or countermeasure.  You must state reason for nonconformance and describe in detail alternate methods and how you achieve equivalent environmental protection.)

112.8 (b)(1)	Facility Drainage / Diked Storage Area Drainage

(The rule prescribes requirements for drainage from diked areas; it does not mandate the use of diked areas.  If you use diked areas the rule prescribes minimum requirements for drainage of those facilities.  You have to restrain the drainage from diked areas by valves to prevent a discharge into the drainage system or effluent treatment system not designed to control such discharge.  Can use pumps or ejectors, but must be manually activated and must inspect the accumulation of water to ensure no oil will be discharged.)

112.8 (b)(2)	Diked Storage Areas – Valves Used; Inspection of Retained Stormwater

(Can only use valves of manual, open and closed design for the drainage of diked areas, no flapper type valves.  If facility drains to watercourse you must inspect and may drain uncontaminated retained stormwater as provided in (c((3)(ii), (iii), and (iv) of this section)

112.8 (b)(3)	Drainage from Undiked Areas; Areas Subject to Flooding

(Design facility drainage systems from undiked areas with a potential for a discharge to flow into ponds, lagoons, or catchment basins designed to retain oil or return it to the facility.  The rules recommend, not require, that ponds, lagoons, catchment basins, or other facility drainage systems with a potential to discharge not be located in areas subject to periodic flooding.)

112.8 (b)(4)	Diversion Systems

(If a facility drainage is not engineered as in (b)(3), equip the final discharge of all ditches inside the facility with a diversion system that would retain the oil in the facility in the event of an uncontrolled discharge.  The rule applies only to drainage from petroleum areas of the facility.  This rule aims to retain within the facility minimal amounts of contaminated water in undiked areas subject to periodic flooding.  A diversion system is to retain water.)

112.8 (b)(5)	Natural Hydraulic Flow, Pumps

(Where drainage waters are treated in more than one treatment unit and such treatment is continuous, and pump transfer is required, provide two “lift” pumps and permanently install one of the pumps.  You must engineer drainage systems to prevent a discharge in case there is an equipment failure or human error at the facility.)

112.8 (c(    Bulk Storage Containers

((1) Container material must be compatible with the oil stored in it and the conditions of storage of such as pressure and temperature.

(2) Construct all bulk storage containers so you provide a secondary means of containment designed to hold the entire contents of the largest single tank or container, and to allow sufficient freeboard for precipitation.  Dikes, containment curbs, and pits are used for this purpose.  Diked areas must be sufficiently impervious to contain the discharged oil.  If a pit is used as a form of secondary containment, take measures to mitigate the effects of the pit on birds and wildlife, such as netting, fencing, or other means to keep wildlife away.  Also, since a pit can discharge over the top or seep through the ground, don’t use pits where a pit may be a source of discharge.  Show freeboard calculations in plan.  May also use a drainage trench enclosure that terminates in a catchment basin or holding pond.

(3) Drainage of rainwater. Do not allow drainage of uncontaminated rainwater from the diked area into a storm drain or discharge of an effluent into an open watercourse, lake or pond, bypassing the treatment system unless you (i) normally keep bypass valve sealed closed, (ii) inspect retained rainwater to ensure that its presence will not cause a discharge as described in 112.1(b), (iii) open the bypass valve and reseal it following drainage under responsible supervision, and (iv) keep adequate records of such events, for example any records required of any storm water permits.  KPDES records can show compliance with this rule.

(4) Protect completely buried metal tanks installed on or after Jan. 10, 1974 from corrosion by coatings or cathodic protection, and regularly leak test such tanks.

(5) Do not use partially buried or bunkered metal tanks unless you protect them from corrosion by coatings or cathodic protection, and regularly leak test such tanks.

(6) Test each AST for integrity on a regular schedule and whenever material repairs are made.  The frequency and type of testing takes into account the container size and design (floating roof, skid mounted, elevated, or partially buried).   In addition to monthly visual inspections one of the following methods of integrity testing will be employed: hydrostatic testing, radiographic testing, ultrasonic testing, acoustic emissions testing, or another form of nondestructive shell testing.  Inspections will be in accordance with industry standards.  “Industry standards” includes a wide variety of organizations that have standards for inspecting welds and metal thickness.  Examples are API Standard 653 “Tank Inspection, Repair, Alteration and Reconstruction”, API Recommended Practice 575 “Inspection of Atmospheric and Low-Pressure Tanks” or Steel Tank Institute Standard SP001-00 “Standard for Inspection of In-Service, Shop Fabricated  Aboveground Tanks for Storage of Combustible and Flammable Liquids.”  Inspect the containers' foundation and supports.  Frequently inspect the outside of the container for sign of deterioration, discharges, or accumulation of oil inside diked areas.  Maintain records of inspections and tests.  Tanks which touch the ground must be evaluated for integrity.  Small shop built containers in which internal corrosion poses minimal risk of failure, where all sides are visible, and that don’t touch the ground, can get by with the monthly visual.

(7) Control leakage through defective heating coils by monitoring the steam return and exhaust lines for contamination from internal heating coils that discharge to open watercourse, or pass through settling tank, skimmer, or other separation and retention system.

(8) Engineer or update each container installation to avoid discharges.  Provide at least one of the following:  (i) high liquid level alarms with audible or visual signal, (ii) high liquid level pump cutoff device to stop flow at a predetermined container level, (iii) communication between container gauges and pumping station, (iv) fast response system for determining the liquid level of each container such as digital computers, telepulse, or direct vision gauges (if use this a person must be present to monitor overall filling of bulk storage container), (v) must test liquid level sensing devises to ensure proper operation.

(9) Observe effluent treatment facilities frequently enough to detect possible system upsets that could cause a discharge.

(10) Clean up of visible oil leaks. Promptly clean up any visible leak or spills found and promptly correct visible discharges that result in loss of oil including seams, gaskets, piping, pumps, valves, rivets, and bolts. Oil will promptly be removed from diked areas.

(11) Position or locate mobile or portable oil storage containers to prevent a discharge.  Provide a secondary means of containment such as dike or catchment basin to contain largest single tank plus freeboard to contain precipitation.)

112.8(d)	Facility Transfer Operations, Pumping, and Facility Processes

((1) Provide buried piping that is installed after Aug. 16, 2002 with a protective wrapping and coating.  Must also provide cathodic protection or otherwise meet requirements of Part 280 of State program.  If part of buried pipe becomes exposed for any reason you must inspection for deterioration.  If damage found undertake additional examination and corrective action as required.

(2) Cap or blank flange terminal connections when such piping is not in service or in standby for an extended period of time.

(3) Design pipe supports to minimize abrasion and corrosion and allow for expansion and contraction.

(4) Regularly inspect all aboveground valves, piping, and appurtenances.  Assess the general condition of such items such as flange joints, valve glands and bodies, expansion joints, catch pans, pipeline supports, locking of valves and metal surfaces. Conduct integrity and leak testing of buried piping at time of installation, modification, construction, relocation or replacement.

(5) Warn all vehicles of the overhead piping to be sure no vehicle will endanger the piping.)

## TABLE 1 – PETROLEUM MATERIALS LIST FOR DISTRICT 5, LOT NO. 497, SHELBY COUNTY *

| Type of Oil | Location | Quantity (gal) | Type of Container | Secondary Containment (1) | Capacity (5) |
| --- | --- | --- | --- | --- | --- |
| Diesel Fuel | mobile (3) | 90 | steel | none | N/A |
| Gasoline |  |  |  |  |  |
| Used Oil |  | 300 |  | none |  |
| Motor Oil |  |  |  |  |  |
| Hydraulic Oil | shop | 55 | steel drum | none | N/A |
| Machine Grease |  | 120 # (4) |  |  |  |
| Oil Distributor | mobile | 1350 |  | none | N/A |
| Tack Oil (2) | behind shop | ? |  | concrete | ? |
| Trucks | mobile | ? | steel | none | N/A |

* based on meeting with Shelby Jett and Carl Henry

(1)	Secondary containment is required.

(2)	Tack oil container is empty with the electricity cut off.  Still remains in calculations until demonstration made that the tank is abandoned and won't be used again.

(3)	For mobile tanks list what piece of equipment it is.

(4)	What size gallon container is this?

(5)	Convert feet or inches to gallons.

TABLE 2 – EMERGENCY CONTACTS LIST

| District No. |  |
| --- | --- |
| District Name |  |

| Facility Personnel |  |  |  |
| --- | --- | --- | --- |
| District Engineer |  | Office Mobile |  |
| Operations Manager |  | Office Mobile |  |
| Environmental Analysis |
|  |  | Office |  |
|  |  | Office Mobile Pager |  |
| Spill Response Contractors |  |  |  |
|  |  | Office Emergency No. |  |
| Agency Personnel |  |  |  |
| Fire Department |  | Emergency Non-emergency | 911 |
| County Local Emergency Planning Committee (LEPC) |  | Day 24-hr |  |
| Kentucky Emergency Response Team |  | 24-hr Emergency Spill Hotline | (800) 928-2380 |
| National Response Center |  | 24-hr Hotline | (800) 424-8802 |

table 3 - spill notification data sheet

| LOCATION | FACILITY NAME AND NUMBER | DATE | TIME AM PM |
| --- | --- | --- | --- |
|  | LOCATION ADDRESS | COUNTY |
|  | CITY/STATE/ZIP CODE | TELEPHONE |
| INCIDENT TYPE |  |
|  | DATE AND TME OF INCIDENT |
|  | TYPE OF MATERIAL DISCHARGED |
|  | ESTIMATED QUANTITY OF DISCHARGED MATERIAL |
|  | SOURCE OF DISCHARGE |
|  | DESCRIPTION OF AFFECTED MEDIA |
|  | CAUSE OF THE DISCHARGE |
|  | ANY DAMAGE OR INJURY |
|  | ACTIONS USED TO STOP OR REMOVE AND MITIGATE EFFECTS OF THE DISCHARGE |
|  | EVACUATION NECESSARY |
|  | ( AREA SUPERVISOR DATE NOTIFIED TIME | ( DIST. MGR DATE NOTIFIED TIME | ( REG MGR. DATE NOTIFIED TIME |
|  | ( ENVIRON. MGR. DATE NOTIFIED TIME | NAME OF INDIVIDUAL TAKING REPORT DATE TIME |
| Local Fire Dept. Notified | NAME OF FIRE DEPT. | NAME OF INDIVIDUAL TAKING REPORT | Rept.# | Date | Time |
| GOVT. AGENCIES NOTIFIED (if applicable) | National Response Center (1-800-424-8802) | NAME OF INDIVIDUAL TAKING REPORT | Rept # | Date | Time |
|  | STATE ERT (1-800-928-2380) | NAME OF INDIVIDUAL TAKING REPORT | Rept # | Date | Time |
|  | Other – State / County, Etc. | NAME OF INDIVIDUAL TAKING REPORT | Rept # | Date | Time |
| Incident Description, Action Taken, General Comments |  |
| Prepared by |  | TITLE | DATE |  |

# APPENDIX 1

# COPY OF REGULATION 40 CFR Part 112

# APPENDIX 2

# STATEMENT FOR PLAN AMENDMENT

This statement is to be signed and kept with the SPCC Plan after the five-year review and evaluation of the Plan.

“I have completed a review and evaluation of the SPCC Plan for the _______(District name)              on _______(date)            and will / will not amend the Plan as a result.”

Signature

Print Name

Title

# APPENDIX 3

# Site Inspection Form

| Date/Time: |  |  |  |
| --- | --- | --- | --- |
| Inspector: |  |  |  |
| Weather Conditions |  |  |  |
| Inspection Items | Yes | No | Comments |
| 1. Are there any leaks or spills around any tank or drums? |  |  |  |
| 2. Leaks at valves, piping, or terminal connections? |  |  |  |
| 3. Is there any floor dry remaining from a clean up? |  |  |  |
| 4. Are there any leaks or spills around the oil/water separator? |  |  |  |
| 5. Vehicle inspections being performed? |  |  |  |
| 6. Any leaks or spills from the overhead piping, hoses, or guns? |  |  |  |
| 7. Is there discoloration, residue or other stains on the ground around the facility? |  |  |  |
| 8. Water in diked areas or secondary containment? |  |  |  |
| 9. Valves to drains from secondary containment locked? |  |  |  |
| 10. Training of employees performed annually or when new? |  |  |  |
| 11. Water in secondary containment have a sheen? |  |  |  |
| If so, water cannot be discharged. |  |  |  |
| 12. Integrity tests required? |  |  |  |
| 13. Any alterations or change in uses of petroleum tanks? |  |  |  |
| If so, plan must be revised. |  |  |  |
| 14. Has it been five years since the plan was reviewed / revised? |  |  |  |
| Additional Comments: |  |  |  |
| Is any action necessary to maintain compliance? _______ No _______ Yes |  |  |  |
| Explain action: |  |  |  |  |

# Certification

This is to certify in accordance with 40 CFR Part 112.3(d) that I am a licensed Professional Engineer and I have reviewed the Spill Prevention, Control, and Countermeasure (SPCC) Plan for _____(District Name)__________________________ and certify the Plan to be effective to satisfy the requirements of 40 CFR part 112.  By means of this certification, I attest:

That I am familiar with the requirements of 40 CFR Part 112,

That I, or my agent, has visited and examined the facility,

That the Plan has been prepared in accordance with good engineering practice, including consideration of applicable industry standards, and with the requirements of 40 CFR part 112,

That procedures for required inspections and testing have been established, and

That the Plan is adequate for the facility.

This certification in no way relieves the owner or operator of a facility of his duty to prepare and fully implement the Plan in accordance with the requirements of this Part.

Certification:

Registration No.

Date: