## Slide 1
Sympson Lake
Dam
TO BOSTON
TO LEXINGTON
TO I65
BARDSTOWN WTP
US62 OVER SYMPSON LAKE: FROM RISK TO REPAIR
Presenters
  Aaron Wallace, P.E – KYTC Geotechnical Branch
  Bryan Robbins, P.E. – HDR
  Drake Moulton, P.E. – HDR
Notes: AW

## Slide 2
Sympson Lake
Dam
TO BOSTON
TO LEXINGTON
TO I65
BARDSTOWN WTP
BLUEGRASS PARKWAY
Notes: AW

## Slide 3
Dam Overview
Constructed in 1963
Significant Hazard Dam (Class B) w/ a current Unsatisfactory Rating
Primary Water Supply Reservoir for City of Bardstown
Normal Pool EL. 520.2 ft
Zoned Embankment:
  73-ft height
  1,030-ft length
  Crest Elev. 530 ft.
  2:1 Slopes
Critical Infrastructure & Features
1979 Spillway Rehabilitation
109-ft Overflow Ogee Weir
Concrete-Lined Spillway
Design Storm: Elev. 529.3 ft.
4 ft × 4 ft RCBC w/ 30-in. Raw Water Line Along Foundation
Existing 14-in. Raw Water Line
8-in. Sludge Force Main Up and Over
Site Overview
US62
Notes: AW

## Slide 4
1963
Dam Constructed
WTP Constructed
Fissured Rock Observed w/ Significant Flow at WTP
1974-1986
Four (4) Sinkholes Observed
(3 Downstream & 1 Upstream)
Dye Trace Test
Grouting Repairs (Unsuccessful)
Current Spillway Constructed (1979)
Two Ground Explorations
(1976 and 1979)
1990-2020
8-in. FM Sludge Line Constructed
Intake Tower Improvements
Continued Observations
Additional Remediation Attempts (Unsuccessful)
2021
New Sinkhole in US62
Upstream Sinkhole Reopens (1984)
GPR and Drilling
Temporary Repairs
2022-2024
2025
New Active Sinkhole in Lake
Seepage Discharge Pipe Discovered
Dye Trace Test
2026+
Additional Instrumentation
Additional Ground Exploration
Cutoff Wall Design
Construction (On-Going)
Sympson Lake Dam
Timeline
STAKEHOLDERS
Semi-Quantitative Risk Assessment (SQRA)
Ground Exploration & Instrumentation
CURRENT INVOLVEMENT
Notes: AW

## Slide 5
HISTORICAL SINKHOLES
Notes: AW

## Slide 6
1984 Sinkhole (Depression A)
  Still active with water noted flowing into the depression.
  Debris and loose soil was removed to expose the sinkhole.
  Plugged with 9 CYs of concrete and isolated from lake pool with earth berm in January 2022.
  2021 Sinkhole (Depression B)
  GPR Investigation (August 2021)
      Two areas identified as “possible voids or wet areas” (One at the sinkhole and one 82 ft. east of bridge).
    Two Geotechnical Borings (September 2021)
      One at sinkhole. “Extremely” wet soils noted from 31.3 ft. to 44.2 ft. below ground surface.
      Second located 82 ft. east of spillway bridge. No wet areas identified.
Depression B
Depression A
Depression A
2021 Sinkhole, Inspection, & Investigation
Notes: AW

## Slide 7
SQRA:
  3-day workshop including a site visit
  19 people attended from a combination of KYTC, KDOW, City of Bardstown and HDR
  Potential Failure Modes (PFMs)
    Team identified 7 credible PFMs including;
      Concentrated Leak Erosion (CLE) into or along foundation/abutment
      Internal Erosion/CLE along conduit
      Backwards Erosion Piping out of conduit
  Identified Next Steps
    Perform video inspection of 4-foot by 4-foot culvert penetration
    Perform additional geotechnical investigation and install piezometers for monitoring
2022 Semi-Quantitative Risk Assessment (SQRA)
Risk Characterization and Risk Reduction Measures
Review and Adopt Risk Matrix and PFM Order
Estimate Consequences & Confidence
Assign Likelihood of Failure & Confidence
Potential Failure Modes Analysis (PFMA)
Workshop Kick-off and Definitions
Site Visit
PFM # | Brief Description
Credible | 
1 | Concentrated Leak Erosion (Scour) Through Embankment (e.g. excavation limits for the Spillway, tree roots, and sheet piling)
2 | Concentrated Leak Erosion (Scour) of Embankment into or along Foundation/Abutment
3 [A, B, C, D] | Internal Erosion Along Conduit or Penetrating Structure, Concentrated Leak Erosion or Backward Erosion Piping along Conduit or Penetrating Structure 4 feet by 4 feet Box Culvert 14 inch Raw Water Intake 8 inch Force Main Spillway
4 | Backward Erosion Piping into Conduit, Tunnel, Drain, Pipe
5 [B, C, E] | Concentrated Leak Erosion or Backward Erosion Piping Out of Conduit 14 inch Raw Water Intake 8 inch Force Main 30 inch Raw Water Intake
6 | Embankment Overtopping
7 | Failure Due to Spillway Operation, Erosion of Lined Channel, and Stilling Basin
Ruled Out After Discussion | 
N/A | Internal Migration via Progressive Slumping
N/A | Concentrated Leak Erosion (Scour) Through Foundation
N/A | Concentrated Leak Erosion or Backwards Erosion Piping Out of Conduit
N/A | Stilling Basin Failure
SQRA = Likelihood And Consequences Of Potential Failure Modes And Prioritize Risk Mitigation Efforts
Notes: BAR

## Slide 8
2024 Subsurface Investigation
Notes: BAR

## Slide 9
2024 Subsurface Investigation
(Continued)
Geotechnical Investigation:
12 Sample (Continuous) Borings w/ Coring (5’ to ~30’ Core Length)
6 Borings w/ Fully Grouted VW Piezometers.
14 Unconfined Compression Tests on Bedrock (3,596 psi – 9,950 psi)
Stratigraphy Generally Consisted of:
  Clay Embankment Core, Weathered Bedrock, And Competent Limestone And Dolostone Bedrock W/ Minor Shale Beds.
Geophysical Investigation:
Seismic Refraction: 3 Survey Lines (Crest, Mid-Slope, Toe)
GPR: Spillway, 10’ to 12’ Spacing, 120’ Length Along Chute
  Findings:
  Highly Weathered Bedrock With Potentially Erodible Clay Seams And Shale Beds
  Open Features (Voids)
  Grout Loss During Backfilling
  Poor Bedrock Quality Just East of Spillway
  Rock Quality Increases Towards Abutments & With Depth
Notes: BAR

## Slide 10
Chart: 
1010-PZ-L Tip El. | 475.5 | 475.5
1010-PZ-M Tip El. | 481.5 | 481.5
1010-PZ-U Tip El. | 499.5 | 499.5
Normal Pool El. (520.2) | 520.2 | 520.2
Normal Pool El. 520.2
1010-PZ-U Tip El. 499.5
1010-PZ-M Tip El. 481.5
1010-PZ-L Tip El. 475.5
Boring 1010 Piezometer Readings
04/07/2025 - 07/21/2026
SITE MAP
Notes: BAR

## Slide 11
2024 Exploration Findings & Leapfrog Model
Notes: BAR

## Slide 12
New Sinkhole Discovered in September 2025 by KYTC D4 Maintenance.
Discovered During Seasonal Low Pool Conditions.
Located Approximately 65-Feet Upstream Of The Spillway
Approximately 5 Feet × 4 Feet
Water Observed Entering Sinkhole At 10 to 20 GPM While Maintaining Constant Water Level.
Proximity To Spillway And Past Sinkholes Prompted Stakeholder Meeting and Additional Investigation.
2025 Sinkhole Discovery
Notes: BAR

## Slide 13
2025 Discharge Pipe Discovery
Site Visit Performed on October 10th Prompted by a Rainfall Event Producing Approximately 3 to 4 Inches of Rain
During Inspection, a Previously Undocumented 14-inch Pipe was Discovered Discharging Water Approximately 200 GPM (Pipe Aligned Towards WTP)
Per WTP, Manganese and Iron Concentrations Not Consistent with Treated Water and More Characteristic of Water Samples from Bottom of Lake
Discharge Noted To Be Turbid With Sediment And Shells
Notes: BAR

## Slide 14
Notes: BAR

## Slide 15
Discharge Pipe Outlet /Headwall
1984 Sinkhole
2025 Sinkhole
2021 Sinkhole
Possible Seepage Connection
Approximate Alignment of Discharge Pipe
USACE Levee/Flood Wall
Rock Fissure/Back Wash Filter
Aerial of Sinkholes and
Discharge Pipe
Notes: BAR

## Slide 16
  Dye Trace Test Performed By KDOW To Investigate Seepage Pathways Associated with Sinkhole:
    10 Minutes: Observed at Backwash Filter Well.
    20 Minutes: Observed Exiting 12” Pipe Near The WTP at Toe of Dam.
    40 Minutes: Observed At Two Locations in Old Principal Spillway Channel.
  Water Samples Found Traces Of Solids.
  WTP Personnel Indicated Previous Dye Testing Identified the Same Seepage Locations.
Historic Dye Trace Test: 1984
Notes: BAR

## Slide 17
2025 Dye Trace Test
  Performed By Crawford Hydrology Laboratory (WKU).
  Evaluated Hydraulic Connections Between The Newly Discovered Sinkhole, Reservoir, And Downstream Seepage Features.
  Injected Fluorescein Dye (Green) And Rhodamine Dye (Red).
  Monitored 6 Locations Using Visual Observations, Activated Charcoal Receptors, And Continuous Fluorometric Monitoring.
  Fluorescein Dye Was Observed at The Spillway Joints, Discharge Pipe, Underdrains, And Box Culvert.
  Dye Reached the Discharge Pipe In Approximately 39 Minutes.
  Rhodamine Dye Not Visually Observed but Detected by Receptors.
Notes: BAR

## Slide 18
Notes: BAR

## Slide 19
Map of Receptor Locations & Inferred Flow Paths
(From Crawford Hydrology Laboratory
Report Dated December 2025)
Notes: BAR

## Slide 20
Fluorescein Dye
Notes: BAR

## Slide 21
Notes: BAR

## Slide 22
Lake & Seepage Monitoring Instrumentation
(Fall 2025 – Winter 2026)
Weir Flow Monitoring:
Geokon Vibrating Wire Weir Monitor
Geokon Cellular Data Logger
Custom Stainless-Steel Weir Box Fabricated Locally For Site-Specific Conditions
Lake Level Monitoring:
Campbell Scientific Aspen 10 Cellular Data Logger
RangeVue 15 Radar Water Level Sensor Mounted to Intake Tower
Initial Monitoring Utilized a Vibrating Wire Piezometer With Cellular Telemetry
Monitoring Approach Was Revised After Data Indicated Significant Sensitivity to Barometric Pressure Fluctuations
Notes: DTM

## Slide 23
Lake Level & Weir Flow Monitoring Instrumentation
Notes: DTM

## Slide 24
Power BI Instrumentation Dashboard
Provides Centralized Access to Monitoring Data
Parameters Monitored:
  Reservoir Elevation
  Lake Level Rate of Change
  Seepage Flow Rate (V-Notch Weir)
  Local Precipitation
Supports Threshold-Based Decision Making and EAP Implementation
Tracks Reservoir Levels Throughout Construction
Notes: DTM

## Slide 25
Emergency Response and Accelerated Design Schedule
New Sinkhole Discovery And Uncontrolled Seepage/Sediment Transport Required Immediate Evaluation and Development of Remediation Alternatives.
Project Advanced Through Additional Investigation to Final Design on an Accelerated Schedule to Support Emergency Procurement.
Design Completed in Eight (8) Weeks:
Week | Major Milestone
1 | Emergency Action Plan development and mapping
2 | Identification of remediation alternatives
3-4 | Design development and preparation of plans
5 | Quality Control Review Workshop
6-7 | Final design revisions and comment resolution
8 | Final contract documents completed for advertisement
Ready to Advertised Plans/Specifications Produced in Approximately 8 Weeks.
Notes: DTM

## Slide 26
Emergency Action Plan (EAP)
January 2026
Development of Roles & Responsibilities Between Stakeholders and Local Emergency Management
Inundation Mapping
Utilizes Recently Installed Instrumentation to Set Emergency Level Thresholds
Development Of Communications Chains
Prompted Installation of Pumps to Allow for Drawdown of Lake in Emergency Situations.
  Pumps Used To Lower Lake For Treatment Of Sinkhole (Per KYTC Standard Detail)
Notes: DTM

## Slide 27
Prime Aire: Model PA12A60C-B-E125
12" × 12" Electric Priming-Assisted Centrifugal Pumps
Maximum Pumping Capacity: 5,800 GPM
Powered By 125 HP Electric Motors
Solids-handling Capability Up To 3 Inches
Notes: DTM

## Slide 28
2026 Geotechnical Investigation
Purpose:
  Supplement 2024 Investigation, Provide Rock Information at Abutments, and Update PFM Risk Analyses
Ten (10) Rock Core Borings Spaced Approximately 75-Feet Along US62
22 Unconfined Compressive Strength Tests Performed on Core Samples
Results Utilized for Determination of Cutoff Wall Extents And Depth
Notes: DTM

## Slide 29
DESIGN TIP ELEVATION: 440 FT
2026 Geotechnical Investigation Results & Updated Leapfrog Model
Formation Members Mapped as “Low” Karst Potential by KGS
More Frequent Clay, Shale Seams And Weathering Present On The East Side
Bedrock Quality Generally Increases Westward
Design Wall Tip Elevation Set at El. 440.0 Feet:
  Extends Below Weathered Rock Zones
  Extend Below Elevation of Discharge Pipe
Notes: DTM
Add the roadway profile. Ask Sarah about dip/strike relationship

## Slide 30
Wall Length: ~ 990 feet Established by
Pool Level, Embankment Geometry, and Bedrock Quality.
Utility Crossings: 4’x4’ RCBC, 14” Raw Water Line, 8” Sludge FM
SECANT SHAFT CUTOFF WALL:
  370 Total, 46” Diameter Shafts
Wall Top:
  Ogee Spillway Weir: El. 517’
  Else, Existing Pavement Grade Of US62, Minus 27 Inches
  Seepage Barrier Extends to Dam Crest
Wall Tip Elev/Depth:
  West/Right Abutment: 10 ft. into Competent Bedrock
  Else: Elev. 440 ft.
Cutoff Wall Design
Notes: DTM

## Slide 31
Cutoff Wall Design (Continued)
Notes: DTM

## Slide 32
Lake Level Control & Intake Tower Modifications
Lake Level Control is Required for Wall Construction.
Currently No Means for Controlled Drawdown Which Impacts the KDOW’s Condition Assessment of the Dam (Poor Rating).
Conflicting Information on Historic As-builts.
Dive Inspections and a Hydrographic Survey Were Performed By Marine Solutions, Inc (MSI).
Raw Water Supply Constraints Precluded Modification Of The Existing Intake Structures.
A Penetration/Siphon System is Being Evaluated as A Drawdown Measure.
Notes: DTM

## Slide 33
Hydrographic Survey Results from Marine Solutions Inc., Dated March 13, 2026
INLET OF 24” LOW LEVEL CONTROL PIPE
INTAKE TOWER
Results of Hydrographic Survey
UPPER INTAKE PIPES
Notes: DTM

## Slide 34
Advanced Advertisement: April 16, 2026
Mandatory Pre-Bid Meeting: April 30, 2026
Letting Date: May 21, 2026
Engineer’s Estimate: $33,513,497.60
Two Bidders:
    Schnabel Foundation Company: $21,992,077.21
      (Awarded on 5/27/26)
    Richard Goettle Inc: $27,727,000.00
Fixed Contract Completion Date: August 1, 2027
Current Construction Activities: Maintenance of Traffic Operations
Cutoff Wall Construction to Start End of September / Early October
Letting, Award, & Construction Status
Notes: AW

## Slide 35
FamilyID=Office_ArchiveTorn
Construction Status Photos
Notes: AW

## Slide 36
QUESTIONS?
Notes: AW

## Slide 37
Down Stream Filter Diaphragm
Notes: DTM