## qProjectsIssues
Review Date | Catergories | Topics | Project Type | District | County | Issue | Solution
2018-03-05 | Design | Erosion Control | BRIDGE REPLACEMENT(P) | 5 | FRANKLIN | During construction activities, KYTC’s Erosion Control Specialist contributed to the decision to place additional channel lining along the creek’s side slopes. However, the contract did not include the necessary amount of channel lining based on this decision. | A change order was issued to increase the amount of Class II channel lining and district construction personnel directed its placement.
2018-03-05 | Proposal | Quantities | BRIDGE REPLACEMENT(P) | 5 | FRANKLIN | Generally, mobilization is not included as a bid item in projects under $2 million. As such, bidders add the cost of mobilization in to other bid items (such as, asphalt surface), which can lead to overcharging if there are overruns on those items. | The Cabinet should consider including mobilization on smaller contracts to eliminate cost shifting and potential overcharging. Further study on this issue may be warranted.
2018-03-05 | Structures | Wing Walls | BRIDGE REPLACEMENT(P) | 5 | FRANKLIN | Because the area above the wing walls had not been accounted for, the plans required the addition of a larger area of full-depth construction. District design stated they did not realize how far the Conspan wing wall anchors would go into the existing roadway. | A change order was issued to add quantities necessary for full-depth construction, including crushed aggregate 57s, DGA, Asphalt base, and Asphalt surface.
2018-03-05 | Structures | Bearing Pad | BRIDGE REPLACEMENT(P) | 5 | FRANKLIN | The contract did not include an essential 1.5 foot wide moment slab directly under the Bridge Rail Type III. The Bridge Rail requires a 1.5 foot moment slab for structural integrity. | The district requested a change order to include one 1.5 foot moment slab. Once approved, the district installed and paid for the slab per Standard Drawing BHS-008-02.
2018-03-05 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 5 | FRANKLIN | The plans included guardrail end connectors Type D for connection to the Conspan precast wing walls. However, Type D connectors interfered with the precast culvert wing walls that were left and right of Station 11+60 and 11+90. | A change order was issued to switch from Type D to Type A guardrail connectors. Type As were installed on all four bridge ends.
2018-03-05 | Design | Lighting | MAJOR WIDENING(O) | 5 | OLDHAM | The plans called for partial removal of highway lighting along off-ramp I-71 south bound without consideration of power interruption to the remaining highway lights. Therefore, the electric was interrupted absent contract requirements that electricity be provided to the remaining highway lights. | A change order was issued to reenergize the circuit by installing a temporary aerial distribution power crossing. The existing highway lights were reenergized.
2018-03-05 | Construction | Railroads | MAJOR WIDENING(O) | 5 | OLDHAM | The plans called for roadway excavation with blasting to within 150 feet of an existing rail line. Excavated rock was to be used for Rock Roadbed installation within the project. During construction, the railroad company moved the blasting zone limit to 300 feet. This unforeseen revision created a shortage of Rock Roadbed for the project. Also, an unexpected seam of non-durable shale was discovered, which further reduced the amount of Rock Roadbed available. | A change order was issued to include CRUSH STONE Surge Stone Rock Roadbed, to be used in place of Rock Roadbed.
2018-03-05 | Construction | Revisions | MAJOR WIDENING(O) | 5 | OLDHAM | As designed, the project eliminated a TARC Park & Ride parking lot on the north side of Commerce Parkway. To compensate, future plans for an adjacent Kroger parking lot were to include a designated section for TARC parking. Unfortunately, Kroger delayed their project which led to a loss in TARC Park & Ride parking. | Oldham County and KYTC agreed to build a temporary gravel parking lot for TARC Park & Ride on the south side of Commerce Parkway to be installed by KYTC.
2018-02-15 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 4 | MARION | The gas company tried to prevent the contractor from blasting for roadway excavation near the company’s 30-inch gas line. Lawyers representing the gas company and the contractor became involved in this issue, but were never able to reach an agreement. The gas company wanted to hold the contractor liable for any gas line damages that might occur. This was unacceptable to the contractor. | The contractor ultimately proceeded with limited blasting (low shot / small number of holes / about 13 holes per shot) without any resulting damages to the gas line. (D4 noted seismograph readings were very low and were not even close to exceeding allowable limits.)
2018-02-15 | Structures | Wing Walls | RECONSTRUCTION(O) | 4 | MARION | The bridge could not be constructed as designed due to a conflict with the existing road. The plans depicted one of the bridges’ wing walls encroaching two feet into the existing lane. As depicted, this would have created problems for traffic on the old road, as well as transitioning traffic onto the new road/bridge. (It was noted that bridge plans are oftentimes submitted extremely late in the process preventing adequate time to review phasing aspects of a project.) | Traffic was allowed to move on to the new alignment following construction of a burrito wrap fill wall that allowed for a near vertical fill. A construction joint was also placed in the bent. (It was noted that recently, bridge plans have been received earlier.)
2018-02-15 | Traffic | Raised Pavement Markers | NEW ROUTE(O) | 4 | MEADE | The plans called for the installation of raised pavement markers; however, the district does not advocate raised markers due to safety and maintenance concerns. For example, snow plows are prone to dislodging and projecting pavement markers into surrounding areas, possibly striking vehicles and pedestrians. Replacing dislodged markers also creates maintenance issues for the district. (Safety and maintenance concerns have been discussed in other districts, as well.) | In place of raised pavement markers, inlaid pavement markers were installed. Snow plows do not pose a dislodging risk to inlaid pavement markers, thereby eliminating safety and maintenance concerns. (A change order was initiated to address this revision, but was never officially issued.)
2018-02-15 | Design | Sight Distance | RECONSTRUCTION(O) | 4 | MARION | The original plan was to leave an existing bridge at one of the private property entrances. However, D4 construction found issues with limited site distance and steepness where the entrance intersected with the new roadway. | The property owner was compensated under a right-of-way settlement for the construction of a new bridge at a higher elevation that lessened the grade of the entrance and improved the site distance at the intersection with the new roadway. The district helped the property owner connect with a bridge contractor, but the work was contracted by the property owner. It was noted that the right-of-way settlement was the most cost effective way to address this problem. The district did install a temporary entrance (pipe) for the property owner while the new bridge was being built.
2018-02-15 | Construction | Inspection | NEW ROUTE(O) | 4 | MEADE | The contractor erroneously covered the rock cross drains, which prevented them from draining. This resulted in a super-saturated roadway embankment that ultimately led to shoulder settlement (base and pavement separation). | The rock cross drains were uncovered which allowed the drains to function properly. Once opened, ground water came “filtering-out,” which allowed the embankment to dry. Lastly, shoulder settlement and pavement separation were repaired.
2018-02-15 | Design | Plans | NEW ROUTE(O) | 4 | MEADE | The plans erroneously specified a Case I condition for the proposed concrete retaining wall. As such, the concrete wall base was too small to provide stability (i.e. subject to overturning). | A larger concrete wall was constructed based on a Case III condition. A change order was issued for additional class B Concrete needed for the larger concrete wall.
2018-02-15 | Drainage | Ponding | NEW ROUTE(O) | 4 | MEADE | The sinkhole selected to receive surface flow from the site ditches could not take water fast enough, creating backwater problems and standing water in the upstream ditches after rainfall. It was noted that the intake capacity of sinkholes can be difficult to determine. | A detention basin was built to receive and store the surface water from the ditches. This eliminated backed-up water since the detention basin could receive surface flow much faster than the sinkhole.
2018-02-15 | Design | Omission | RECONSTRUCTION(O) | 4 | MARION | The project had numerous slopes steeper than a 3:1, but the contract did not include Crown Vetch. Section 212.03.03 of the Standard Specifications states that all slopes steeper than a 3:1 shall be sown in Crown Vetch. D4 stated that this was simply an oversight a simple plan omission. | A change order was issued to include Crown Vetch in the contract. Subsequently, Crown Vetch was sown on all slopes steeper than a 3:1 as required by the Standard Specifications.
2018-02-15 | Design | Guardrail | RECONSTRUCTION(O) | 4 | MARION | The plans erroneously called for Type 2 guardrail end treatment to be installed in oncoming traffic. D4 stated that Type 2 end treatments are not appropriate for oncoming traffic. | A change order was issued to add one Type 7 guardrail end treatment in place of Type 2.
2018-02-15 | Design |  | RECONSTRUCTION(O) | 4 | MARION | Problems with type-4 fabric wrinkling and tearing during construction reduced the blanket’s ability to prevent aggregate migration and increase subgrade strength. | Type-4 was placed, however D4 recommended using type-5 fabric as it is heavier, stronger, and less likely to wrinkle. D4 also recommended eliminating the fabric and increasing the amount of roadway aggregate to provide for enhanced subgrade strength.
2018-02-15 | Utilities | Relocation | RECONSTRUCTION(O) | 4 | MARION | The utility designer did not take the profile (cross-section) into account when relocating the water. As a result, the relocated waterline was not placed deep enough under the side entrances. | The water line sections at side entrances were relocated deeper. The municipal utility company performed this work and, as negotiated with them, the district paid for about half the cost of this effort.
2018-02-15 | Drainage | Elevation | RECONSTRUCTION(O) | 4 | MARION | There were drainage issues at Mt. Airy Road. As the vertical curve was lessened, it created a shallow ditch that was not draining. As a result, some of the new homes were negatively impacted. | The grade of the ditch was raised and a pipe was added to carry surface flow towards the south away from the impacted properties.
2018-02-15 | Drainage | Flooding | RECONSTRUCTION(O) | 4 | MARION | The abutments for the new replacement bridge created a bigger opening than the abutments of the original bridge. This allowed more water to pass through and created flooding issues for a downstream property owner. | A 3-foot earth berm was constructed around the property to keep the water out.
2018-02-15 | Structures | Beams | RECONSTRUCTION(O) | 4 | MARION | A camber issue with one beam created a cover height problem. As such, the plan quantity of bridge deck concrete was insufficient to meet the height (thickness) required for proper cover. | Additional concrete was placed to meet the cover requirements. The contractor incurred the cost of the additional concrete needed.
2018-02-02 | Maintenance of Traffic | Diversions | BRIDGE REPLACEMENT(P) | 9 | NICHOLAS | Initially, asphalt pavement courses were placed “straight-up” at longitudinal joint locations to provide for a 20-foot width road. However, this did not include a necessary longitudinal joint for subsequent road widening. | A change order was written to include milling that would create a necessary “stair-step” longitudinal joint rather than vertical.
2018-02-02 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 9 | NICHOLAS | Originally, two feet of the rock roadbed was to be constructed from existing rock. However, the existing rock was determined unsuitable due to its high soil content. Consequently, the pavement design was inadequate and needed revision. | A change order was issued placing an additional 2.75 inch lift of asphalt base and using quarried rock in lieu of rock roadbed.
2018-02-02 | Geotechnical | Cut-Slope | BRIDGE REPLACEMENT(P) | 9 | NICHOLAS | Geotechnical expected more rock in the subsurface between bridge Pier 3 and Abutment 2 than was found. As a result, erosion control protection was needed for the excavated outslope, but the contract did not include crushed aggregate for this purpose. Moreover, KY Division of Water (DOW) asked for additional slope protection around the old bridge pier, which also added to the need for aggregate. | A change order was issued for 645 tons of Crushed Aggregate Slope Protection to be placed as on the slope as needed. “A few loads” were added around the old bridge pier as an agreed upon enhancement with DOW.
2018-02-02 | Geotechnical | Slides | LANDSLIDE REPAIR(P) | 9 | ROWAN | A landslide outside of the ROW limits was triggered by roadway excavation. The landslide became very active, whereby material and trees began encroaching into the roadbed construction area creating a work zone safety hazard. | A change order was issued to include cost-plus work for clearing and grubbing the landslide, as well as the purchase of additional ROW for landslide abatement beyond the original limits.
2018-02-02 | Geotechnical | Slides | LANDSLIDE REPAIR(P) | 9 | ROWAN | The roadway bench was cut to planned elevation. Overnight, however, the bench slid, rotated up four feet, and was noticeably saturated. It was stated that the plan excavation depth did not go below the slip plane. As such, it was unsuitable to build structural fill across this area. | A change order was issued to over-excavate this area to the slip plane. Additional quantities of granular embankment, # 2 Stone, and erosion control blanket were added to create a stable embankment. Drainage from an underground spring was collected in a granular buttress drain and daylighted into an adjacent stream.
2018-02-02 | Maintenance of Traffic | Diversions | BRIDGE REPLACEMENT(P) | 9 | NICHOLAS | A traffic switch between phases 2 and 3 did not account for an eight-foot vertical difference and the very sharp turn to diversion (26 feet shift in 150 feet length). As such, D9 construction felt the MOT could not be implemented as designed. | The diversion was pushed alongside the hill to lessen the sharpness. Also, 80 linear feet of 18” pipe was placed within the 8-foot vertical drop which carried drainage through this area while the diversion was in place.
2018-02-02 | Geotechnical | Top of Rock | BRIDGE REPLACEMENT(P) | 9 | NICHOLAS | The top of the competent rock elevation at bridge pier two was inaccurate; consequently, the pier’s footing could not be poured at the planned elevation. | Additional excavation was required to get to suitable subgrade. A change order was issued for the mass concrete required to compensate for the extra depth needed to seat the footing on competent rock.
2018-01-23 | Utilities | Relocation | MAJOR WIDENING(O) | 7 | MONTGOMERY | Existing utilities (water, sewer, and telephone) were relocated 10 to 20 feet too close to the roadway construction from the beginning of the project to Valhalla Subdivision. The cause for building them in the wrong location is unknown. | To avoid relocating utilities again or purchase of additional right-of-way, roadway outslopes were steepened, and additional storm sewer pipe was installed to eliminate a ditch.
2018-01-23 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 7 | MONTGOMERY | An existing, six-inch water line that fed the Old Silo Golf Course was not identified in the plans and was interfering with roadway construction. | A change order was issued to relocate the water line. It was noted that it would have been difficult to know that this private utility existed.
2018-01-23 | Traffic | Omission | MAJOR WIDENING(O) | 7 | MONTGOMERY | The plans called for 24-inch Thermo Stop Bar(s) at several locations, but a pay item was not established. D7 stated this was an omission by them. | A change order was issued to include a pay item for 24-inch Thermo Stop Bar.
2018-01-23 | Utilities | Conflicting Information | MAJOR WIDENING(O) | 7 | MONTGOMERY | Gas line relocations were programed for $2 million as let. Once roadway construction began, however, Spectra Energy (gas line owner) stated the gas line relocations would cost $15 million. At that point, the project became too expensive to construct. | The project was halted, and a roadway redesign was conducted to reduce the amount of gas line relocations. Based on the redesign, the relocations efforts were reduced. This reduced the total relocation cost $5-6 million.
2018-01-23 | Utilities | CAP | CONGESTION MITIGTN(O) | 7 | FAYETTE | The original intent of the project was to supply “underground electric” to the trailhead restrooms in order to maintain a primitive environment at the campground. However, the project plans did not specifically request underground installation. Rather, the plans stated that it was the contractor’s responsibility to supply electric service as incidental to the restrooms. As such, the contractor’s bid was based on the less expensive overhead installation. | A change order was issued to compensate for the cost difference between underground and overhead installation. The district stated this was a “reasonable” solution to this issue.
2018-01-23 | Utilities | Relocation | CONGESTION MITIGTN(O) | 7 | FAYETTE | An underground electric service interfered with the construction of the pervious parking lot. As designed, the lot required “multiple feet” of excavation to install the permeable media (layers of aggregates) beneath it. | The existing electrical service was excavated, then reburied deeper to allow the pervious parking lot to be constructed as initially designed. A change order was issued for relocation of the electrical service.
2018-01-23 | Utilities | Relocation | SAFETY(P) | 7 | FAYETTE | An underground electric service interfered with the construction of the pervious parking lot. As designed, the lot required “multiple feet” of excavation to install the permeable media (layers of aggregates) beneath it. | The existing electrical service was excavated, then reburied deeper to allow the pervious parking lot to be constructed as initially designed. A change order was issued for relocation of the electrical service.
2018-01-23 | Utilities | Inaccurate Location | SAFETY(P) | 7 | FAYETTE | An existing 42-inch, high pressure water main was incorrectly located on the project plan set and ultimately interfered with the planned culvert extension. This led to a construction delay for needed revisions of the culvert and the handrail. | A change order was issued to add 175 days to the project, pushing final completion from August 21, 2016, to February 9, 2017. This allowed sufficient time to revise the culvert extension (basically shortening the barrel outlet) and complete the handrail fabrication as needed. As part of the solution, the water main was accurately located by potholing.
2018-01-23 | Utilities | CAP | SAFETY(P) | 7 | FAYETTE | The original intent of the project was to supply “underground electric” to the trailhead restrooms in order to maintain a primitive environment at the campground. However, the project plans did not specifically request underground installation. Rather, the plans stated that it was the contractor’s responsibility to supply electric service as incidental to the restrooms. As such, the contractor’s bid was based on the less expensive overhead installation. | A change order was issued to compensate for the cost difference between underground and overhead installation. The district stated this was a “reasonable” solution to this issue.
2018-01-23 | Design | Quantities | CONGESTION MITIGTN(O) | 7 | FAYETTE | Designers estimated 10% of the #8 Crushed Aggregate used to develop a two-inch lift above the #2 Stone would filter down into the #2 Stone; however, twice that amount filtered into the #2 Stone. Therefore, there was an insufficient amount of #8 Crush Aggregate in the contract to complete this work. | A change order was issued for additional #8 Crushed Aggregate to achieve the two-inch lift while allowing for 20% filtering into the #2 Stone. (The district noted that the #2 Stone appeared to meet specifications for this size rock.)
2018-01-23 | Utilities | Inaccurate Location | CONGESTION MITIGTN(O) | 7 | FAYETTE | An existing 42-inch, high pressure water main was incorrectly located on the project plan set and ultimately interfered with the planned culvert extension. This led to a construction delay for needed revisions of the culvert and the handrail. | A change order was issued to add 175 days to the project, pushing final completion from August 21, 2016, to February 9, 2017. This allowed sufficient time to revise the culvert extension (basically shortening the barrel outlet) and complete the handrail fabrication as needed. As part of the solution, the water main was accurately located by potholing.
2018-01-23 | Construction | Omission | MAJOR WIDENING(O) | 7 | MONTGOMERY | The edge key was accidentally deleted in change order 1. This was an error by construction. No information was known on how it occurred. | It was added back in change order 2.
2018-01-23 | Drainage | Temporary Drainage | MAJOR WIDENING(O) | 7 | MONTGOMERY | There were no provisions in the project plans to safeload the temporary drainage pipe once it was no longer needed. D7 noted that removing the pipe was not feasible as it would require digging up the new road. | A change order was issued to safeload the pipe to provide for long-term stability.
2018-01-23 | Design | Quantities | SAFETY(P) | 7 | FAYETTE | Designers estimated 10% of the #8 Crushed Aggregate used to develop a two-inch lift above the #2 Stone would filter down into the #2 Stone; however, twice that amount filtered into the #2 Stone. Therefore, there was an insufficient amount of #8 Crush Aggregate in the contract to complete this work. | A change order was issued for additional #8 Crushed Aggregate to achieve the two-inch lift while allowing for 20% filtering into the #2 Stone. (The district noted that the #2 Stone appeared to meet specifications for this size rock.)
2017-12-05 | Drainage | Sheet Flow | NEW ROUTE(O) | 2 | CHRISTIAN | A drop box was built on an entrance adjacent to the roadway. Asphalt paving from the roadway did not extend to the drop box. As such, sheet flow from the pavement eroded the soils around the drop box and does not enter the drop box. The drop box inlet is currently higher than the surrounding ground level. | D2 construction stated they should have paved to the drop box which would have prevented erosion.
2017-12-05 | Design | Shoulders | NEW ROUTE(O) | 2 | CHRISTIAN | To facilitate concrete curb / gutter installation in areas adjacent to the existing pavement, where the pavement was being salvaged, longitudinal saw cutting of the existing pavement was identified as a bid item. However, the normal six-inch offset dimension to create a working area, from face of saw cut to the face of new gutter, was not identified on the plans, nor was a bid item and quantity provision made to backfill the resulting void area. | Flowable fill was placed in the void next to the concrete curb to provide for a solid base. (It was noted that for future projects, a six-inch (width) by nine-inch (deep) by length can be used to calculate the amount of flowable fill needed to fill these voids. It was also noted that all slip form machines need the additional six-inches from existing road to install concrete curb.)
2017-12-05 | Utilities | Existing Utilities | NEW ROUTE(O) | 2 | CHRISTIAN | There were several areas where underground utilities were not located accurately on the plans. This included a waterline location that was off by ten feet. This led to delay problems during construction. The waterline locations in question were based on inaccurate BUD locations (paint) that were mapped by the survey crew. See Comments Section, Note 2. | A change order was issued to pay the contractor to find the underground utilities. Once located, adjustments were made in the field to relocate them as determined by D2 construction personnel. In hindsight, SUE confirmations would have prevented this error.
2017-12-05 | Utilities | Omission | NEW ROUTE(O) | 2 | CHRISTIAN | A 12-inch valve needed for water line relocation was not in the bid items. It was erroneously omitted from the contract. | A change order was issued to include this item in the contract. The water line was relocated to facilitate roadway construction.
2017-12-05 | Geotechnical | Cut-Slope | DESIGN ENGINEERING(O) | 2 | WEBSTER | Due to budgetary constraints, ramp construction cut slopes were designed on a 2:1 to minimize earthwork efforts. However, the insitu material in these cut sections was very weak (SDI Index 6 to 7) and as such, 2:1 slopes became very unstable. It was noted that the geotech report stated 2:1 slopes would be stable, but this statement was found to be erroneous. | The short term solution will be to continually remove the silt from the ditches generated from the erodible slopes. Long term solution would be to flatten the cuts to a 3:1 slope and establish vegetation to eliminate erosion.
2017-12-05 | Utilities | Existing Utilities | DESIGN ENGINEERING(O) | 2 | WEBSTER | The outlet end of a culvert as designed on Ramp 2, encroached upon a high pressure gas line owned by Century Aluminum. The gas line was not known about and therefore not accounted for in the design. FHWA wants KYTC to purchase additional ROW and move the line. This is an ongoing discussion with FHWA, but KYTC has no relocation work planned at this time. | The outlet of the culvert was shortened by two sections to avoid the gas line. As constructed, the outlet is about 3 feet from the gas line. The slope above the pipe needed to be steepened and rock backfill was installed to stabilize this area. To move the gas line more ROW will need to be purchased.
2017-12-05 | Design | Guardrail | DESIGN ENGINEERING(O) | 2 | WEBSTER | The guardrail at a ramp entrance did not extend far enough according to D2 construction personnel. As designed, it stopped at the tangent which was subject to a motorist hitting the end of this or perhaps going off the road an down a steep embankment. | A change order was written to extend the guardrail from Ramp 4 on to KY 56 thereby increasing safety in this area.
2017-12-05 | Drainage | Sheet Flow | DESIGN ENGINEERING(O) | 2 | WEBSTER | There was numerous embankment washouts from roadway sheet flow that was threatening the stability of the road. As noted, no asphalt wedge curb or concrete flumes were set up in the contract to properly handle roadway sheet flow. | A change order was issued to include concrete curbs and flumes to properly channel surface runoff and prevent road embankment erosion gullies. It was noted that concrete wedge curb is preferred over asphalt for long-term durability reasons.
2017-12-05 | Traffic | Lighting | DESIGN ENGINEERING(O) | 2 | WEBSTER | Navigational light junction boxes access doors could not be opened as they were located next to the KY 56 bridge rail. As such, it could not be accessed for maintenance. | A meeting was held in the central office with Traffic Branch representatives. Ultimately a change order was issued and new boxes were made which allowed access for maintenance.
2017-12-05 | Traffic | Signs | DESIGN ENGINEERING(O) | 2 | WEBSTER | The signage (SBM Alum Sheet Signs) as called for in the plans did not meet FHWA standards for interstate highways. As such, these signs would have prevented the parkway from being shielded (i.e. designated Interstate 69.) | A change order was issued to installed signs (SBM Alum Sheet Signs Type IX) which met FHWA standards for Interstates.
2017-12-05 | Drainage | Error | DESIGN ENGINEERING(O) | 2 | WEBSTER | The mountable median, as designed on KY 56, called for a Curb Box Inlet Type A, but this type is four inches higher than the surrounding median. This Inlet type is not designed to be driven on. | A change order was written to use a Drop Box Inlet Type 12A which matches the elevation of the median and can handle all traffic loads.
2017-12-05 | Drainage | Headwalls | DESIGN ENGINEERING(O) | 2 | WEBSTER | When cross drain headwalls are installed on a fill mid-slope, the slope tends to be undercut by drains outflow. When this happens, the headwalls pull away from the pipe and becomes nonfunctional. | D2 construction recommend installing non-perforated pipe from the cross drain headwalls to the toe of the slope. On this project, cross drains were daylighted at the toe of slope.
2017-12-04 | Design | Survey | BRIDGE REPLACEMENT(P) | 1 | CALLOWAY | There was an error in the survey data which caused the bridge to be built three feet higher than intended. In turn, embankment quantities for the approaches on both sides of the bridge were insufficient as embankment needed to be three feet higher to meet the bridge. The survey data error stemmed from a translational error going from assumed coordinates to state plane coordinates. The coordinate control sheet was not updated to reflect the updated state plane coordinate system. Initially, assumed coordinates were established at the beginning of the design process, but as the project progressed state plane coordinates were established. The higher embankment caused the side slopes to be steepened to keep the footprint within the right of way. | A change order was issued to increase embankment quantities needed to construct the approach embankments to meet the bridge. As noted, the project error actually improved vertical alignment as it took some of the sag out of the roadway. To prevent erosion on the steepened side slopes, aggregate was placed on the slopes. (It was noted that additional right of way could have been purchased to solve the problem, but it would have been too time consuming.)
2017-12-04 | Traffic | Raised Pavement Markers | SAFETY(P) | 1 | MARSHALL | There were no pavement markers set up for the reconstructed ramps and to replace those on the mainline that were missing. | A change order was issued to include Pavement Marker Type V-B W/R and Pavement Marker Type V-B Y/R which are the raised type. (District noted that they are moving towards inlaid markers instead of raised. District 1, similar to District 10, favor them due to better durability. For this project, the decision to use raised was based on consistency, as the existing parkway were marked with raised markers.)
2017-12-04 | Design | Omission | SAFETY(P) | 1 | MARSHALL | The district field office prefers a masonry coating or other aesthetic enhancement (e.g. form pattern) on exposed concrete gravity walls. However, no bid item or note requiring these enhancements were in the plans or contract documents. | A change order was issued to provide for a masonry coating to be applied to the concrete gravity walls.
2017-12-04 | Geotechnical | Unsuitable Material | SAFETY(P) | 1 | MARSHALL | The plans called for widening existing ramps to bring them up to interstate standards as agreed upon with FHWA. As the widening efforts proceeded, unsuitable subgrade material in parts of the widening areas were discovered. However, no provisions were included in the plans to address these areas. | A change order was issued to add No. 23 Stone and to increase the amount of filter fabric and excavation (undercut item) which were already set up. As unsuitable subgrade areas were discovered, they were undercut two feet and No. 23 Stone wrapped in filter fabric was installed. This created a suitable subgrade capable of supporting the ramp widening areas. It was noted that three ramps were involved in subgrade enhancement efforts.
2017-12-04 | Design | Communication | SAFETY(P) | 1 | MARSHALL | The term “Operational Limits of the Interstate” was not defined by FHWA in the interstate conversion agreement with KYTC/D1. In the conversion agreement, FHWA stated that all curbs shall be removed within the Operational Limits of the Interstate limits. As such, D1 construction personnel did not have a clear understanding of how much curb to remove. | During construction an FHWA representative reviewed the project with D1 construction personnel and determined what sections needed to come out. During this meeting the FHWA representative stated that on upcoming projects this term will be defined.
2017-12-04 | Construction | Revisions | SAFETY(P) | 1 | MARSHALL | Sections of the inside fast lanes did not properly drain due to errors in resurfacing work done in 2007. However there was not enough pavement set up in the plans to best correct this problem. There was enough pavement set up to fix the inside lanes, but there was not enough pavement to carry it through the outside lanes. | A change order was issued to increase pavement quantities to surface all lanes. Raised medians were taken out and the roadway was resurfaced with a normal crown configuration (2% cross slopes) through the outside lanes. This allowed the surface flow to properly drain, eliminate ponding water, and provide for a consistent cross slope for all lanes. Paving both lanes was considered the best fix by District 1. (It was noted that the district asked the consultant to develop a basic design package with quantities that would allow them to get started on the project. As such, issues such as these were expected to be addressed by D1 construction personnel.)
2017-11-21 | Design | Omission | SAFETY(P) | 11 | HARLAN | No fuel adjustment bid item was set up in the contract documents. This omission was an error in the contract documents submitted to the central office. | A change order was issued to include a Fuel Adjustment bid item in the contract as required by Section 109.07.02 in the specifications. Better QA/QC may have prevented this omission from occurring.
2017-11-21 | Drainage | Existing Pipe | NEW ROUTE(O) | 11 | LAUREL | During construction near the Flav-O-Rich property, the outlet of a 30-inch or 36-inch diameter metal pipe was unexpectedly encountered; no provisions were in the plans to address it. The pipe was degraded and in extremely poor condition at this end. (D11 construction personnel noted that this pipe would have been difficult to know about during design phase as is was “hidden in a hole.” It was also noted that it drains Flav-O-Rich’s parking lot) | Beginning at the outlet, sections of the degraded metal pipe were removed. Pipe removal proceeded upstream towards Flav-O-Rich’s new entrance. Eventually, the pipe condition improved and was determined to be suitable. It was cut at this location and a Manhole (Type C) attached. New pipe to replace the degraded pipe was attached to the manhole; the newly installed pipe daylighted on the opposite side of the frontage road.
2017-11-21 | Design | Omission | NEW ROUTE(O) | 11 | LAUREL | The cross sections didn’t depict how the roadway embankment slope was to tie into the adjacent dam embankment slope. The plans were unclear in this regard. | D11 construction stated “they did the minimum (benching into the dam wall), they could get by with.” The dam’s outflow drainage was rerouted which required “tearing out and fixing some pipes.” (It was also noted that D11 did not need to disturb the dam overflow (emergency spillway) as it was on the far side away from the roadway construction)
2017-11-21 | Utilities | Existing Utilities | NEW ROUTE(O) | 11 | LAUREL | Three abandoned sewer manholes were unexpectedly encountered during construction but no provisions in the roadway contract were set up to address them. It was noted that the top of these manholes were located at approximate grade level and as such they did not lend themselves to be dug up and removed. | For this project, a change order was issued to safe load the manholes to provide long-term subgrade stability. Ideally, the district utilities supervisor should include abandoned utilities (e.g. manhole) as part of the utility relocation contract.
2017-11-21 | Drainage | Existing Pipe | SAFETY(P) | 11 | HARLAN | During roadway construction, an existing old cut sandstone culvert (est. 1920s vintage) was found to be severely compromised. It collapsed during construction but no provisions were in the contract to address this problem. (District design noted that they believed the culvert was in suitable condition and therefore intentionally left it out of the project.) | A change order was issued to install a 54-inch concrete culvert to handle the drainage at this location.
2017-11-21 | Geotechnical | Quantities | NEW ROUTE(O) | 11 | LAUREL | The structural solid rock excavation quantities needed to install three culverts were significantly low (13 cubic yards per structure) There was no coring done by geotech. Division of Structural Design stated that when no geotech data is collected, this is the quantity typical setup. (It was noted that the district “got lucky” as the contractor bid this item at a reasonable unit price; many times when an item quantity is significantly under estimated, contractors will include a unit bid price significantly above an average unit price.) | A change order was issued to include the proper amount of structural rock excavation to install all three culverts. The revised quantities were based on actual field survey measurements. D11’s PD&P recommends to at least include the entire footer (length, width & depth) for rock excavation estimates when no geotech data is available.
2017-11-21 | Construction | Public Relations | NEW ROUTE(O) | 11 | LAUREL | There were conflicts with adjacent sewer line work being performed on the behalf of the city of London. The sewer line ran along a road that was needed to access the roadway project. The road became damaged due to construction traffic by both KYTC’s contractor and the city of London’s sewer contractor. However, the residents that lived on this road primarily blamed KYTC for the damage. | To appease the residents, a change order was issued to repair the road (asphalt placement and to maintain traffic.) At the completion of KYTC’s project, asphalt was placed to repair sections of the road back to pre-construction conditions. (Also noted, leveling and wedging could have been setup to routinely fix certain spots during the construction period.)
2017-11-21 | Geotechnical | Slides | SAFETY(P) | 11 | HARLAN | A slide above KY 38 developed 300 feet outside of the excavation limits, but within the project limits. The slide moved downward and damaged KY 38. Due to the proximity of the slide to KYTC’s excavation work, it was perceived by the public that road construction was the cause of the slide. However, it was noted that draining abandoned mine portals were located just above the slide and this was a significant factor in its movement. | A change order was issued to add asphalt to repair the damage caused by the slide to KY 38. The slide material was removed and placed in the designated waste area.
2017-11-21 | Geotechnical | Subsurface | NEW ROUTE(O) | 11 | LAUREL | A proposed drainage pipe near hotel was designed to be 17 feet deep. However, during installation efforts, side slopes of the trench kept collapsing making it virtually impossible to install. | A pipe was installed at a shallower depth (approximately nine feet.) Since the grade was less than designed, a larger diameter pipe was needed as to meet the hydraulic design. In was noted that the pipe as installed will meet future demand and be easier to maintain.
2017-11-21 | Construction | Damages | SAFETY(P) | 11 | HARLAN | A topic was raised by central office construction attendees that some plan notes (in other districts) contain application ambiguities regarding liquidated damages (LD’s) and disincentive fee (DF’s.) As such, contractors have been able to successfully argue with central office construction that they only required to paid for one but not both fees. | Plan notes regarding LD’s and DF’s need to clearly state that LD’s and DF’s will be added together when both are in violation. This will meet the objectives of the Cabinet, as the Cabinet intends is to collect on both when the contractor is in violation of both.
2017-11-21 | Utilities | Delays | NEW ROUTE(O) | 11 | LAUREL | Construction work was slowed due to overhead utilities lines not being relocated in time. Ideally, the contractor needed to start installing the main culvert first but could not until the lines were moved. Moreover, district design personnel stated that the plans impact note regarding utility relocation was not worded strongly enough to place the utility relocation responsibility primarily on the contractor. | The contractor worked in other areas of the project until the utilities were moved. Once the utilities were moved, the contractor began installing the main culvert. A change order was issued for an additional 203 days.
2017-11-21 | Design | Shelved Plans | NEW ROUTE(O) | 11 | LAUREL | The plans as let, erroneously called for a four-way stop at the intersection of Parker Road and the new frontage road/Kirby Lane. It was noted that originally this project was larger, whereby the frontage road was to have continued southward beyond Parker Road; in this configuration it would have made sense to have a four-way stop or perhaps other traffic control (e.g. round a bout.) | District personnel agreed that it did not make sense to have motorist stop on Parker Road as the project was built. D11 construction installed a two-way stop at this intersection; traffic on Parker Road as built is allowed to travel through this intersection without stopping. Better QA/QC may have caught this plan error.
2017-11-21 | Design | Omission | NEW ROUTE(O) | 11 | LAUREL | A Junction Box Type B was called for in the plans but was left off bid items. It was missing from both the General Summary and Final Estimate. | A change order was issued to add Junction Box Type B in the project’s bid items. The box was installed as depicted in the plans.
2017-10-26 | Utilities | Plans | BRIDGE REPLACEMENT(P) | 10 | PERRY | The utility relocation plans were not thoroughly coordinated with the roadway. The utility plans did not completely accommodate for the actual work items needed to get the existing utilities (water and sewer) properly relocated. D10 noted they did not develop the relocation plans, as they were received by a third party engineer working on behalf of the city. | A change order was issued to properly relocate both the water and sewer lines outside of the new roadway footprint. It was noted that this utility work was part of the roadway contract and this was the preferred arrangement for dealing with all publicly-owned relocation work. It gives them the best control when relocation efforts are needed and puts greater responsibility on the roadway contractor regarding location work. As noted, the more “skin in the game” the roadway contractor has greatly reduces potential relocation problems. D10 stated that nearly 100% of the time this is the way their contracts are set up.
2017-10-26 | Traffic | Markings | NEW INTERCHANGE(O) | 10 | MAGOFFIN | Based on current KYTC policy, inlaid pavement markers needed to be installed on this roadway but they were not set up in the contract. Instead, raised pavement markers were set up. | A change order was issued to install inlaid pavement markers in lieu of raised pavement markers. It was noted by D10 that inlaid pavement markers are preferred over raised markers because they are more durable.
2017-10-26 | Maintenance of Traffic | Striping | NEW INTERCHANGE(O) | 10 | MAGOFFIN | There was no temporary striping tape setup in the plans that was needed for MOT. The contractor used paint for the temporary striping instead. | Temporary tape should have been set up in the contract. Because paint was used instead, a change order was issued for water blasting to remove the painted lines. It was noted that one benefit to using painted lines is their durability under traffic compared to striping tape.
2017-10-26 | Construction | Safety | NEW INTERCHANGE(O) | 10 | MAGOFFIN | After the project was let, the contractor requested a temporary debris barrier wall (TDBW) be added to the project for safety reasons, but this item was not set up in the contract. It was noted that during project design phase that a TDBW was considered, but it was decided not to include it. It was stated that no clear KYTC/D10 guidelines exist on when to include TDBWs in the plans. Moreover, TDBWs inclusion are on a “project by project basis” as determined by the project development group. | A change order was written to include this wall as requested by the contractor. It was noted by both design and construction staff that they were in agreement with this change order request. It was still perceived to be a positive addition to the project. It was also noted that contractors routinely reuse the TDBW from project to project, but KYTC does not see any reduction in cost for it.
2017-10-26 | Utilities | Existing Utilities | NEW INTERCHANGE(O) | 10 | MAGOFFIN | AT&T did not have all of their utilities moved prior to roadway construction work as agreed upon with KYTC; a small section of AT&T line remained. It was in the way of proposed roadway construction and needed to be moved. It was noted by D10 that this type of problem is routine; primarily because agreements between KYTC & utility companies do not have any contractual monetary penalties that can be used against them by KYTC. | A change order was issued to move the utility line. This required an additional 0.9 acres of area to be disturbed by the contractor to facilitate relocation efforts. It was noted that an additional in-lieu fee for tree removal was paid.
2017-10-26 | Traffic | Signs | NEW INTERCHANGE(O) | 10 | MAGOFFIN | Visibility for KY 30 Exit (1/2 mile) roadway sign is severely limited due to the new interchange bridge pier. As such, motorists traveling eastward on Mountain Parkway cannot see the sign clearly. (It was noted that this sign was not part of this roadway contract.) | The sign should be relocated as part of subsequent projects efforts. It should be relocated further east which will allow for a clear view of the sign.
2017-10-26 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 10 | PERRY | To construct the new bridge, the contractor assumed they would be able to walk the beams into place, which was the preferred method. However, once the job was let, the Contractor discovered AECOM, the engineering firm representing CSX would not allow the beams to be walked into place (i.e. beams being lifted/transported as the crane moved.) Because of the slow process, the Contractor had to reschedule one load of beams that ultimately resulted in a three week delay. Contractor noted that in their opinion, the iterative method that AECOM did allowed (see solutions below) was less safe than walking them into place. | As approved by AECOM, each beam was moved into place by an iterative process that involved picking each member up, rotating the boom and then setting the member back down. The crane would then move (without the member) to the next location, and the process would start again. (During this project, D10 discovered that AECOM had more stringent requirements than URS. A construction liaison in attendance, stated there were other areas of the state that was having trouble with AECOM elevated requirements.)
2017-10-26 | Construction | Coordination | NEW INTERCHANGE(O) | 10 | MAGOFFIN | The prestressed concrete beams for the project had been rejected by KYTC (in July 2015) due to damage while they were at the Prestress Service’s Inc. (beam fabricator) lot. However, this information was not communicated to Central Bridge (bridge sub-contractor.) This led to the beams being delivered to the job site with some damage to them and in need of some repairs as noticed D10 construction personnel. This led to some time delays on the project and questions about who was responsible for these delays. | Repairs were made on-site with KYTC approved methodology. Also the time delay was resolved by KYTC central office approval.
2017-10-26 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 10 | PERRY | It took several iterations to get demolition plans approved by CSX for the old bridge section over CSX’s lines. This caused significant delay. Initially, the contractor wanted to drop the span going over rails but could not get approval from CSX. | First, the old bridge section was made as light as possible which required the removal asphalt roadway and some structural members. Then the frame was lifted off by a crane and set aside where it was completely demolished and removed from the project limits. KYTC granted extra days on the contract for the additional work and effort. No additional funds from the contractor was requested. The approval process as well as the demolition itself, led to additional flagmen-days which KYTC’s covered all costs for this service.
2017-10-26 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 10 | PERRY | As part of the demolition of the old bridge, the contractor wanted to roll the old bridge over then pick up, but there was unexpected concern regarding two adjacent utility lines (AEP’s electric & Windstream’s data lines.) Both companies were concerned that the lines might be too close and suffer damage during the roll over process. This caused additional delays in the demolition phase. | To address the liability risk, AEP shut the electricity off of their line as a safety measure, but did leave the line in place. During this time, AEP created a backfeed in their system to ensure customers had electrical service. Windstream’s line was physically lowered to eliminate the risk to their line. Likewise, no disruption of service was experienced by their customers. (It was generally believed that Windstream’s line was a greater risk to receive damage from the bridge demolition than AEP line, which was higher on the pole.)
2017-10-19 | Geotechnical | Sinkhole | NEW INTERCHANGE(O) | 3 | WARREN | During roadway grade work, a large sinkhole was encountered in mainline at sag point. | It was backfilled with aggregate and filter fabric, then covered with a clay cap. Also drainage plans were revised to move surface water to the outside and away from the middle (i.e. sag point.) This enhanced the long term stability of this area by prevent subsurface drainage from further eroding the sinkhole area.
2017-10-19 | Design | Guardrail | NEW INTERCHANGE(O) | 3 | WARREN | As designed, the length of guardrail at this location is not adequate to protect sign base (right side base, as approaching on-ramps for I-65 north & south.) It should have been longer to protect the sign base. | District 3 has plans to extend the length of guardrail.
2017-10-19 | Geotechnical | Sinkhole | NEW INTERCHANGE(O) | 3 | WARREN | During the gradework at Ramp 5, a large sink hole was encountered. Initially an attempt was made to backfilled with aggregate but this was not solving the problem. After 55 loads of aggregate, it did not fill the void and the aggregate kept slumping down. | A two foot thick reinforced concrete slab was pour to seal off the hole. Then bentonite was used on the ditch above it to prevent surface water from permeating into the ground. (According to a construction specialist meeting attendee, this should have capped immediately rather than continued dumping of rock down the hole.)
2017-10-19 | Environmental | Permitting | NEW INTERCHANGE(O) | 3 | WARREN | The project was let without an Army Corp of Engineers (COE) permit to work parts of the project area. These areas were over sinkholes and other areas that received groundwater whereby these were being considered jurisdictional waters of the United States. | The Contractor was directed to work in areas (primarily bridge & ramps area) that did not require COE permit. This allowed the project to move forward in construction for the first year. Then COE permit was approved which allowed construction in the entire project area.
2017-10-19 | Traffic | Coordination | NEW INTERCHANGE(O) | 3 | WARREN | As designed, the ramp had dual left turning lanes but was set up with stop sign only for traffic control. It was stated that dual left turning lanes should always be signalized for proper traffic management. | The two lanes were restriped, hashing out one of the left turns. It was noted that it is available for future expansion for two left turning lanes, but signalization will need to be installed at such time.
2017-10-19 | Structures | Beams | NEW INTERCHANGE(O) | 3 | WARREN | Outside beam camber (elevations) were different from the interior beams which led to construction problems as this difference was not accounted for in the design—this was central to all issues that followed. There were issues with clearance from outside beam to interior beams, as the outside beam was lower. This all resulted in difficulties achieving the proper concrete cover over the reinforcing steel and meeting super elevation parameters. Although there were several dry runs, the steel clearance “determined to be off” after the pour. | The contractor had to pour an additional 90 cubic yards (above the plan quantity) of concrete to get the bridge deck superelevation correct. A decision was reached by D3 whereby they did not charge a clearance penalty but the Contractor had to pay the expense of the additional 90 cubic yards of concrete.
2017-10-19 | Design | Railroads | NEW INTERCHANGE(O) | 3 | WARREN | The bridge as constructed over the railroad did not meet clearance limits required by the CSX (it was believed to be about two inches less than required.) The rail had been raised during railbed maintenance after the design was completed. | It was recommended to field verify track elevation before going to construction, particularly with older plans. A wavier was issued by the railroad which allowed the bridge to remain as constructed.
2017-10-19 | Design | Drainage | NEW INTERCHANGE(O) | 3 | WARREN | There was an area between cross sections that did not adequately address an area between the two sections. As such, a small area was left that created a drainage problem. | Contractor provided a redesign proposal that was accepted by D3. This resulted in an additional 10,000 cubic yards of embankment quantities to allow proper drainage in this area. A change order was written for this work.
2017-10-19 | Pavement | Repair | NEW INTERCHANGE(O) | 3 | WARREN | Resurfacing of the inside lanes of I-65 were necessary due to unavoidable damage caused by heavy equipment. No asphalt was set up in the plans to accommodate this need. | The inside lanes were paved as needed. (It was noted that fortunately there was enough asphalt setup to do this paving without having to issue a change order for additional quantities)
2017-10-19 | Design | Omission | NEW INTERCHANGE(O) | 3 | WARREN | The concrete barrier wall around the center bridge pier as called for in the plans was incorrect. One of the three transition walls as required going into the pier area, was not included in the plans. Lastly it was stated that the concrete quantity estimates for this area were not accurate as well. | A change order was written to construct the barrier wall with the proper taper as called for by standard drawing RBM-060 with the revised accurate quantities.
2017-10-19 | Geotechnical | Subsurface | NEW INTERCHANGE(O) | 3 | WARREN | There were foundation issues with the bridge piers due to bed rock line inconsistencies and karst holes. It was noted that “pre drilling” puts too much responsibility on construction personnel in the field. This is because it is setup on a “percentage amount” of total piles to be seating in rock. Therefore construction personnel must pick and choose where to drill. | A change order was issued for “mass concrete placement” that developed an adequate sub grade to support the bridge piers. Piers were then constructed on top of the mass concrete foundation. Predrilling needs to be enough (i.e. 100%) set up to drill every hole OR complete geotech exploration up front prior to letting.
2017-10-19 | Geotechnical | Sinkhole | NEW INTERCHANGE(O) | 3 | WARREN | In the new roadbed, a large sinkhole developed which prevented roadway construction to proceed as designed. It was noted that many problems throughout the project was due to sinkholes. | The sinkhole was capped with grout as directed by D3 construction personnel. This allowed road gradework and other construction work to proceed.
2017-10-19 | Design | Communication | NEW INTERCHANGE(O) | 3 | WARREN | Insufficient coordination between structure plans and surface/lighting plans resulted in the outside barrier wall without the needed area to mount a light pole. Change had been made to add light pole base onto structure but not communicated to construction. | A modified design was implemented based on West Virginia designs to add a base mounted on outside of wall. A change order was issued to perform the work.
2017-10-19 | Design | Elevations | CONGESTION MITIGTN(O) | 3 | TODD | The bottom of the existing bridge (where the new bridge abutment was designed to be seated) was lower than depicted on the plans. Therefore that abutment could not be built as shown in the plans without some modification. (It was stated that the designer could not have known this without “as-built” plans which were unavailable.) | A change order was issued to include mass concrete to build up the foundation to the level depicted in the plans. This allowed the abutment to be constructed as depicted in the plans. It was stated that this was the best solution. (It was noted that the bridge was designed by a statewide consultant.)
2017-10-19 | Utilities | Communication | CONGESTION MITIGTN(O) | 3 | TODD | The utility designers did not know that KYTC was lowering the road which led to an issue (i.e. insufficient cover) with a section of the existing water main. As such, no provision was setup in the contract to deal with relocation/lowering the existing water main. | The 350-375 linear feet of the existing water main was lowered so that the top of it was 36-inches below the finished grade. As stated, 36-inches is the frost line for that location and was approved by the city utility officials. (It was noted that the utility design was performed by the utility companies.)
2017-10-19 | Utilities | Relocation | CONGESTION MITIGTN(O) | 3 | TODD | The sanitary sewer could not be extended as designed. As originally designed, proposed manhole #5 (MH5) was to feed proposed downstream manhole #6 (MH6); MH6 was then to feed proposed downstream manhole #7 (MH7) which was a “tie in point” to the existing sewer line at that location (middle of Water Street) However, it was discovered that the invert elevation at MH7 was at the higher than MH6 invert elevation; therefore, it would not drain to MH7 as planned. | D3 discovered an “existing manhole” (not shown on plans) downstream “in the corner” that did have enough fall in elevation to drain from proposed MH6. A change order was written to provide for additional sanitary sewer line (111 feet of 10-inch SDR) to reach this discovered manhole. MH7 was eliminated altogether. It was stated that this was the most cost effective solution.
2017-10-19 | Design | Quantities | CONGESTION MITIGTN(O) | 3 | TODD | Plan quantity for structural granular backfill not adequate to backfill to the subgrade level. It was believed that plan quantity was not estimated up to the proposed subgrade level, and therefore the quantity estimate was low. (It was stated that no additional excavation occurred that would have led to this issue.) | A change order was issued to include an additional amount (250 cubic yards) of structural granular backfill. This allowed the granular aggregate backfill to come up to subgrade level as depicted in the drawings.
2017-10-19 | Design | Omission | CONGESTION MITIGTN(O) | 3 | TODD | A plan omission to provide electric to one building was discovered after the project was let. | Change order (#1) added trenching, conduit and wiring to the contract, to provide electric service to the building. Better QA/QC may have caught this plan omission.
2017-10-19 | Utilities | Existing Utilities | CONGESTION MITIGTN(O) | 3 | TODD | During excavation for water line replacement work, 20 linear feet of Asbestos Cement Pipe (ACP) was discovered. The ACP prevented water line work (i.e. lowering the water line) from proceeding. | A change order was issued to remove and properly disposed of the ACP. Water line work then resumed.
2017-10-19 | Construction | Delays | CONGESTION MITIGTN(O) | 3 | TODD | The contract completion date was set in advance of the school year, but due to the 100-plus year flood this delayed construction. It was inferred by D3 that this was an unavoidable “significant event” that created problems beyond anyone’s control. | Change order #3 was issued to override (nullify) liquated damages. This allowed the contractor to complete the work beyond the original contract ending date without incurring liquated damages.
2017-10-19 | Construction | Public Relations | CONGESTION MITIGTN(O) | 3 | TODD | A 100-plus year flood occurred during bridge construction with numerous nearby residences/businesses that experienced flooding. This created the perception with a few property owners that the new bridge construction created the flooding. | D3 personnel attended a local Rotary Club Meeting and explained that the bridge opening was actually wider than the previous bridge opening, and therefore did not create or worsen the flooding problem. This explanation satisfied the people at the meeting.
2017-10-19 | Geotechnical | Subsurface | CONGESTION MITIGTN(O) | 3 | TODD | While excavating for the northern bridge abutment, a spring was encountered that led to material washing out, losing material from there back slope, and ponding water. | The water was pumped out to provide for better stability and a suitable subgrade area. The foundation was then constructed as designed.
2017-10-19 | Construction | Revisions | CONGESTION MITIGTN(O) | 3 | TODD | The buildings in town were so close together it became difficult to follow the design plans regarding sidewalk installation. Some of the elevations taken off the plans did not match field conditions. | Numerous adjustments were made “on the fly” keeping two basic parameters in mind: Is ADA complaint? Is it draining? Removing and regrading landings were part of the solution as well as adding a small Type 12 drop box not called for in the plans.
2017-09-28 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | PIKE | The construction side slopes had to be laid back further than anticipated, due to encountering unsuitable material (i.e. material that was pumping and heaving.) This led to a larger void to backfill than what was anticipated in the plans. | A change order was issued to include an additional 28 cubic yards of flowable fill to backfill the larger void. The additional flowable fill provided for the needed cover and roadway subgrade at the culvert.
2017-09-28 | Design | Omission | BRIDGE REPLACEMENT(P) | 12 | PIKE | There was no Class III set up for culvert inlet protection (i.e. scour prevention) as needed. It should have been set up as a matter of standard practice for culvert installation. | A change order was issued to provide for the require amount of Class III needed. It was also noted that the Class III was grouted as typical practice.
2017-09-28 | Proposal | Coordination | BRIDGE REPLACEMENT(P) | 12 | PIKE | The project was mainly constructed during the late fall and winter months (began early November 2016, completed early May 2017). As such, D12 construction personnel felt that for safety reasons, the traffic diversion needed to be paved instead of a DGA surface. However no asphalt was set up in the plans. (It was noted that the project was originally planned to begin in the middle of construction season. It was let in July 2016 but due to some unknown delay in the central office, actual construction could not begin until November 2016. Had it have been constructed over the summer/fall months, DGA surface would have been acceptable, and paving the temporary diversion would not have been necessary.) | A change order was issued to provide for asphalt that was needed to pave the temporary diversion. It was approved prior to the winter shut down of the asphalt plants. Another possible solution may have been to delay the construction until the primary construction season (i.e. spring time) opened up.
2017-09-28 | Construction | Bench Marks | RELOCATION(O) | 12 | LETCHER | The surveyor for the construction company set an erroneous benchmark which led to the bridge being constructed at the wrong elevation. The engineer did not tie into existing KYTC’s vertical control point when setting the benchmark; instead, the benchmark’s vertical control was based on GPS data point obtained the by construction company’s engineer. | Once the error was discovered, adjustment were made to compensate bridge’s elevation. It is advisable to use established control instead establishing new control where possible.
2017-09-28 | Geotechnical | Investigation | RELOCATION(O) | 12 | LETCHER | On the plans, five settlement platforms were located in the driving lanes. As designed, they would have interfered with roadway construction due to their height above roadbed level. | After consultation with the Geotech Branch, the settlement platforms were cut off below pavement level.
2017-09-28 | Design | Evaluations | RELOCATION(O) | 12 | LETCHER | Additional excavation in the roadway rock cut section slope, near the end of the project (adjacent to future project, Section 5), could have been taken out at the contract unit price but Central Office denied D12’s request to perform the work. It was stated that this excavation will be needed for Section 5 construction and would have been far less expensive since it could, at the time, be done without traffic control. It will likely be significantly higher to excavate (perhaps several dollars higher per cubic yard) under the next contract. | More forethought during project development may have alerted designers to this possibility, although that can’t be stated with complete certainty.
2017-09-28 | Geotechnical | Unsuitable Material | RELOCATION(O) | 12 | LETCHER | Plans called for excavating soft unsuitable material prior to roadway embankment fill. This could not be accomplished because it required excavation to be lower than the elevation of an adjacent creek. Still, the area did require subgrade improvement prior to embankment fill. | The soft material was “pushed out” (instead of excavated) away from the roadway embankment area. It was approved by central office geotech personnel to install geogrid to increase the subgrade capacity to an acceptable strength.
2017-09-28 | Geotechnical | Slides | RELOCATION(O) | 12 | LETCHER | A slide developed at a haul road location above the roadway cut section. Slide material kept moving downward towards the roadbed level. D12 construction personnel requested that all of this material be taken out, but that did not occur. This will be an ongoing maintenance issue for years to come unless fixed. (At this time no plans are in the works to address this slide.) | Removal of the material or construction of ditches to keep the water off of this area will stabilize the area.
2017-09-28 | Geotechnical | Subsurface | RELOCATION(O) | 12 | LETCHER | A coal seam was encountered during abutment excavation activities; the coal seam will not provide adequate bearing capacity to support the abutment. This could not have been anticipated. | The coal seam was removed and mass concrete placed to design grade. This provided for an adequate subgrade location for the abutment.
2017-09-28 | Structures | Reinforcement Steel | RELOCATION(O) | 12 | LETCHER | Bridge Number (#25292@ Sta. 51+708.5) the reinforcement steel as specified (side to side) in the plans were two feet too long. (It was speculated by D12 that this bridge and another bridge approximately 193 feet down baseline were designed on slightly different skews. Because they were similar designs, D12 thought perhaps as a matter of design expediency, both bridges called for the same lengths for reinforcement steel (side to side.) However, in the field side to side reinforcement lengths for one bridge was not the same for the other bridge due to the slight difference in skews. Exact reason for the error is not known. | A change order was issued and the steel reinforcement members were sawed off to the proper lengths. It was stated that this was the most prudent corrective measure possible.
2017-09-28 | Design | Slopes | RELOCATION(O) | 12 | LETCHER | The plans called for a vertical highwall (i.e. without benches) in a roadway cut section. It was stated that this was difficult, if not impossible to build. Moreover, even if it was built as designed, it would have led to long-term stability and maintenance problems. | A change order was issued to construct benches at this location. This provided for a more stable cut section and will allow future cuts on the next construction project most effectively.
2017-09-28 | Structures | Omission | RELOCATION(O) | 12 | LETCHER | The culvert design drawings were extremely vague which led to numerous problems during construction. There was no wing wall laid out, no reinforcement bars listed and no spiral steel listed. The plans erroneously called for AA concrete as well. | A re-design of the culvert(s) occurred during the construction phase. Better plan review during plan development would have prevented these problems.
2017-09-28 | Structures | Bridge Deck | RELOCATION(O) | 12 | LETCHER | Due to poor machine control and setting the reinforcing steel too high, the contractor’s foreman built the deck up to three inches too thick, overrunning the plan quantity for concrete by 60 cubic yards. It was noted that the contractor did a dry run, but during the pour the contractor kept adjusting the machine up without approval. | The contractor should have had better quality control on steel placement. The contractor should have caught potential errors prior to the pour.
2017-03-28 | Utilities | Plans | SAFETY(P) | 11 | KNOX | The utility design consultant made an erroneous relocation of KYTC storm sewer in an AutoCAD drawing; the storm sewers were erroneously moved to a new datum (elevation.) This error created numerous problems during construction activities because the utility plans, as drawn, were in conflict with the existing water lines. | The utilities were redesigned as construction proceeded. D11 stated it took a long time to get the storm sewers worked out and they were still were not quite to the functionality they would have preferred. A change order was issued to provide for an incentive to the contractor to complete this work as quickly as possible.
2017-03-28 | Geotechnical | Subsurface | SAFETY(P) | 11 | KNOX | Although there was subgrade issues anticipated in design, these were much more severe than planned. As designed, only one-foot of crush stone aggregate No 2 was setup, but it was determined that two and sometimes three feet of aggregate base along with geogrid was needed to construct a stable subgrade. Consequently, this also required additional excavation of soft soil material (saturated brown soil) to be removed that was not included in the plans. It was noted that, “visually” the existing road did not exhibit problems (e.g. base failure) and therefore it was a surprising discovery as to the amount subgrade preparation it took to rebuild the road. | A change order was issued to include geogrid in the contract and to additional quantities of crush stone aggregate No. 2 and excavation. As the subbase was being constructed, field decisions were made regarding the thickness of the crush stone placement and whether to place geogrid.
2017-03-28 | Design | CAP | SAFETY(P) | 11 | KNOX | To improve traffic management at the intersection of KY 6 & 1487, the plans called for restricting access to the Stop & Go Market from KY 1487. The primary design objective was to prevent cars from cutting though the store’s parking lot to make right-hand turns from KY 1487. An erroneous construction revision was made, whereby the restricted access as designed was altered after complaints about this restriction were made by the store owner. This resulted in the relocation of a drop box inlet that allowed access from KY 1487 into the parking lot. As noted, during plan development an agreement was reached with store owner for this design (i.e. access restriction) but this agreement was not in the CAP notes. | Communication with the design branch by construction management personnel, may have prevented this erroneous revision. Better QA/QC to ensure the CAP notes describing this agreement may have reinforced the design objective.
2017-03-28 | Design |  | RECONSTRUCTION(O) | 11 | WHITLEY | The time frame of 60-days to build the bridge was extremely limited. District design set it up this way to complete work prior to start of school year at the University of the Cumberlands campus. | Ultimately a 30-day extension was granted due to the extra work associated with the unsuitable material encountered. The contractor stated that had the extended time not been granted, it was doubtful the project could have been done in the 60-day time frame. The contractor stated it would have been idea for a three sided culvert to expedite the work.
2017-03-28 | Design | Drainage | SAFETY(P) | 11 | KNOX | It was determined very late in the design phase that the parking lot couldn’t be level (i.e. the parking lot elevation couldn’t change) with the road. This left a steep, potentially unstable slope between the parking lot and adjacent sidewalk but no provisions were in the plans to address this problem. | A change order was issued for a 3.5 feet tall concrete gravity wall. This provided for stabilization of the parking lot and prevented it from sloughing off into the newly constructed sidewalk.
2017-03-28 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 11 | WHITLEY | The one-foot depth of aggregate placement as called for in the plans was not enough to construct a stable subgrade. Unsuitable foundation material was encountered between stations 107+00 to 110+00 / 121+00 to 123+00 which required an additional two-feet of excavation and crushed aggregate placement above what was depicted in the plans. | A change order was issued to accommodate for an additional two feet of undercut and placement of crushed aggregate Size No. 2. (As a side note to the discussions, it was recommended that geogrid when used, can save money and time; It can save both on excavation and aggregate needed to construct a suitable subgrade. However, it was not used on this project)
2017-03-28 | Design | Communication | RECONSTRUCTION(O) | 11 | WHITLEY | The plans did not reflect the construction memorandum 01-13 that directs payment for quantities of aggregate and filter fabric for temporary construction entrances. District design stated that they were unaware of this this memos and therefore these quantities were not setup in the plans. It was stated that D11 Project Development does not receive construction memo via email when they are issued. | A change ordered was issued to include these quantities. It was also noted that the district decided to use Class II aggregate instead of No. 2 Stone. The larger aggregate provide better bearing capacity for the large construction vehicles. Central Office Construction Branch should consider emailing newly issued construction memos to district design branch managers.
2017-03-28 | Design | Safety | RECONSTRUCTION(O) | 11 | WHITLEY | The plans did not call for wing barrier walls / fencing next the sidewalks on either side of the bridge to protect pedestrians from the adjacent 30-foot drop-off. This was considered a safety issue by construction personnel. | The construction branch decided wing barrier walls with fencing were needed on all four corners of the bridge. A change order was written to include concrete, fencing and other items needed to construct these features.
2017-03-28 | Design | Plans | RECONSTRUCTION(O) | 11 | WHITLEY | There was an existing pipe on the drawings that its diameter was incorrectly noted. As designed the erroneous diameter noted on the plans led to the incorrect size headwall being delivered to the site. This pipe was larger than the headwall and therefore could not be installed. | A section of the pipe was removed and no headwall was installed.
2017-03-28 | Drainage | Pipes | RECONSTRUCTION(O) | 11 | WHITLEY | As designed, a 54-inch diameter corrugated metal pipe (CMP) was installed between stations 115+00 to 123+00 LT. for storm sewer. Some district personnel felt it should have been a reinforced concrete pipe (RCP) instead. As stated, it will not be durable enough and will be “rusted out in 30 years.” Consequently, this will lead to failing curb and gutter above it, along with drainage problems as the pipe will be subject to collapsing. | Install a RCP instead of a CMP. RCP’s are significantly more durable than CMP as stated by district personnel. See Comment #1.
2017-03-28 | Design | Guardrail | SAFETY(P) | 11 | HARLAN | There was a special note on the plans that called for 9” x 9” wooden posts only to be used to mount the COR-TEN (weathering steel) guardrail. The contractor bid the job anticipating these posts could be installed by being driven. However, it was realized during construction that the wooden posts could not be driven into the rock cut sections or hard rock fill (basically entire length of the road). | As a result, all wooden posts were installed by drilling holes for each one (approximately 850 posts). There needs to be a revised note put in plans that states that steel COR-TEN W beams will be allowed in place of wooden posts. This will allow bidders to consider this when submitting bid packages. It was noted that these can be driven and are much less expensive than wooden post installation in this scenario. The district was willing to switch to COR-TEN W beams in place of the wood posts for this project, but the supplier could not get them in a timely manner.
2017-03-28 | Geotechnical | Slides | SAFETY(P) | 11 | HARLAN | A small slide occurred between LT. Sta. 310+00 (uphill side of road) that began to threaten the road and ditch line. | A change order was issued to pay for the removal of the slide material, aggregate backfill and filter fabric placement to serve as a toe buttress.
2017-03-28 | Design | Quantities | SAFETY(P) | 11 | HARLAN | The quantities as setup in the contract for shoulder asphalt base were insufficient. As stated, it was likely attributed to numerous late changes in the plans but the exact reason for this error is unknown. | A change order was issued to provide for the required asphalt base as needed. Additional QA/QC may have caught this error before plan finalization.
2017-03-28 | Geotechnical | Investigation | SAFETY(P) | 11 | HARLAN | There were numerous redesigns due to several geotech drilling and data collection efforts. It was noted that this slowed the design of the project (approximately 18 months) due to ongoing recommendation revisions from the Geotech Branch. Furthermore, it was stated that geotech is a “recommendation” but for this project was treated like a directive. | As noted, the district should have requested geotech assistance earlier in the design phase. It is important for designers to realize they have leeway to make design different from the geotech recommendations.
2017-03-28 | Design | Drainage | SAFETY(P) | 11 | HARLAN | As designed, a 24-inch pipe was installed at Sta. 338+75 to carry drainage from the right-of-way towards CR 1073. However, the drainage from the newly installed 24-inch pipe flowed to a smaller downstream 15-inch pipe beneath CR 1073. This caused a drainage problem at one of the nearby homes, whereby a basement was flooded with water and silt. The district noted this drainage situation should have been addressed prior to finalizing the plans. As noted, the project manager that was originally responsible for plan development, left the cabinet prior to completion of the final plans. It was then assigned to a new project manager who finalized the plans which included an important matter of addressing another critical issue. This along with the pressure to complete the design, diverted attention away from the downstream undersized 15-inch pipe. | A change order was issued to replace the 15-inch pipe under CR 1073 with a 24-inch diameter pipe. The contractor provided assistance to the property owner to address the property damage caused by the water and silt.
2017-03-28 | Environmental | Underground Tank | SAFETY(P) | 11 | KNOX | During utility relocation efforts, an underground storage tank (containing fuel) was unexpectedly discovered. As required by law, special handling of the tank and fuel was needed but no provisions were setup in the plans. | KYTC contacted the Kentucky Underground Storage Tank Branch (UST), who dispatched their mitigation team. A private contractor who routinely works for UST was hired to properly remove and dispose of the tank and fuel. This work was paid for by an approved change order under the roadway contract.
2017-02-28 | Design | Evaluations | BRIDGE REPLACEMENT(P) | 8 | ROCKCASTLE | The plans called for gabion baskets to be installed to direct stream flow away from the new upstream bridge abutment as an erosion control measure. District personnel were concerned about long term stability of the gabions, as well as maintenance issues associated with them. | A change order was issued to switch from gabion baskets to cyclopean stone to serve as the protective erosion control measure. District personnel stated that cyclopean stone would be much easier to maintain than gabion baskets.
2017-02-28 | Geotechnical | Subsurface | SAFETY(P) | 8 | MCCREARY | Pavement structure failure occurred after the final base was placed, beginning at station 14+50 to 17+00 Lt. Cracks in the pavement began developing shortly after this area began receiving traffic. | The area was undercut by two feet French Drain containing crushed aggregate size No. 2 wrapped in geotextile type IV was installed in the undercut area. This provided a stable subgrade suitable for road reconstruction.
2017-02-28 | Geotechnical | Subsurface | SAFETY(P) | 8 | MCCREARY | The subgrade from approximate station 11+00 to 17+00 Rt. was subjected to groundwater infiltration from the adjacent roadway cut. The subgrade was clay material, that was saturated due to this infiltration and it was not suitable for road construction. | Approximately 600 linear feet of one-foot thick crush aggregate size No. 2 wrapped in geotextile type IV (i.e. French Drain) was installed just beneath the ditch line. This drained the groundwater and allowed the clay subgrade to dry. It was then suitable for road construction.
2017-02-28 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 8 | ROCKCASTLE | The existing water lines were not moved prior to the letting as originally discussed with the utility company. (This type of utility problem has been a routine occurrence on many projects.) | A change order was issued to allow the prime contractor to oversee utility work for a 5% handling fee. The prime contractor chose the lowest bid from a qualified subcontractor who did the actual relocation work.
2017-02-28 | Design | Communication | BRIDGE REPLACEMENT(P) | 8 | ROCKCASTLE | Initially, the district had this bridge project bundled together with two other nearby (within a few miles) bridge replacement projects. All three of these projects had plan, line and grade completed by the design consultant. Then it was discovered the Rural Roads program issued funds directly to Rockcastle County to replace two of these bridges. No coordination or communication occurred between Rural Roads and the normal KYTC process. (A similar experience in District 2 was mentioned by a former location engineer at the meeting.) | Once this quasi-redundancy was discovered, District 8 reached out to Rural Roads and assumed complete control of these two projects. Ultimately, all three were bid separately and administered by District 8.
2017-02-28 | Erosion Control Plan | Slope Protection | SAFETY(P) | 8 | MCCREARY | District construction personnel were concerned about the potential for washouts of seeding and straw mulching on the long fill slopes. This was a short project (approximately two and half months), and as such the contractor would not be on site to redo washed out areas after completion. | A change order was issued to include erosion control blanket (ECB). ECB placement would prevent washouts during rain events and therefore would eliminate additional revegetation efforts.
2017-02-28 | Construction | Revisions | SAFETY(P) | 8 | MCCREARY | The contractor requested to install a concrete curb in lieu of the asphalt wedge curb that was set-up in the contract. The district stated that the contractor’s request was likely precipitated by a desire to use a subcontractor, minimal profit and installation difficulties associated with this feature. | A change order was issued to switch from asphalt to concrete. The district noted that it was proposed by the contractor at the same unit price, so there was no additional cost for this item.
2017-02-15 | Pavement | Ride Quality | PAVEMENT REHAB-PRI(P) | 6 | BOONE | The placed concrete pavement did not meet the minimum rideability standards. District personnel stated that due to a tight time frame, (placement on weekends) a high early strength concrete was used and small sections were done so it could be ready for the traffic flow on Monday. The type of concrete used and small section placement both led to rideability issues. | A diamond grinder was use to smooth out the main-line concrete pavement only (not turning lanes) to acceptable rideability. This was done at the contractor’s expense as required by contract. The district considered closing US 42 but this idea was not implemented due to heavy truck volumes traveling to Industrial Road (State Rt. 1829).
2017-02-15 | Pavement | Ride Quality | CONGESTION MITIGTN(O) | 6 | BOONE | The placed concrete pavement did not meet the minimum rideability standards. District personnel stated that due to a tight time frame, (placement on weekends) a high early strength concrete was used and small sections were done so it could be ready for the traffic flow on Monday. The type of concrete used and small section placement both led to rideability issues. | A diamond grinder was use to smooth out the main-line concrete pavement only (not turning lanes) to acceptable rideability. This was done at the contractor’s expense as required by contract. The district considered closing US 42 but this idea was not implemented due to heavy truck volumes traveling to Industrial Road (State Rt. 1829).
2017-02-15 | Maintenance of Traffic | Shoulders | CONGESTION MITIGTN(O) | 6 | BOONE | The design called for a six-inch gap between the existing pavement and the widen section in phase one. Construction personnel were concerned about the drop-off this created. This could lead to vehicle damage and/or an accident should a tire enter this gap. | The pavement in phase one was place entirely to the edge of the existing pavement thereby eliminating this drop-off. In phase two, the top pavement layer was removed to create an edge key.
2017-02-15 | Pavement | Approaches | PAVEMENT REHAB-PRI(P) | 6 | BOONE | The plan at the I-75 southbound on/off ramp approaches was to be rehabbed with new asphalt; due to significant ruts in the existing pavement, district maintenance staff was concerned that trucks would rut the new pavement. | A change order was issued whereby these ramp approaches rehabbed with concrete. Concrete will provide for increased longevity and less maintenance versus asphalt.
2017-02-15 | Maintenance of Traffic | Shoulders | PAVEMENT REHAB-PRI(P) | 6 | BOONE | The design called for a six-inch gap between the existing pavement and the widen section in phase one. Construction personnel were concerned about the drop-off this created. This could lead to vehicle damage and/or an accident should a tire enter this gap. | The pavement in phase one was place entirely to the edge of the existing pavement thereby eliminating this drop-off. In phase two, the top pavement layer was removed to create an edge key.
2017-02-15 | Maintenance of Traffic | Striping | CONGESTION MITIGTN(O) | 6 | BOONE | This project was originally setup to use black tape to mark out all the striping on the east side of I-75 which provided for continually changing lanes shifts each weekend or night. District construction personnel felt this was not safest plan available. | A safer MOT plan was implemented as proposed by the Contractor. This led to a change order being issued to water blast off all of the existing striping and install temporary stripping. This provided for constant traffic patterns for the traveling public thus increasing safety in the work zone. This revision also generated a significant savings of over $36,000.00
2017-02-15 | Construction | Layout | PAVEMENT REHAB-PRI(P) | 6 | BOONE | This contract included two separate projects. US 42 Rehab and Mall Road intersection improvements were designed in different coordinate systems. US 42 was done under KY Single Zone and Mall Road was done under KY North Zone. This led to an initial layout error by the contractor’s surveyor whereby a small amount of pipe was set in the wrong location. Apparently, the data collector being used was not set in the correct coordinate system. | The data collector was reset in the proper coordinates system and layout work continued. Pipe was pulled up and reinstalled in the proper location. This was done at the contractor’s expense. It is noted since October 2009, all KYTC mapping is done in KY Single Zone system.
2017-02-15 | Maintenance of Traffic | Striping | PAVEMENT REHAB-PRI(P) | 6 | BOONE | This project was originally setup to use black tape to mark out all the striping on the east side of I-75 which provided for continually changing lanes shifts each weekend or night. District construction personnel felt this was not safest plan available. | A safer MOT plan was implemented as proposed by the Contractor. This led to a change order being issued to water blast off all of the existing striping and install temporary stripping. This provided for constant traffic patterns for the traveling public thus increasing safety in the work zone. This revision also generated a significant savings of over $36,000.00
2017-02-15 | Pavement | Approaches | CONGESTION MITIGTN(O) | 6 | BOONE | The plan at the I-75 southbound on/off ramp approaches was to be rehabbed with new asphalt; due to significant ruts in the existing pavement, district maintenance staff was concerned that trucks would rut the new pavement. | A change order was issued whereby these ramp approaches rehabbed with concrete. Concrete will provide for increased longevity and less maintenance versus asphalt.
2017-02-15 | Pavement | Repair | CONGESTION MITIGTN(O) | 6 | BOONE | Once the main-line concrete pavement was diamond grinded, this led to aesthetics and drainage issues. Both the public and local officials were complaining about these problems. | A change order was issued to diamond grind the turning lanes so it matched the mainline concrete pavement (a perceived aesthetic improvement) AND allow the entire roadway (mainline & turning lanes) to drain appropriately.
2017-02-15 | Pavement | Repair | PAVEMENT REHAB-PRI(P) | 6 | BOONE | Once the main-line concrete pavement was diamond grinded, this led to aesthetics and drainage issues. Both the public and local officials were complaining about these problems. | A change order was issued to diamond grind the turning lanes so it matched the mainline concrete pavement (a perceived aesthetic improvement) AND allow the entire roadway (mainline & turning lanes) to drain appropriately.
2017-02-15 | Structures | Guardrail | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Island Header Curb was left off of the design plans but it was needed as is an integral part of the guardrail system. District personnel stated without this item the system is NOT crash worthy. Erroneous omission of this item is a “fairly common occurrence” as stated by D6 personnel. | A change order was issued to include the Island Header Curb. The system was properly installed to make it crash worthy.
2017-02-15 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | At the beginning of bridge construction, an old bridge abutment was discovered and did not allow for the new bridge abutment #2 to be constructed at the design location. This prevented the bridge abutment from being built as designed. | Geotech was contacted and additional core drilling was performed. It was determined that old bridge abutments existed at BOTH proposed abutments #1 and #2 locations. With new geotech information, KYTC/district personnel determined that the bridge could be shifted 5 feet south from the design location.
2017-02-15 | Structures | Coordination | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Due to the historic value of existing truss bridge, by law the bridge could not simply be demolished to make room for the new bridge. As such, it is a requirement to advertise in local newspaper(s) to inform that public of its existence so to find possible uses by other public entities. (It was stated that only about 200 truss bridge exist in the Kentucky.) | Information was put in the local paper as required by law. However, it was a causal conversation between the Bracken County Judge Executive and the Henderson County Judge Executive that was responsible for Henderson County taking ownership of the bridge. An agreement was worked out between, KYTC, Henderson County officials and contractor to transport the bridge to Henderson County for use on a reclamation project. It may be helpful to have an established clearinghouse to share with all county judges and mayors.
2017-02-15 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Field conditions did not allow for Guardrail End Treatment Type 7 to be installed as depicted in the plans. There was not 25 feet as required to install this feature—it was too close to the wing walls on the adjacent railroad tunnel. | A change order was issued for the installation of Guardrail Terminal Section No. 1 to be used in its place.
2017-02-15 | Construction | Layout | CONGESTION MITIGTN(O) | 6 | BOONE | This contract included two separate projects. US 42 Rehab and Mall Road intersection improvements were designed in different coordinate systems. US 42 was done under KY Single Zone and Mall Road was done under KY North Zone. This led to an initial layout error by the contractor’s surveyor whereby a small amount of pipe was set in the wrong location. Apparently, the data collector being used was not set in the correct coordinate system. | The data collector was reset in the proper coordinates system and layout work continued. Pipe was pulled up and reinstalled in the proper location. This was done at the contractor’s expense. It is noted since October 2009, all KYTC mapping is done in KY Single Zone system.
2017-02-15 | Maintenance of Traffic | Phasing | CONGESTION MITIGTN(O) | 6 | BOONE | The original MOT plan called for two US 42 eastbound lanes approaching the intersection with Mall Road in phase one of construction. The right lane was a straight through lane and the left lane was a straight/left turn combo lane. District personnel stated this was not the best MOT plan based on two reasons: • The original MOT plan will cause motorist to have to “quickly” merge into one lane just after crossing the intersection, as only one lane is proposed on the east side of the US 42/ Mall Road intersection. This creates a safety concern for motorist and workers. • There is no protected left hand turn phase included in the straight/left turn combo lane. This will create traffic backups during heavy US 42 west bound on-coming traffic, as it will impede motorists turning left. | A MOT revision request was submitted by district personnel and was approved for phase one construction. It requested the eastbound straight/left turn combo lane be turned into a left turn only lane with a protect phase. This guided motorists to decide prior to the Mall Road intersection, to choose either the right straight through lane OR the left-hand turn lane.
2017-02-15 | Design | Omission | CONGESTION MITIGTN(O) | 6 | BOONE | There were two quasi-triangular shaped slivers located on US 42 just west of the intersection with Mall Road; one was located 8 feet north and one was located 10 feet to the south (both from station 50+90 to 52+80.) Both of these needed work and should have been included in one of the construction phases. However, neither area was included in any phase. | A MOT revision requested during construction phase one was submitted by district personnel and was approved. Traveling eastbound on US 42 towards the intersection with Mall Road, it requested the eastbound straight/left turn combo lane be changed into a left turn only lane. This allowed shifting (northerly direction) the eastbound lane earlier thereby providing additional area to rehab the south sliver. During construction phases two and three, MOT revisions were submitted by district personnel and were approved. This similarly provided additional area in phases two and three to rehab the north sliver. It was noted that most of the north silver was addressed in phase three.
2017-02-15 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-PRI(P) | 6 | BOONE | The original MOT plan called for two US 42 eastbound lanes approaching the intersection with Mall Road in phase one of construction. The right lane was a straight through lane and the left lane was a straight/left turn combo lane. District personnel stated this was not the best MOT plan based on two reasons: • The original MOT plan will cause motorist to have to “quickly” merge into one lane just after crossing the intersection, as only one lane is proposed on the east side of the US 42/ Mall Road intersection. This creates a safety concern for motorist and workers. • There is no protected left hand turn phase included in the straight/left turn combo lane. This will create traffic backups during heavy US 42 west bound on-coming traffic, as it will impede motorists turning left. | A MOT revision request was submitted by district personnel and was approved for phase one construction. It requested the eastbound straight/left turn combo lane be turned into a left turn only lane with a protect phase. This guided motorists to decide prior to the Mall Road intersection, to choose either the right straight through lane OR the left-hand turn lane.
2017-02-15 | Design | Omission | PAVEMENT REHAB-PRI(P) | 6 | BOONE | There were two quasi-triangular shaped slivers located on US 42 just west of the intersection with Mall Road; one was located 8 feet north and one was located 10 feet to the south (both from station 50+90 to 52+80.) Both of these needed work and should have been included in one of the construction phases. However, neither area was included in any phase. | A MOT revision requested during construction phase one was submitted by district personnel and was approved. Traveling eastbound on US 42 towards the intersection with Mall Road, it requested the eastbound straight/left turn combo lane be changed into a left turn only lane. This allowed shifting (northerly direction) the eastbound lane earlier thereby providing additional area to rehab the south sliver. During construction phases two and three, MOT revisions were submitted by district personnel and were approved. This similarly provided additional area in phases two and three to rehab the north sliver. It was noted that most of the north silver was addressed in phase three.
2017-01-31 | Design | Evaluations | MINOR WIDENING(O) | 7 | MADISON | The elevations on the plans did not match field conditions. A cross drain (pipe) was installed as designed but once installed it was discovered that the inlet invert elevation of an existing “downstream” pipe that was to accept drainage was 3 feet too high. (It was unknown whether the inlet invert elevation of the existing pipe was surveyed in the design phase—the reason for this error was not known.) | The drainage from the cross drain was re-routed in a roadside ditch in a westerly direction toward Village Drive. The installed cross drain was safe loaded to prevent future problems.
2017-01-31 | Geotechnical | Subsurface | MINOR WIDENING(O) | 7 | MADISON | There were no provisions in the plans to address weak subgrade conditions that existed in the roadway. It was noted that the LPA-hired consultant did not perform or request any geotech during plan development. Therefore, no asphalt cores or subsurface data was collected which would have alerted designer to the poor subsurface conditions. | After the project was let, KYTC construction staff contacted geotech who immediately suggested subgrade stabilization. A change order was issued for No. 2 crushed aggregate and fabric-geotextile type IV. The roadway was undercut whereby aggregate and filter fabric were installed. It was noted that some areas had to be undercut a second time to increase the aggregate base 2 feet depth in the mainline to provide for adequate subgrade strength.
2017-01-31 | Pavement | Design | MINOR WIDENING(O) | 7 | MADISON | To make the plan profile, the plans called for six inches of milling but there was only eight inches of asphalt existing which was not enough base to support the new pavement. | The district decided not to mill the pavement. It was overlaid only.
2017-01-31 | Design | Safety | MINOR WIDENING(O) | 7 | MADISON | Installed headwalls on the 15 inch diameter CMP at the entrance to the power substation (left of approximate station 12+75), were higher than the roadway. As such, KYTC construction staff determined they posed a roadside safety risk for motorist. | D7 staff decided to remove the headwalls. It was concluded that it would be safer to hit the pipe rather than a headwall.
2017-01-31 | Drainage | Pipes | MINOR WIDENING(O) | 7 | MADISON | Existing twin 48 inch diameter CMPs cross drains were to be extended with additional 48 inch diameter circular CMPs on the north side of the KY 595 to provide for widening. However, once the existing pipes were excavated, it was discovered that they were not circular shaped due to deflection. It was noted that the existing pipe were originally circular shaped. This did not allow the new extension pipes to be directly installed as planned. | The contractor was able to deflect the extension pipes with pressure from a backhoe until they took the shape of the existing pipes, then they were able to fit onto the ends of the existing pipes. It was also noted that dual pipes are more difficult to maintain as they are subject to collecting debris and are not self-cleaning; district personnel stated that completely replacing the cross drain with a reinforced concrete box culvert would have been best in the long run. The design plans should have installed a single RCBC to replace the pipes.
2017-01-31 | Design | Safety | MINOR WIDENING(O) | 7 | MADISON | Roadside safety concerns exists at the 48” diameter cross drain location for two reasons. First, the twin 48 inch diameter CMPs extension headwalls were too high and above the roadway. Also the roadside embankment was steep (2:1 or so) which caused roadway safety concerns too. | A guardrail was installed at this area to prevent motorist from hitting the headwalls and/or traversing an unrecoverable slope.
2017-01-31 | Traffic | Coordination | MINOR WIDENING(O) | 7 | MADISON | Positive offset turn lanes (POTL) were not part of the plans but were added during striping after the road was built. In part, because POTL’s were not part of the plans, this caused reduced shoulder of less than five feet at these locations. | Once in construction District traffic personnel was consulted and a decision was made to install POTL. The traffic section became involved and highly recommended them at intersection locations on KY 595 within the project limits. During plan development, traffic personnel should have been consulted which may have led to their inclusion in the plans.
2017-01-27 | Geotechnical | Slides
2017-01-26 | Design | Quantities | MAJOR WIDENING(O) | 5 | SHELBY | Large overruns on asphalt base were encountered. A plan review revealed quantities for asphalt to be placed under the median and gutter pan as depicted in the plans, were not included in the quantities. | A change order was issued to include quantities for asphalt as needed to construct these features as depicted in the plans. A more careful review during plan development could have alerted designers to include asphalt quantities for these areas.
2017-01-26 | Design | Shelved Plans | RECONSTRUCTION(O) | 5 | FRANKLIN | The design plans called for an asphalt entrance at 74 C Michael Davenport Blvd (old gas station), but there was a concrete dumpster pad at the top of the entrance whereby large garbage trucks would be traversing. Due to the anticipated loading conditions in this area, asphalt would not be durable enough. It was noted the concrete pad was installed after the design plans were developed. | A change order was issued to use concrete in lieu of asphalt leading to the dumpster pad. (It was noted that the rest of the entrance was constructed with asphalt)
2017-01-26 | Design | Drainage | RECONSTRUCTION(O) | 5 | FRANKLIN | The design plans called for concrete curb installation around two side of a perimeter parking lot at 74 C Michael Davenport Blvd (old gas station), but the plans did not address drainage runoff as a result of the curb installation. | A change order was issued that included milling in the curb installation footprint and placing additional asphalt to help direct parking lot runoff into the new drop box that was installed in the project limits.
2017-01-26 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 5 | FRANKLIN | The storm sewer installation could not be installed using a 24-inch circular corrugated metal pipe (CMP) as called for in the plans. This was due to the vertical clearance required by this pipe as it conflicted with an existing utility gas line. | An elliptical corrugated metal pipe (that required less vertical clearance) was installed instead as it was able to pass beneath the existing line. It was noted that the elliptical pipe’s hydraulic capacity was equivalent to the 24-inch diameter circular CMP.
2017-01-26 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 5 | FRANKLIN | There were 54 utility lines located within the project limits, some were known and some were discovered during work activities. This created work slowdowns and/or stoppages until it could be determined if they were alive or dead and what approach to take regarding them. | Utility lines that were in use, were relocated or repositioned to allow for proper road construction. It was stated that the prime contractor, sub-contractor and district personnel worked very well together addressing these problems in an efficient manor.
2017-01-26 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 5 | FRANKLIN | Throughout the project area, weak subgrade conditions were encountered. These areas were unable to properly support road construction in their existing condition. These weak subgrade conditions in part, were due to the vast number of underground utility lines. | A change order was issued for crush aggregate No. 2 and geogrid reinforcement to strengthen the subgrade to an acceptable level for road construction. (It was also stated that chemical stabilization (CS) could have been used instead but was not chosen as the preferred method. CS was not chosen due to the small size of the project and the amount of traffic moving through the area—aggregate subgrade enhancement is a quicker way to stabilize poor subgrade thus friendly to MOT.)
2017-01-26 | Design | Shelved Plans | RECONSTRUCTION(O) | 5 | FRANKLIN | Field conditions changed during period between plans development and construction activity (approximate 8 years). The Augusta subdivision located on the northwestern side of the project area built a berm for road noise reduction. As drawn, this led to slope transition problems regarding the berm and trees on top of the berm. | The slopes were steepened to tie into the adjacent subdivision property and eliminate the need to remove the berm and trees (Disturbance of the trees and/or berm would have been unacceptable to the property owners.)
2017-01-26 | Design | Omission | RECONSTRUCTION(O) | 5 | FRANKLIN | The design plans called for installation of a new entrance into an existing parking lot at the commercial building located at 73 C Michael Davenport Blvd. However the plans did not address the existing curb nor additional asphalt needed to properly address its installation. | The parking lot and entrance design was modified. The concrete curb was jack hammered out and additional asphalt was placed to properly construct the new entrance.
2017-01-26 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 5 | SHELBY | Wet weather springs and old utility lines were encountered during road construction which created a soft unsuitable foundation for soil embankment as designed. It was noted that utility companies often inadequately backfill and compact when placing lines across a road, causing soft spots. | A change order issued for additional granular aggregate embankment to be used in lieu of soil embankment at these locations.
2017-01-26 | Maintenance of Traffic | Quantities | MAJOR WIDENING(O) | 5 | SHELBY | An insufficient amount of aggregate was setup in the contract to properly maintain temporary entrances to various commercial properties. Rainy weather and large truck traffic accessing the commercial properties caused a higher number of repairs during the winter season. | A change order was written to include the required amount of aggregate.
2017-01-26 | Maintenance of Traffic | Quantities | MAJOR WIDENING(O) | 5 | SHELBY | As part of maintenance of traffic, the plans called for widening a section of existing southbound roadway four to five feet. Once in construction, the width had to be increased to approximately 11 feet due to an approximate 3 foot vertical drop-off not accounted for in the plans. Additional quantities of aggregate and base was required to day-light the 2:1 outslope into the adjacent ditch line. | A change order was written to include the required quantities of base and aggregate to construct the additional lane needed to move traffic.
2017-01-26 | Traffic | Signals | MAJOR WIDENING(O) | 5 | SHELBY | One of the metal signal poles as planned was too close to the existing electrical transmission lines (ETL). As designed, the signal pole was to be placed within approximately 13 feet of the ETLs which created a significant arcing risk. (It was noted that a 20 feet minimum distance between metal poles and transmission lines are required.) | A change order was written to switch to a wooden pole which eliminated the arcing risk. Examination of the utility sheets may have alerted Traffic to this problem.
2017-01-26 | Design | Shelved Plans | MAJOR WIDENING(O) | 5 | SHELBY | The bridge design elevation as constructed over Norfolk Southern railroad did not meet the minimum clearance of 23 feet as required. The design elevation for the bridge was established approximately 8 years prior to its construction. Between the time of the bridge design and construction, the rail line was raised by Norfolk Southern. This caused the “as designed” elevation to be approximately four inches too low to meet the clearance requirement. | District personnel contacted Norfolk Southern and discussed the clearance situation. Norfolk Southern issued a variance to the district which allow the bridge clearance to remain as constructed. Because of the long time between design and construction phases, a survey to check current conditions could have alerted KYTC of this situation.
2017-01-26 | Construction | Delays | MAJOR WIDENING(O) | 5 | SHELBY | Bridge contractor was not working at a significant pace to keep the project on schedule. Bridge construction was seven months behind the anticipated schedule. | The prime contractor met regularly with the bridge contractor (prime’s sub) in an effort to get them to operate more efficiently. It was stated that the prime contractor (Louisville Paving) is no longer doing business with this particular bridge contractor. District members suggested that KYTC develop a “more enhanced” pre-qualification system for contractors that would prevent poorly performing companies from bidding or working on KYTC projects. It was noted that legal challenges would have to be addressed to prevent poorly performing construction enterprises from merely changing company names to circumvent the intent of a pre-qualification system.
2017-01-26 | Utilities | Relocation | MAJOR WIDENING(O) | 5 | SHELBY | Time Warner utility lines were relocated to the wrong location by the Time Warner contractor twice. | After the second erroneous relocation, Time Warner relocated them correctly on the third time as depicted in the plans. More careful attention to the plans may have prevented these errors by Time Warner.
2016-11-16 | Geotechnical | Cut-Slope | RECONSTRUCTION(O) | 4 | HART | The geotech report did not depict or describe poor soil quality that existed in a cut slope from Station 1836+50 to Station 1839+50. There was concern that the slope would fail as constructed. | It was decided to construct a concrete retaining wall to provide for slope stability. A change order was issued for the necessary construction items.
2016-11-16 | Geotechnical | Quantities | RECONSTRUCTION(O) | 4 | HART | The geotech report overestimated the amount of durable sandstone there would be available to use for embankment. It was discovered that the majority of sandstone that was to be used was severely weathered sandstone. The roadbed could not properly be constructed with this material. | In lieu of excavated sandstone, crush aggregate was used in its place. A change order was issued to add Crushed Aggregate Size No. 2 to construct the 2 foot roadbed.
2016-11-02 | Utilities | Relocation | SAFETY(P) | 1 | MARSHALL | On-site material that was to be used for embankment for road widening etc., was too soft and unworkable for that purpose. It was stated by district construction personnel that this material was in this state due to trenches dug for utility relocation that were left open all winter. The trenches held water and created the super-saturated soft material by the following Spring. | The material was stabilized using cement to bring it to a workable and suitable material for embankment. A change order was issued for cement stabilization.
2016-11-02 | Construction | Omission | SAFETY(P) | 1 | MARSHALL | When cement stabilization was added to the project (i.e. change ordered), no fuel adjustment compensation (FAC) was included for this item. At the time, district construction management erroneously believed that it was not eligible for FAC. In addition, it was also noted that when the fuel index was first calculated, FAC was calculated erroneously low based on the month the project was finalized (not as is should have been when the work was performed. (It was stated that many times inspectors will not override the fuel and asphalt program to reflect when the work was actually performed.) These errors led to insufficient FAC funds available. | District Construction Office Manager (DCOM) did a green check prior to sending it for final processing in the central office. DCOM verified that cement was eligible for FAC. Also, the index was adjusted to reflect the proper amount of FAC funds to be paid. A change order was issued for the required funds needed for appropriate FAC.
2016-11-02 | Design | Quantities | SAFETY(P) | 1 | MARSHALL | The elevations depicted on the plans on the US 68 side of the project were low by four to six-inches. Also there were church entrances that were not accounted for as well. It is believed either one of these problems, OR perhaps both, led to embankment quantity estimates being too low on the bid tabs. The embankment as setup for US 68 and attached entrances could not be built to the grades as designed. (Exact reason for the embankment quantity error is unknown) | A change order was issued to provide for the additional embankment in place material to raise the roadway grade and asphalt to raise the entrances coming off US 68. Embankment was paid according to the new plan quantity.
2016-11-01 | Design | Slopes | RECONSTRUCTION(O) | 2 | HOPKINS | District construction personnel were concerned about slope protection at Ramp L (Sta. 2025+20 – 2030+58) above an installed gravity wall. | A change order was issued to include an adequate amount of aggregate to achieve the objective of slope protection.
2016-11-01 | Design | Slopes | RECONSTRUCTION(O) | 2 | HOPKINS | A 24 inch pipe (with headwall) as designed left an extremely steep slope above it. There was concern by district construction personnel regarding stability problems and/or maintenance issues that would arise as designed. | A change order was issued to extend the pipe an additional 30 feet to lessen the slope in this area thereby eliminating potential problems from a stability and maintenance standpoint.
2016-11-01 | Structures | Bearing Pad | RECONSTRUCTION(O) | 2 | HOPKINS | During construction, it was determined that 12 bridge bearings were in poor shape but the servicing of them were not previously identified and not included in the RFP. | A change order was issued to clean, remove rust and grease them as needed.
2016-11-01 | Structures | Approaches | RECONSTRUCTION(O) | 2 | HOPKINS | No approach slabs were setup in the RFP but District 2 felt these were needed to provide adequate support at the end of the bridge. Without them the district felt more maintenance would be required at the bridge end bents. | A change order was issued to provide for the slabs. This decision was made to include them after a meeting was held at the district office. The bridge engineer wanted to include them.
2016-11-01 | Structures | Beams | RECONSTRUCTION(O) | 2 | HOPKINS | It was determined that one of the pre-cast pre-stressed concrete beams for Ramp M did not meet the concrete strength as defined in the plans. This led to a dilemma in the field on whether to use the beam or simply reject it. | It was determined by the design consultant that the beam’s strength was acceptable to be used to support the outside shoulder. A construction revision based on the design consultant’s recommendation was issued to allow for a lower strength beam to be installed on the outside edge of the bridge. By being placed on the outside edge, it receives a lower (& acceptable) load than if it was placed in the center of the bridge. It was noted that bridge beams are typically designed based on the greatest load (normally the center of the bridge), then that becomes the specified beam to be used throughout a bridge.
2016-11-01 | Traffic | Coordination | RECONSTRUCTION(O) | 2 | HOPKINS | It was decided by KYTC central office to install overhead truss signage (versus roadside signs) but this was not included in the design-build request for proposals (RFP); therefore, no bid items were included in the project initially but ultimately were needed based on decisions made after the letting. | The original signage was taken out of the project initially, then the desired overhead truss signage was added later per an issued change order. It should have been decided on earlier and put into RFP.
2016-11-01 | Geotechnical | Subsurface | PAVEMENT REHAB-PRK(P) | 2 | HENDERSON | It was stated that 4-inch of asphalt milling as called for on the ramps was too much. Once the amount of existing pavement was milled on two of the four ramps, the base was not structurally suitable subgrade for new pavement placement. (It was thought that no asphalt coring was performed on the ramps) | On the remaining two ramps, 1.5 inches was milled off. This provided for a more stable subbase to work with for repaving. Coring of the ramp pavement during the design phase may have identified the issue.
2016-11-01 | Construction | Communication | PAVEMENT REHAB-PRK(P) | 2 | HENDERSON | During the bidding process a question was mistakenly answered regarding the method of payment for ditching. It was stated that the ditch work would be compensated by plan quantity bid which was not the intended unit price. KYTC is legally bound to the stated answer to the questions posed by contractors during the bidding process. (The intended method was linear feet as stated in the specifications) | Better QA/QC should be considered to ensure answers to questions raised during advertisement are accurate and in harmony with KYTC standards.
2016-10-12 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Excavated material from cut sections was deemed unsuitable for roadbed embankment construction as depicted in the plans. Geotech information regarding the material strength and durability was inaccurate. | A change order was issued to provide for a one foot layer of No. 2 crushed aggregate and filter fabric to be placed over the constructed embankment which allowed for the appropriate roadbed foundation strength.
2016-10-12 | Construction | Revisions | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | A 20 foot extension of a concrete retaining wall was needed, but not enough quantities for reinforcement steel and concrete were on the contract to build. Without the extension wall, there was concern by D10 construction personnel that the KY 30 fill slope above might be subject to fail. | A change order was issued to add the necessary amount of concrete and reinforcement steel to construct the extension. Better QA/QC may have arrived at the need for the small extension in the design phase. Also, a handrail was extended as well due to a sidewalk above the wall.
2016-10-12 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The height of a water hydrant had to be unexpectedly adjusted due to a water line being deeper than the design plans depicted. | A change order was issued to appropriately compensate the contractor for this work.
2016-10-12 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The plans called for bore and jack method for waterline installation but there was no bid item included in the design package. It was stated that this was an omission. | A change order was issued as a pay item for the bore and jack installation method. Better QA/QC may have caught this omission prior to the plans being submitted to construction procurement.
2016-10-12 | Geotechnical | Quantities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Due to an error in the Geotech report, there was not enough suitable material (i.e. embankment volume) for roadbed construction. | A change order was issued to obtain embankment material from an offsite borrow area. The contractor was tasked with finding the borrow area.
2016-10-12 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | There was a note on Sheet S-8 that called for mass concrete installation but there was no bid item setup for this concrete. It was to go from the top of footing to bedrock. | A change order was issued to set up a bid item for the placement of this concrete. The concrete was placed at twice the delivered cost.
2016-10-12 | Drainage | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | There was an existing RCBC that was depicted in the plans to be removed but no bid item was set up for this effort. | A change order was issued for a bid item to have this feature removed. Better QA/QC may have caught this omission prior to the plans being submitted for construction procurement.
2016-10-12 | Maintenance of Traffic |  | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | A safety issue arose at the intersection of Old Buck Road and KY 30 due to the high volume of traffic entering the construction zone opposite of the single direction flow. District personnel became concerned that a head-on collision may occur at the location unless a traffic signal was installed. | An additional temporary traffic signal was installed at the intersection of Old Buck Road and KY 30 (the additional signal created a multiphase signal set up.) A change order was issued to provide for a temporary traffic signal.
2016-10-12 | Design | CAP | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | There was an agreement with a property owner, as stated in a memorandum of agreement, that a concrete steps with handrail would be reconstructed as part of the project. This information was never communicated to the designer. The designers instructed to remove the existing concrete features only. Therefore no depiction in the plans nor were any quantities included in the contract documents for these features. | A change order was issued to add the approximate amount of concrete, steel and handrail to install these features. (Agreements with the property owner need to be put in the CAP notes. Also it was mentioned that more “detail” needs to be included with written agreements with property owners.)
2016-10-12 | Design | Quantities | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | There was not enough cyclopean stone riprap setup on the contract to place it as depicted in the plans. More stone was need to adequately protect the slopes beneath the bridge abutments and surrounding areas. | A change order was issued to increase the amount of cyclopean stone riprap to the appropriate level.
2016-10-12 | Design | Quantities | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | There was not enough asphalt base & crushed stone quantities to repair the roadway that was disturbed to facilitate retaining wall construction. The asphalt base needed to be placed back to maintain traffic flow and accommodate truck turning movements. | A change order was issued for both asphalt base & crushed stone items to repair the roadway as needed.
2016-10-11 | Construction | Permits | PREFINANCD CONVRSN(O) | 12 | LETCHER | One of the three designated waste areas was not used but 200,000 dollars of in lieu fees were paid to the Corp of Engineers (COE) for its use. It is not known by district personnel if these funds can be transferred to another project. | District 12 personnel should notify Division of Environmental Analysis (DEA) so they can contact the COE to determine if these funds can be transferred to another project. (It was mentioned that years ago COE would allow coal companies to bank mediation credits to use on other sites.)
2016-10-11 | Geotechnical | Subsurface | PREFINANCD CONVRSN(O) | 12 | LETCHER | Rock strata beneath abutment #1 was determined not to be adequate foundation for this feature. As designed the abutment was to set directly the rock ledge (without pilings); however, the rock crumbled easily and had water coming out of it which made it an unsuitable foundation. | As recommended by the Geotech personnel during construction activities, HP 12x53 piling was added for abutment foundational support. A change order was issued for the pilings, 12-inch pile points, and drilling needed to install them.
2016-10-11 | Geotechnical | Piling/Drilled Shaft | PREFINANCD CONVRSN(O) | 12 | LETCHER | Permanent casing was needed to keep the drilled 54-inch diameter shafts open but the casing was not called for in the plans. Without permanent casing the concrete piers could not be established in the drilled shafts due to the holes collapsing. | A change order was issued to include permanent casing as part of the drilling bid item. This allowed the shaft to remain open and therefore concrete piers could be established. It was also noted that this project was designed about 15 years ago, and since that time the Geotech Branch began including casing on projects.
2016-10-11 | Design | Communication | PREFINANCD CONVRSN(O) | 12 | LETCHER | No type of guardrail end treatments were depicted on the drawings and therefore the amount of roadside grade work could not be determined at these locations. The type of end treatment dictates the amount of roadside gradework required. | The type of guardrail end treatments (with stationing) needs to be shown on the plans of future grade and drain only projects. This will allow constructors to determine the precise amount of roadside gradework required that is required at these locations.
2016-10-11 | Design | Evaluations | BRIDGE REPLACEMENT(P) | 12 | PIKE | End Bents could not be built on soil as depicted in the design plans and as allowed for in Special Provision 69. It was discovered that one of the end bents was within the 100 year flood elevation and therefore subject to scour. | End Bents were built on durable rock to provide for a scour resistant foundation for the end bents. A change order was written to allow for the durable rock to be used for the foundation.
2016-10-11 | Geotechnical | Elevations | BRIDGE REPLACEMENT(P) | 12 | PIKE | The rock line at Pier #1 was 6 feet lower than as depicted in the plans, which ultimately led to the unplanned installation of a cofferdam. | A change order was written for installation of a cofferdam which allowed the pier to be constructed and seated on solid rock. More geotech data collection may have alerted designers to the actual rock line encountered.
2016-10-11 | Drainage | Existing Pipe | BRIDGE REPLACEMENT(P) | 12 | PIKE | During construction it was decided to safeload existing pipes (rather than remove them) due to the depth and proximity of the Fire Department and City Hall. It was felt that removing them (i.e. excavation & backfilling) as called for in the plans, would be disruptive to Fire Department and City Hall activities. | A change order was issued to provide for mass concrete per the 2012 specifications (Section 601.04.04.) (It was acknowledged by design personnel that this revision was a positive change for this situation.)
2016-10-11 | Design | Omission | BRIDGE REPLACEMENT(P) | 12 | PIKE | The plans depicted removal of the sidewalk but there was no bid item for its removal. It was a design omission. | A change order was issued to provide for a bid item for this effort. This allowed for payment for this work. Better QA/QC may have alerted designers to this omission before letting.
2016-10-04 | Geotechnical | Quantities | SPOT IMPROVEMENTS(O) | 3 | BARREN | Unsuitable subgrade was discovered during earthwork activities and needed to be excavated for proper roadbed construction. This was not depicted in the plans nor addressed in the geotech report. It was noted that many times when a subgrade is two to three feet over bedrock there is likely to be saturation problems (and a need to over excavate), yet geotech often does not address this scenario. | A change order was issued to compensate the additional excavation that was required. All of the unsuitable material was removed and aggregate wrapped in Type IV geotextile fabric was constructed to bring the roadbed to the required grade line. (Obtaining additional geotech data was discussed but no consensus on the how much and/or how much more effective it would be in determining unplanned for subgrade problems.)
2016-10-04 | Utilities | Delays | SPOT IMPROVEMENTS(O) | 3 | BARREN | A separate 9,000-feet water line relocation contract was issued ahead of the roadway contract to properly facilitate subsequent highway construction. Unexpectedly, the newly relocated ductile iron pipe (water line) was degrading and fragments were found in the water samples tested. This precipitated the need for the entire line to be removed and another line installed. However, the road construction contract had been let and initial stages of highway work had begun. The work had to be halted for the water line re-installation which put the KYTC at risk for a damages claim by the highway contractor. | This issue could not have been foreseen. There was a 284-day extension granted at the beginning of highway construction activities. Road construction contract should have not been issued until the new water line was completely tested and approved. (It was noted that the company that produced the pipe went bankrupt and is no longer in business. It was also noted that the contractor did not file a claim, likely because they had other work at the time.)
2016-10-04 | Geotechnical | Quantities | RECONSTRUCTION(O) | 3 | EDMONSON | Not enough quantities were setup to address all unsuitable subgrade that was encountered and required numerous undercuts (i.e. over excavation) for proper roadbed construction. As stated in the geotech note #9, a one foot minimum working platform from shoulder to shoulder shall be constructed at saturated subgrade locations; however, the aggregate and excavation quantities were set up based on the one foot minimum depth and field conditions dictate that more than one foot is needed to provide for an adequate roadbed. It was stated that many times more than one foot is needed. It was stated that overall it is important to have substantial quantities setup to get a reasonable unit bid price which allows for “appropriately priced” modifications at the engineer’s discretion. For this project it was noted that there was enough quantities setup to get a reasonable unit bid price. | A change order was issued to compensate the additional excavation and aggregate that was required. All of the unsuitable material was removed and aggregate wrapped in Type IV geotextile fabric was constructed to bring the roadbed to the required grade line. District personnel generally agreed that inserting quantities of aggregate and excavation based on two or perhaps even three feet depth would yield a more accurate estimate. (Obtaining additional geotech data was discussed but no consensus on the how much and/or how much more effective it would be in determining needed quantities of excavation and aggregate for subgrade problems.)
2016-10-04 | Structures | Beams | SPOT IMPROVEMENTS(O) | 3 | BARREN | There were rideability issues with Fallen Timber Bridge due to the camber of the box beams not completely flattening out when the bridge was upgraded in 1987. This bridge falls within the project limits, however there were no plans to correct this problem. The reason was unknown but attendees speculated because the bridge was relatively young. The length of time between plan development and construction letting was 12 years. It was stated that the bridge was never part of the project scope. | A change order was issued to install a latex concrete overlay on the bridge deck to “flatten it out”, thereby correcting the rideability problem. It was stated that it was now as good as it could possibly be in regards to rideability.
2016-10-04 | Construction | Public Relations | RECONSTRUCTION(O) | 3 | EDMONSON | To facilitate road construction there were disturbances within residential yards but no sod was set up for this project. Seeding can sometimes not establish well which can be upsetting to property owners. | A change order was written to include the proper amount of sod for disturbances in residential yards. It was noted that it is about ten times more expensive but is worth it in regards overall scope of projects that disturb residential areas. Although regular watering is required for the first few weeks after installation, it is considered to be preferable than seeding due to better long term results (i.e. once it get established, there are unusually no problems thereafter.)
2016-10-04 | Drainage | Existing Pipe | SPOT IMPROVEMENTS(O) | 3 | BARREN | As let, the replacement of the two box culverts were determined not to be the most constructible and cost effective approach to widening the road at these locations. As originally planned, both box culverts would have been replaced with longer culverts for road widening but this generated the need for “less desirable traffic diversions” to facilitate new culvert installation. | A change order was issued to install an HDPE pipe liner into the existing culvert and extend the pipe liner beyond the existing culvert thereby allowing the road to be widened in these locations. This was a less expensive approach than total culvert replacement and allowed traffic to flow uninterrupted. (It was noted that the existing culverts were in good condition.)
2016-10-04 | Materials | Asphalt Mixtures | SPOT IMPROVEMENTS(O) | 3 | BARREN | There were five places in the recently placed asphalt that potholed. These occurred in areas where the base material was placed over existing pavement. Construction staff speculated that water draining through the new pavement was trapped by the old surface course and created hydrostatic pressure. | It was recommended to grind the pavement down to the old base layer which would allow for the better drainage of water in base.
2016-10-04 | Design | Omission | RECONSTRUCTION(O) | 3 | EDMONSON | The structural aggregate backfill needed for bridge construction over Sulphur Branch Creek did not have a pay item included in the design documents. It was an omission as stated by the district’s design staff. | A change order was written for No. 57 Aggregate backfill in lieu of structural aggregate backfill for ease of field calculations.
2016-05-16 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 8 | ADAIR | Existing Utilities were not moved before the start of construction. These needed to be relocated to facilitate roadway construction. | Relocation work was performed under the roadway contract per an approved change order. It was done by a contractor approved by the water district.
2016-05-16 | Design | Omission | SAFETY-HAZARD ELIM(P) | 8 | ADAIR | There was no sod setup on the contract to repair “in kind” disturbances to the residential lawns. Lawn disturbances were needed to facilitate utility and roadway construction. | All residential areas disturbed were revegetated with sod. A change order was issued to add sod onto the contract.
2016-05-16 | Maintenance of Traffic | Safety | RELOCATION(O) | 8 | CUMBERLAND | The designated detour (Gary Morgan Road) had inadequate site distance at the intersection with Old Columbia Road. At this intersection, there were two horizontal curves on each side which limited sight distance and created a safety concern. | During the design phase regarding Maintenance of Traffic (MOT) more consideration needs to be given to sight distance (& other safety factors) throughout proposed detour routes. During the design phase, driving detour routes could lead to work being included in the project plans to address safety concerns.
2016-05-16 | Structures | Expansion Joints | RELOCATION(O) | 8 | CUMBERLAND | Expensive repairs (up to $12,900.00) on some bridge end bents (BEB) in the district have been on the rise since shorter bridges are being designed without expansion joints. This causes a void (1.5 feet in some cases) between the roadway and BEB due to the expansion of the bridges. | Two possible solutions were discussed. First, adding expansion joints to shorter bridges would reduce/eliminate these problems. Second, finger joints at the BEB but it was believed that KYTC was reluctant to use them due to corrosion concerns from snow and ice removal chemicals. Special Note: This issue was not an observed problem on this project but discussed as an overall concern for shorter bridges without expansion joints.
2016-05-16 | Structures | Specifications | RELOCATION(O) | 8 | CUMBERLAND | The standard specifications allows backfilling RCBCs with soil material, which many times are clay. The district stated that this causes undue hydrostatic pressure on RCBCs because it does not allow subsurface flow to travel to the wick drains quickly enough. It was stated that water has been observed bleeding out of the culvert seams which indicates the backfill is saturated. | District personnel recommends backfilling with No. 23 stone which will drain very efficiently and in turn, allow subsurface water to daylight quickly. The district stated that this will significantly reduce the pressure on RCBCs backfilled with No. 23 stone compared to soil backfilled RCBCs.
2016-05-16 | Geotechnical | Quantities | RELOCATION(O) | 8 | CUMBERLAND | The amount of onsite rock available for road construction estimate was too low. The geotech estimate of rock available did not accurately reflect the quantity available on site. This may have led to a slight increase in the over cost as the contractor did his own coring prior to letting and was aware of this rock material. | As proposed by the Contractor, KYTC approved a change order to use the excavated rock in lieu of quarried aggregate for road construction. At that point in the project, this saved approximately 200,000 dollars.
2016-05-16 | Design | Omission | RELOCATION(O) | 8 | CUMBERLAND | Due to an extremely saturated area, a section of roadway (approximately 270 feet) and embankments required additional aggregate / undercutting for construction in lieu of cement stabilization. Also, cohesive pile cores, as designed, would not properly support the bridge end bents due to saturated conditions. This unsuitable area was not properly addressed in the plans. | By an approved change order, additional aggregate was added to the contract in place of cement stabilization. It was discussed that field walks during design development could have discovered this problem and therefore could have been addressed in the plans.
2016-05-16 | Design | Drainage | RELOCATION(O) | 8 | CUMBERLAND | The design plans called for a concrete curb and gutter system (with corrugated metal pipe) to daylight into the side of the reinforced concrete box culvert (RCBC). District personnel stated that this resulted water leaking into the RCBC backfill, as the pipe is not water tight. Apparently it was designed this way because there was not enough R/W purchased to daylight it outside the RCBC. | District personnel recommended that the curb and gutter system be daylighted at the toe of slope or even back of ditch. Additional R/W purchase would have allowed for this revision.
2016-05-16 | Design | Omission | RELOCATION(O) | 8 | CUMBERLAND | The school had requested that the crosswalk be reestablished but it was not included in the plans. School officials were concerned about pedestrian safety. | A mid-block crosswalk with sidewalk ramp was added for access to the school. A change order was issued to install these features on a cost plus basis.
2016-05-12 | Design | Omission | I-CHANGE RECONST(O) | 2 | HENDERSON | The existing island curb headers needed to be replaced due to their poor condition. They also would not direct drainage to the new drop box inlet due to their existing elevation. | A change order was written to include new island curb headers. It was noted by district design this was an omission and they should have been included with the plans. Better QA/QC could have caught this error prior to letting.
2016-05-12 | Drainage | Drop Box Inlets | I-CHANGE RECONST(O) | 2 | HENDERSON | District construction personnel decided that in this application, the curb inlet Type A would be subject to break under unintentional traffic loads (e.g. semi-truck cutting turns too sharp, snow plows inadvertently hitting them). It was also noted that “over all” there is a high occurrence of lids breaking on Type A inlets which is undesirable and a significant maintenance issue. | A change order was written to switch to a drop box inlet Type 13S which is not subject to damage in this application. It was noted, that this solution does have some drawbacks as grates on Type 13S tend to clog with road debris; still it was the opinion of district personnel that the Type 13S was the better solution.
2016-05-12 | Utilities | Existing Utilities | I-CHANGE RECONST(O) | 2 | HENDERSON | An existing AT&T phone line prevented a 54 inch headwall from being installed as depicted in the plans. As noted, the line was shown on the planview but exact depth was not known. It was difficult to perform design reconnaissance in this area because of the fallen trees and debris which was a result of the 2009 ice storm. | A change order was written to include the relocation of the line. The Contactor noted, they really did not want to deal with relocation but there was no other feasible alternative.
2016-05-12 | Construction | Method/Innovation | BRIDGE REPLACEMENT(P) | 2 | HOPKINS | There is disagreement between district design and district construction personnel regarding the amount of slope protection required beneath the bridge. Design plans only depicted aggregate cover from the end bent down to the bridge piers (approximately half the slope.) Construction felt that the aggregate should have been placed down to the ditch line. | By an approved change order, there was an additional 1000 tons of aggregate to increase the slope protection area down to the ditch line at the rail road ballast. More discussion between designers and constructors could lead to complete agreement regarding the philosophy for slope protection.
2016-05-12 | Design | Lighting | I-CHANGE RECONST(O) | 2 | HENDERSON | There was a lighting system quantity error regarding the bore and jack quantity needed for installation of electrical conduit. | A change order was written to include the proper amount of bore and jack to meet the design layout of the electrical system. Better QA/QC could have caught this error prior to letting.
2016-05-12 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 2 | HOPKINS | There was a tie in point on the existing road (Brown Badgett Loop) that had an unacceptable subgrade for new road construction. The soil was dark and could not be stabilized. This was not addressed in the plans. | The material was over excavated then suitable material was placed along with geotextile reinforcement. This work was approved by change order.
2016-05-12 | Design | Drainage | I-CHANGE RECONST(O) | 2 | HENDERSON | Private property located near the end of Ramp C (just off highway R/W) received “muddy surface flow” from the construction area. After heavy weekend rains with silt controls blown out, the property owner strongly complained about his gravel driveway being washed out. The district noted this was a natural drainage pattern traveling towards the property owner that had been channelized early in the construction of project. The district also noted “muddy water” was the main catalyst for his complaint. Not enough attention was given to drainage leading just outside of the R/W area and onto nearby property owner(s). | A change order was issued to construct a ditch to redirect surface flow away from this property. It took most of the surface flow in the opposite direction and to an existing 18” pipe beneath highway 416. No further complaints were made after the redirected ditch was installed.
2016-05-12 | Design | Median | I-CHANGE RECONST(O) | 2 | HENDERSON | Initially traffic requested asphalt medians, but district construction personnel decided that the asphalt medians as designed would become a maintenance issue due to traffic driving/parking on a “mountable median.” They also noted cracks typically appear in asphalt medians whereby weeds and other vegetation grow into the cracks. | A change order was switched from an asphalt median to concrete median/curb. This would dissuade motorist from driving/parking on the median. Also noted, that district 2 favors channelization type medians such as concrete median/curb.
2016-05-09 | Design | Drainage | RELOCATION(O) | 12 | LETCHER | After construction began, unplanned drainage issues (ponding water) arose on private property adjacent to the project. Numerous voids existing in the railroad bed allowed water from the construction site to flow uncontrollably onto properties located on the opposite side. Initially, the district thought the property was owned by a coal company, but later became aware it was owned by the residents. | Water was routed by pipes/subdrains and day-lighted into the nearby river. A change order was issued on a cost plus basis to install the system. All complaints have stopped since the drainage system was installed.
2016-05-09 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 12 | FLOYD | For constructability reasons, district construction personnel stated that Type 4A end treatment could not be installed to the right of station 296+65. At this location, a 4 foot offset was needed for Type 4A installation. However, it could not be obtained due to a ditch line and limited shoulder. | A change order was issued to switch to a Type 1 end treatment. It was stated that Type 1 end treatments are being use much more in recent times versus Type 2A or Type 4A. Constructability issues were discussed as the main reason for this trend.
2016-05-09 | Design | Communication | BRIDGE REPLACEMENT(P) | 12 | FLOYD | As let, the approximate 6 month contract specified a project completion date of October 31st, whereby KY 1428 would be closed at this location while the failing bridge was demolished and reconstructed. However, comments made before the letting to the Floyd County Board of Education School and the general public, stated the bridge should be reopened by August 15th, ten weeks earlier, in time for the start of school. This conflict was not discovered until after letting. (The district noted that some of the traveling public in this area incurred an 11 mile detour while the bridge was out.) | A change order was issued with an incentive for the Contractor to accelerate bridge construction to achieve a re-opening date of August 15th. The incentive amount of $2400.00/day was based on information in KYTC specifications 108.09 “Failure to Complete Work on Time”. The Contractor needed to revise his schedule by 30 days to meet the August 15th date, therefore the agreed amount was $2400.00/day x 30 days = $72,000.00 (The district was complimentary of the plans submitted by the Consultant. It was stated that due to their quality, this allowed project acceleration possible)
2016-05-09 | Design | Excavation | RELOCATION(O) | 12 | LETCHER | There were discrepancies between aerial mapping and actual ground lines in several locations. This resulted in inaccurate earthwork estimates for the project. It was noted that mapping/plan errors were a result of two issues. First, there was an area that was depicted as a fill area on the plans but it actually a side hill cut was needed. Also there was excavation of an existing haul road that was not depicted on the plans. It was stated that heavy tree cover most likely created these inaccuracies. Second, a 2:1 side slope cut area was started several benches lower (about 20 feet) than depicted on the plans, therefore a larger amount of material was excavated than estimated. Mapping used in the plans was developed in the early-1990s and most likely the topography had been altered due to recent coal mining. | A change order was issued for additional earthwork costs to allow the project to be built as designed. Both tree cover areas and projects based on older mapping should be field checked to reduce or eliminate inaccurate earthwork estimates prior to lettings.
2016-05-09 | Design | Quantities | RELOCATION(O) | 12 | LETCHER | The 37 acre Waste Area 3 as designated in the plans was 20 acres larger than needed for this project but the clearing and grubbing (CG) quantity was not revised downward prior to letting (Waste Area 3 was initially to serve a larger project.) This acreage revision was not caught before letting. Overall CG acreage total (including CG roadway & other areas) was reduced from 204 acres to 184 acres (-9.8%). However, CG lump sum price bid was based on 204 acres of CG. | A change order was issued to revise downward the lump sum price bid by the Contractor. The downward revision was prorated based on an area ratio (9.8% less CG area) multiplied times the lump sum bid ($544,500.00) (i.e. 0.098 x $544,500.00 = $53,361). This made the total revised CG payment $500,159.00. Better QA/QC could have caught this before letting.
2016-05-09 | Design | Omission | BRIDGE REPLACEMENT(P) | 12 | FLOYD | Permanent striping was needed on the project but was not setup in the plans. It was an omission in the plans as stated by district personnel. | A change order was written to include striping as needed for the project. Improved QA/QC could have caught this omission.
2016-05-04 | Design | Specifications | BRIDGE REPLACEMENT(P) | 11 | KNOX | There was no bid item that allowed for incremental payments to assist the contractor in cash flow to build & store prefabricated bridge elements (PBE) which is an integral part of accelerated bridge projects (ABC), yet it was reasonable to pay for efforts in this regard. Also it was noted that if the Contractor had gone out of business during the project, it might have been difficult for KYTC to take ownership of PBEs. The contract as written only paid for the PBE after they were in place and accepted by the Engineer. | A separate bid item that defines incremental payment and ownership of PBEs should have been included. This bid item would have allowed KYTC to legally recover PBEs should the contractor have gone out of business in the middle of the project. It is noted that the district did make incremental payments to the contractor for PBEs.
2016-05-04 | Design | Specifications | BRIDGE REPLACEMENT(P) | 11 | KNOX | There was no bid item that allowed for incremental payments to assist the contractor in cash flow to build & store prefabricated bridge elements (PBE) which is an integral part of accelerated bridge projects (ABC), yet it was reasonable to pay for efforts in this regard. Also it was noted that if the Contractor had gone out of business during the project, it might have been difficult for KYTC to take ownership of PBEs. The contract as written only paid for the PBE after they were in place and accepted by the Engineer. | A separate bid item that defines incremental payment and ownership of PBEs should have been included. This bid item would have allowed KYTC to legally recover PBEs should the contractor have gone out of business in the middle of the project. It is noted that the district did make incremental payments to the contractor for PBEs.
2016-05-04 | Structures | Standard Drawings | BRIDGE REPLACEMENT(P) | 11 | KNOX | On the standard drawing, no chamfer strips are shown on the tops and bottoms of the form liners but are needed for proper use. | For this particular project the contractor was aware of this strip and included it but recommended it be included in the standard drawings to prevent potential problems on other projects.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | There was an 8 inch gas line that was not put on the plans and should have been relocated prior to starting the project. | The line was moved during the project itself. Better QA/QC could have caught this omission before letting.
2016-05-04 | Design | Omission | MAJOR WIDENING(O) | 11 | WHITLEY | There were no bid items (aggregate and filter fabric) set up to pay for temporary construction entrances as required by Construction Memorandum 01-13. | A change order was written and payment provisions for these items were set up. Better QA/QC may have prevented this omission from occurring.
2016-05-04 | Design | Communication | MAJOR WIDENING(O) | 11 | WHITLEY | There was some disagreement between design, structural design and construction concerning the replacement of HL93 Box Culvert which eliminated the need for lightweight fill over the existing culvert. Construction changed the plans from filling over existing pipe to installing new Box Culvert/pipe. | Additional discussions between these members prior to letting between KYTC professionals may have everyone in complete agreement.
2016-05-04 | Design | Omission | MAJOR WIDENING(O) | 11 | WHITLEY | The mainline traffic loops were left out of the contract. | A change order was written to include the installation of them for proper MOT. Better QA/QC may have prevented this omission from occurring.
2016-05-04 | Guardrail | Design | MAJOR WIDENING(O) | 11 | WHITLEY | Guardrail was removed as part of the project where 4:1 outslopes (i.e. recoverable slopes) were constructed including areas where steel strain poles were located. Based on clear zone roadside design guidelines, guardrail should have been left around the steel strain poles. (It is noted that design personnel did agree with the decision to remove the guardrail at other locations where 4:1 slopes were constructed) | Better understanding by construction management personnel regarding roadside clear zone guidelines may have led to a decision to leave the guardrail around the steel strain poles.
2016-05-04 | Design | Safety | MAJOR WIDENING(O) | 11 | WHITLEY | Design did not utilize anticipated waste material as embankment to create recoverable 4:1 slopes adjacent to the ramps, thereby eliminating the need for existing guardrail. This was considered to be an overall enhancement to the project. (It is noted as plans were being developed the budgetary constraints as set did influence the initial concept.) | Waste material was used to create 4:1 roadside outslopes which created a safer driving environment for the public.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | There was an 8 inch gas line that was not put on the plans and should have been relocated prior to starting the project. | The line was moved during the project itself. Better QA/QC could have caught this omission before letting.
2016-05-04 | Design | Evaluations | BRIDGE REPLACEMENT(P) | 11 | KNOX | The pavement design (0.75 inch aggregate mix) as specified was not suitable due to an unstable foundation. | Unstable material was undercut and placement of a 1.0 inch asphalt mix (i.e. 1” Nominal Maximum Aggregate Size), instead of 0.75 inch asphalt mix was laid.
2016-05-04 | Design | Evaluations | BRIDGE REPLACEMENT(P) | 11 | KNOX | The pavement design (0.75 inch aggregate mix) as specified was not suitable due to an unstable foundation. | Unstable material was undercut and placement of a 1.0 inch asphalt mix (i.e. 1” Nominal Maximum Aggregate Size), instead of 0.75 inch asphalt mix was laid.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | Rebar was mistakenly galvanized without being first quenched in chromate solution as required. | Galvanizing was stripped, then is was shipped from Louisville to a company in Pennsylvania to be dipped in chromate. The rebar was then re-galvanized. It was noted that there are limited places in the US that does chromate dipping due presumably to strict EPA regulations; district personnel stated that Pennsylvania is one of the closest places to KY that performs this service.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | Rebar was mistakenly galvanized without being first quenched in chromate solution as required. | Galvanizing was stripped, then is was shipped from Louisville to a company in Pennsylvania to be dipped in chromate. The rebar was then re-galvanized. It was noted that there are limited places in the US that does chromate dipping due presumably to strict EPA regulations; district personnel stated that Pennsylvania is one of the closest places to KY that performs this service.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | Steel beams were required to be hot dipped galvanized coated but the first dipping results did not meet specifications. The primary reasons for the rejection was the galvanized coating thickness did not meet tolerances and it was also flaking off in places. Carbon steel beams normally have silicon present in them which makes galvanizing difficult. | The beams were re-galvanized (i.e. re-dipped) and were accepted by the district. During the second effort, the beams were not in the galvanized bath as long and angle of insertion was less as each beam entered the bath. A specification that reduces or eliminates silicon from the steel should be used for future projects. (It is noted that the galvanized coating was stripped off each beam prior to the second galvanizing effort. The cost for this effort was shared between KYTC and the Contractor. The cost for the second dipping was incurred by AZZ Galvanizing Inc. who was hired by the Contractor for this service)
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | Steel beams were required to be hot dipped galvanized coated but the first dipping results did not meet specifications. The primary reasons for the rejection was the galvanized coating thickness did not meet tolerances and it was also flaking off in places. Carbon steel beams normally have silicon present in them which makes galvanizing difficult. | The beams were re-galvanized (i.e. re-dipped) and were accepted by the district. During the second effort, the beams were not in the galvanized bath as long and angle of insertion was less as each beam entered the bath. A specification that reduces or eliminates silicon from the steel should be used for future projects. (It is noted that the galvanized coating was stripped off each beam prior to the second galvanizing effort. The cost for this effort was shared between KYTC and the Contractor. The cost for the second dipping was incurred by AZZ Galvanizing Inc. who was hired by the Contractor for this service)
2016-05-04 | Design | Omission | MAJOR WIDENING(O) | 11 | WHITLEY | Crash walls as designed on right side of the overpass were not included in the contract. | A change order was issued to include this item. Better QA/QC may have prevented this omission from occurring.
2016-05-04 | Design | Diversion | BRIDGE REPLACEMENT(P) | 11 | KNOX | Preemption of traffic signals at the railroad crossing should not have been included in design because a simple temporary detour was feasible. The preemption would have caused a lot complicated work that was unnecessary and expensive. | Even before construction began, a simple temporary detour route was designated farther away from the construction zone. This was implemented to better manage traffic in and out of downtown Barbourville. This eliminated the need for preemption of traffic signals near the construction zone and saved over $200,000.
2016-05-04 | Structures | Painting | BRIDGE REPLACEMENT(P) | 11 | KNOX | The design called for staining the concrete bridge barrier wall but the appearance/color was not acceptable to district personnel. It was meant to appear like an old stone wall built with natural stone in the area. However it did not match any of the natural stone in the surrounding area. Also it was not clear in the plans whether the stain sealer was part of the staining process. | An alternate acid based stain from Scofield System, Lithochrome Chemstain Classic, was tested, approved and used. The district recommended stain standards be developed. For this project the Contractor treated the stain and sealer as one bid item, but for future projects better definition regarding payment was recommended.
2016-05-04 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 11 | KNOX | No contractual language existed in the plans specifically regarding the implementation of the railroad flag person services, which led to the responsibility of additional CSX charges incurred by KYTC. District design personnel stated that the Contractor was not conservative enough regarding the use of these services without regard to the actual need for flagging. The district stated that these required railroad services are “very expensive” and stated they are “not worth the cost.” However they are required by law when working on railroad right of way. | A change order was written to cover the additional expenses for railroad services for this project. For future projects better language needs to be added to the plans and / or contract documents that defines clear instructions regarding Contractor implementation of railroad flag person services. Moreover, the language should be written to state when a Contractor is to be held accountable for cost overages. It should be noted that during the meeting no clear language was determined but development of this contract clause should occur.
2016-05-04 | Design | Omission | BRIDGE REPLACEMENT(P) | 11 | KNOX | There was an insufficient quantity setup of Erosion Control Blanket (ECB) to install on slopes 3:1 or greater. District personnel was still not clear how this omission was not caught before letting. | A change order was issued to add a sufficient amount of ECB to the contract. More attention should be given to QA/QC prior to project letting to reduce and/or eliminate contract omissions.
2016-04-28 | Erosion Control Plan | Channel Lining | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | Concerns regarding potential scour around the bridge piers were raised based on the dynamic discharges and velocities observed. The anticipated scour would negativity effect the bridge pier and Relict Darter habitat. | A change order was written to provide for the installation of R650 aggregate (Cyclopean Stone) that will prevent scour and erosion.
2016-04-28 | Design | Quantities | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | The Relict Darter which is rare and on the federal endangered species list, was known only to exist within the drainage basin (Bayou du Chien) at bridge 3 (northern bridge most in project.) Some erosion control measures initially designed were not accurately quantified based on requirements by Fish and Wildlife. | Enhanced erosion control measures, revised construction technique and special seeding mixes were implemented to protect the Relict Darter. Part width construction was performed to increase manageability of erosion control within the area. A more expense coconut fiber erosion control blanket was installed at bridge 3, which is biodegradable and more environmentally acceptable to Fish and Wildlife. Likewise a special seed mix was used that was deemed more wildlife friendly. Rock berm with filter fabric intertwined was installed to enhance erosion control measures. A catch tarp was constructed to prevent debris from entering the stream during bridge demolition. A change order was written to revise amounts and include quantities needed to construct said features.
2016-04-28 | Design | Communication | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | At time of bidding, no 60,000 pound weight restriction was stated in the plans and therefore the Contractor bid the project based on transporting fill weighing up to 80,000 pounds across the KY 68 / Edger’s Ferry Bridge. This route was the only reasonable way to transport materials to the project area. However, after the project was let, the district discovered the road was classified as a AA truck route which limits trucks to 60,000 pounds. This cause additional labor and equipment expenses to the contractor that were not reflected in the unit bid prices. | A change order was written to properly compensate the contractor for the additional truck loads that would be required.
2016-04-28 | Geotechnical | Investigation | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | A redesign was performed based on a less expensive 1000 year seismic event. The redesign continued even after the construction letting. This allowed the reduction of DSM required when in conjunction flattening embankment outslopes from a 3:1 to a 4:1. An indirect benefit outslope flattening is that it allowed items covered in the environmental report, such as multi use paths, fishing paths, etc. to be more easily incorporated into the project. | Dynamic (static and pseudo-static) pile load testing data was obtained during this project and was used for design data for the main span project. It gave accurate “real world information” that the size hammer that would be required for main span pile installation (this information likely averted a sizable change order during the main span project.)
2016-04-28 | Design | Phasing | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | A redesign was performed based on a less expensive 1000 year seismic event. The redesign continued even after the construction letting. This allowed the reduction of DSM required when in conjunction flattening embankment outslopes from a 3:1 to a 4:1. An indirect benefit outslope flattening is that it allowed items covered in the environmental report, such as multi use paths, fishing paths, etc. to be more easily incorporated into the project. | There was a desire to let the project by the district with an understanding by district personnel that some revisions would be made after the letting. Many of the revisions were reflected in change order 1.
2016-04-28 | Geotechnical | Embankment Stabilization | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | The initial design was based on a 2500 year seismic event, due to the district’s opinion of this being a “critical link” to this area. However when the bids were received they were too expensive and the winning bid was rejected. In particular, it was noticed that deep soil mixing (DSM) was extremely expensive compared to the Engineers Estimate. | A redesign was performed based on a less expensive 1000 year seismic event. The redesign continued even after the construction letting. This allowed the reduction of DSM required when in conjunction flattening embankment outslopes from a 3:1 to a 4:1. An indirect benefit outslope flattening is that it allowed items covered in the environmental report, such as multi use paths, fishing paths, etc. to be more easily incorporated into the project.
2016-04-28 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | The quantity of DGA setup was insufficient to properly complete the project as constructed. Additional DGA was needed for stability, due to part-width construction that was not accounted for in the design phase. | A change order was issued for additional DGA. Better understanding of construction technique and QA/QC could have led to a more accurate DGA estimate prior to letting.
2016-04-28 | Design | Communication | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | The contractor requested a 5 inch Strip Seal in lieu of the 3.5 inch Neoprene Expansion Dam. | A change order was approved and the strip seals were installed. It was mentioned that it is easier to install and maintain.
2016-04-28 | Construction | Earthwork | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | As excavation for the road proceeded, wet blue clay was encountered and was hampering construction of the road bed. This problem was exacerbated by part width construction technique whereby the adjacent cut slope would fall in unless aggregate backfill was placed in a timely manner. | After consulting with geotech it was decided to include more aggregate than setup. A change order for additional Granular Embankment was approved.
2016-04-28 | Design | Omission | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | There was language in the plans under Cleaning and Painting notes declaring “Cleaning and Painting” (607.03.23) standard specification in force but no discussion regarding painting “step back” at the connections desired by the district. Moreover, there is no discussion or references in the standard specifications (607.03.23) discussing the “step back” at the connection points. Steel members as delivered to the site had all 3 painted layers brought to “one line” at the contention point which would not allow for a continuous painted coating at these points. This was unacceptable to the district based on information produced by the Society for Protection Coatings (SSPC). | The connection points were sanded back to remove the top and intermediate coats of paint. This created acceptable steel members for construction as they could then create a continuous coating at the connections as recommended by SSPC. The cost of the work was shared among the district and the Contractor as approved by a change order.
2016-04-28 | Geotechnical | Piling/Drilled Shaft | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | The estimated pipe pile installation depths based on geotech data in the plans, did not coincide close enough with what was actually required based on dynamic pile testing. In order to complete construction within the given time, and because lead time for ordering pipe piles is so long, the contractor ordered the pipe piles for the project prior to the dynamic pile testing. As a result, the contractor purchased approximately twice the amount of pipe piles needed and mobilized a bigger more expensive pile driver than needed. The contractor decided to order both testing and construction piles up front to ensure work could continue without having to possibly wait 30 to 60 days for the mill to roll piles. Typically steel yards do not have pipe piles readily available. | Drive test piles during the design phase thereby providing a more accurate estimates during the bidding process. (It is noted that KYTC denied a claim for additional compensation for this issue.) There is a major conflict by what is required in the standard specification and the ability to expedite construction.
2016-03-24 | Design | Quantities | SAFETY(P) | 6 | GRANT | Not enough Erosion Control Blanket (ECB) was setup in the contract. | A change order was issued for the required amount of ECB.
2016-03-24 | Construction | Inspection | SAFETY(P) | 6 | GRANT | The flag person who was working for CSX was padding his time. KYTC was reimbursing (in part) CSX for flagging services on an hourly rate so this became a problem for the district. Also noted, CSX paid $20,000 to KYTC for flagging services, however it did not cover all of the expenses in this regard. | District personnel began documenting the actual time the flag person was on site and performing duties. This information was passed along to representatives of CSX who had the flag person replaced.
2016-03-24 | Maintenance of Traffic | Tie Ins | RECONSTRUCTION(O) | 6 | BOONE | The MOT design did allow enough room on the north end to accommodate construction work. This did not work with full depth reconstruction as planned. Likewise, on the south end near Rogers Lane, more room was needed for proper MOT and construction. | More consideration needs to be given in the design phase regarding construction methods and the area that will be needed to facilitate construction and allow for proper MOT. On the north end, a change order was approved for supplemental traffic control items. On the south end, the Contractor was able to eliminate lime stabilization and include #2 stone aggregate with cross drain at the vertical low point which allowed for better MOT. It was noted that placing MOT design on the cross sections could alert designers to potential problems and allow for them to be addressed in the design phase.
2016-03-24 | Design | Survey | SAFETY(P) | 6 | GRANT | The survey data was not accurate whereby the existing ground at the location of an end bent was off by 13 to 18 feet than depicted on the plans. This led to incorrect embankment estimates in the design documents. | Field verification of plans prior to construction efforts could have caught this error. A change order was issued for the additional embankment yardage needed to construct features as designed.
2016-03-24 | Structures | Retaining Walls/MSE | RECONSTRUCTION(O) | 6 | BOONE | It was difficult to compact next to the MSE wall because there was no temporary support for the wall as it was going up and in transition areas. The bridge pilings also interfered with the installation of the tie back straps. Also potential damage to tie back straps was an issue. | Provide barrier walls or bulk head to support the wall until compaction can be achieved. Evaluate tie back strap placement in conjunction of piling locations. Plate compactors were use within a 3-feet area along the wall.
2016-03-24 | Design | Quantities | RECONSTRUCTION(O) | 6 | BOONE | In one area, the survey data was not accurate. This resulted in the existing groundline was on average 18 inches lower than depicted on the cross sections. This led to incorrect embankment estimates in the design documents. It is noted that the survey data was approximately 12 years old and over that time there had been significant agricultural disturbance (farm/nursery) in this area. | Field verification of older survey data could have a caught this error prior to construction. Designers should be vigilant concerning earthwork estimates in areas that are known to have been disturbed after survey data was collected. A change order was issued for the additional embankment yardage needed to construct features as designed.
2016-03-24 | Utilities | Relocation | SAFETY(P) | 6 | GRANT | The Contractor stated that bridge beams could not be set until an existing utility pole (phone line only) was relocated. The Contractor verbally put the district on notice it was viewing it as “change conditions” and was considering filing a claim. Also noted that no utility relocation design plan existed. | Cincinnati Bell was contacted by district construction personnel and it was moved in one day. Due to the expediency of the relocation, it never did cause a delay. The pole was moved before the Contractor was even able to get a flagman on site. Therefore the Contractor’s argument for damages “went away” and never was submitted to the district.
2016-03-24 | Construction | Specifications | RECONSTRUCTION(O) | 6 | BOONE | There was a disagreement between the Contractor and the district regarding the specification for a particular geogrid that the contractor wanted to use. The contactor did not have product testing data to demonstrate that it met specifications. This geogrid product was less expensive to the Contractor and was the catalyst for its use. | Initially the district would not approve this geogrid but reversed its decision after the Contractor demonstrated that it met KYTC’s specification (i.e. meet or exceed TX-5.) At that point, the contractor had already purchased the more expensive product. KYTC approved payment for the difference in price of the two geogrids.
2016-03-24 | Design | Communication | RECONSTRUCTION(O) | 6 | BOONE | During the bidding process, questions posed by contractors were not answered accurately or specifically enough in some cases. This includes times when a plan note or specification is stated as the answer to a question but is still not specific enough. This lack of specificity can lead to increase costs, when a contractor assumes “worst case scenario” which can lead to higher bid price(s) than may be needed. It can also lead to bids that are too low and do not properly quantify the work to be done. | The project manager need to strive to provide specific and complete answers to questions. A single designated point of contact may reduce problems of vague or inaccurate responses. Contractors should submit questions as soon as possible to allow the district time to develop a detailed and specific response.
2016-03-24 | Maintenance of Traffic | Slopes | RECONSTRUCTION(O) | 6 | BOONE | The maintenance of traffic (MOT) design did not take into account for a five-foot drop off that was generated to facilitate construction work. This created a dangerous situation for motorist. | MOT plan development needs to include cross sections as part of this design plans; cross sections help identify 3-D problems so they can be addressed as part of design. 3-D modeling of a project would have also helped. A change order was written for a concrete median barrier and other items to provide for safe passage of motorists.
2016-03-10 | Design | Drainage | RECONSTRUCTION(O) | 5 | SPENCER | The plans called for a more expensive bore and jack method to install a pipe but it was determined during construction this method was not necessary. The designer stated that they proposed bore and jack method (over open cut) as it is considered a preferred method for most roadway pipe installations to avoid land closures. | Contractor proposed switching from a bore and jack pipe installation method to an open cut method. The proposal was accepted by the district as it was determined that traffic could be properly managed. District construction personnel stated that it would have been difficult to conceive of the open cut approach for this particular pipe installation.
2016-03-10 | Design | Excavation | RECONSTRUCTION(O) | 5 | SPENCER | Mapping was inaccurate in one location which lead to inaccurate design excavation estimates. The aerial survey showed an incorrect slope most likely due to leaf cover. | The district survey crew conducted field survey work to determine the actual yardage to be excavated. A change order was written to pay for the actual yardage excavated. Designers should pay particular interest in areas that are heavily wooded, as these areas are prone to aerial mapping errors.
2016-03-10 | Design | Plans | NEW INTERCHANGE(O) | 5 | OLDHAM | The design plan did not consider the depth of the proposed pipe which caused a guardrail installation problem. Guardrail posts could not be installed to the proper depth because the pipe beneath them was too shallow. | The guardrail was moved to the back of the multiuse path approximately 8 feet from the back of curb. Crash cushions were installed at the ends of the roadway barrier where the guardrail was originally to be placed.
2016-03-10 | Geotechnical | Quantities | RECONSTRUCTION(O) | 5 | SPENCER | The geotech data did not provide an accurate estimate of durable rock available on the project. The estimate was low, therefore it presented a problem for roadway construction. | A change order was written for crushed aggregate to construct an acceptable sub base as required by geotech notes. District construction personnel stated that “local knowledge” of a given area may help estimate the amount of constructible material that exists for a project.
2016-03-10 | Design | Quantities | NEW INTERCHANGE(O) | 5 | OLDHAM | When preparing the subgrade for roadway construction, several areas were discovered to be unstable and unsuitable to properly support the road. It was noted by the district construction personnel that unstable subgrade areas are difficult to quantify upfront. | A change order was written to include granular embankment and Type IV fabric to construct a suitable subgrade as needed. It was stated by the district that bid items should be setup in just enough quantity to get a decent unit price.
2016-03-10 | Utilities | Existing Utilities | NEW INTERCHANGE(O) | 5 | OLDHAM | Contrary to a verbal agreement with project designers, Oldham County Water District (OCWD) did not have an existing waterline relocated prior to construction letting. This waterline, in its original location, prevented the construction of a bridge pier. Moreover, because of infrequent interaction, smaller water districts often do not have the trust in KYTC to properly oversee and construct water line projects. | During construction activities, district construction personnel began working with OCWD officials. After discussions between the district and OCWD, a level of trust was built which allowed the district to design and relocate the water line. A change order was issued to pay for the relocation work directly to an OCWD approved Contractor and within OCWD specifications. The waterline relocation work was done according to plans created by OCWD, not KYTC. It is noted that KYTC Utilities Memorandum 1-15 encourages district offices to include utility relocation work within KYTC construction projects; furthermore it discusses using utility company approved subcontractors (if applicable.)
2016-03-10 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 5 | SPENCER | A 72” dia. pipe channeling a creek parallel to the road but outside of the project plans was found to be rusted out and was at risk of failing; if the pipe failed, areas within the project limits would have been subject to flooding. | A change order was issued to replace the pipe with a larger 84” dia. pipe thereby reducing the risk of flooding.
2016-03-10 | Design | Quantities | RECONSTRUCTION(O) | 5 | SPENCER | There was not enough Erosion Control Blanket (ECB) setup for the project. | To meet KYTC specification regarding the use of ECB, a change order was issued to provide for the quantity needed.
2016-03-10 | Design | Median | NEW INTERCHANGE(O) | 5 | OLDHAM | The concrete median originally planned no longer made sense from a consistency and commonality standpoint unlike when it was once part of a larger project. The project had been scaled back from its original plan but the median was never reevaluated and therefore was not deleted from the plans prior to letting. Installation of it would have increased project costs, increased bridge deck construction efforts, and created additional work (hook bolt removal & surfacing improvements) when removed. | A change order was written to remove the concrete median from the contract. Additional plan review when project scope was revised may have alerted designers to the median reevaluation prior to construction letting.
2016-03-10 | Geotechnical | Slides | RECONSTRUCTION(O) | 5 | SPENCER | A slide in a bench area started after completion of roadway. It began undercutting the road and cracking asphalt. | A change order was issued to excavate the slide to the failure plane, reconstruct the slope and install bleeders (subdrains) to collect subsurface drainage. Slope inclinometers were installed to determine the scope of the slide.
2016-03-10 | Design | Omission | NEW INTERCHANGE(O) | 5 | OLDHAM | Although there was permanent signage in the plans, it was not on the general summary. This general summary omission was never caught before the proposal was issued. | A change order was written to put them in the bid items. Better QA/QC in plan processing may have caught this omission prior to the proposal being issued. The district recommended a signing summary page to be included with the plans.
2016-03-10 | Geotechnical | Piling/Drilled Shaft | NEW INTERCHANGE(O) | 5 | OLDHAM | Original design called for drilled shaft for Pier 1 instead of a less expensive spread footer to support the bridge. Steep topography prevented geotech information from being obtained at this particular spot which prevented the consideration of a spread footing in the design phase. It is noted that geotech sampling locations were based on an initial bridge span arrangement. Subsequently, the span arrangement was revised but the originally proposed geotech sampling locations were not. A financial decision was made not to obtain additional geotech which may have revealed the existing rock. | Due to the presence of solid rock subgrade, a change order was written to construct a spread footing instead of a drilled shaft which reduced project costs and met the structural capacity required.
2016-03-10 | Design | Grade | RECONSTRUCTION(O) | 5 | SPENCER | The driveway was asked to be reworked by owner as it was perceived to be too steep. | A change order was issued to lessen the grade on the driveway. Better understanding by R/W negotiators of slope variation may reduce complaints during construction by land owners.
2016-03-01 | Design | Omission | RELOCATION(O) | 9 | MASON | Signage design was not complete at the time of letting. This omission was not discovered until just before the project was let. The project was let without signing plans or quantities. | A change order was approved to install signage as part of the project. It is noted that D9 knew at the time of letting that there would be a change order for this feature.
2016-03-01 | Design | Omission | RELOCATION(O) | 9 | MASON | The new route bisected Slack Pike creating an unacceptable dead-end street for residence whereby vehicles (e.g. garbage truck, school bus) could not turn around. No provision to address this problem were in the plans. | A change order was issued to construct a cul-de-sac to allow vehicles to easily turn around. Better QA/QC may have alerted the designers to this condition while still in the design phase.
2016-03-01 | Traffic | Safety | RELOCATION(O) | 9 | MASON | No provision was included in the plans to protect the workers and prevent cars from running off the cut slope. | A change order for a Concrete Barrier Wall Type T was approved to meet this safety objective. Better QA/QC may have alerted the designers to this situation while still in the design phase.
2016-03-01 | Drainage | Pipes | RELOCATION(O) | 9 | MASON | The 72” pipe as designed, was too short which lead a steep, unstable grade above the pipe to slip. Second the headwall also encroached on one side into the slope. It was noted that many times designers do not take into account the skew of proposed pipes and headwall which leads to problems of this nature. | A change order was written to extend the pipe which allowed the slope to be reconstructed at a stable configuration. Pipe profiles that take into account the skew of proposed pipes would reduce or eliminate these types of the problems.
2016-03-01 | Design | Evaluations | NEW ROUTE(O) | 9 | FLEMING | The “tie in point” for the temporary traffic diversion encroached on new road construction area. It was particularly problematic to construct because of 6 feet grade separation between the new road and the detour lane. This “tie in” encroachment caused some constructability & maintenance of traffic problems. | Allow more room for traffic detour “tie ins” to allow separation of new road construction from the detour tie in. For this particular project, “part width fill construction” was performed so the detour could remain open. However, the contractor voiced displeasure over having to perform part width fill construction. Purchase additional ROW to tie in the detour outside of the roadway construction area. It is noted that this would lead to some cost increases for purchases of temporary right of way and diversions for future projects. More evaluation by KYTC of “increasing tie in areas” for future projects may be warranted.
2016-03-01 | Construction | Ride Quality | NEW ROUTE(O) | 9 | FLEMING | To meet ride quality specification for asphalt and material uniformity a MTV was necessary. There was no bid item OR note directing the required use of this machinery. | For this project a change order was written for payment of the MTV. For future projects, a special note stating that a MTV will be required for asphalt placement. Ensure all contractors who bid are aware of this requirement and know that MTV are incidental to placement of asphalt per KYTC’s Standard Specifications for Road and Bridge Construction 2012 Edition (403.04.08) Furthermore, all highway professionals should be aware that ride quality as defined in Section 410 of the KYTC’s Standard Specifications for Road and Bridge Construction 2012 Edition does not specify equipment. It is left to the Contractor to determine the best methods of achieving ride quality.
2016-03-01 | Construction | Revisions | NEW ROUTE(O) | 9 | FLEMING | The current compaction requirements for Crushed Stone Base (CSB) may be causing degradation of the aggregate whereby it severely reduces its drainage capacity. | Possible solution is to change the spec to include 4” drainage blanket at problem locations. Another option may be to use DGA plus asphalt drainage blanket. (More study is needed to determine the effectiveness of these solution proposals)
2016-03-01 | Utilities | Delays | RELOCATION(O) | 9 | MASON | The Haydon Bridge Company stated that due to a utility conflict, they couldn’t work on two bridges at the same time. This lead to a claim against KYTC for damages due to delays. | A change order for $115,000 was approved by Director of Construction to settle the claim brought by the Haydon Bridge Company.
2016-03-01 | Construction | Method/Innovation | RELOCATION(O) | 9 | MASON | After the project was let, this project switched to an option that required the use of an MTV. No MTV was setup as part of the contract. | A change order was approved to pay for the equipment for final lift/top coat. Specifications for asphalt placement now requires the use of a MTV and payment is incidental to the unit price of asphalt.
2016-03-01 | Design | Drainage | NEW ROUTE(O) | 9 | FLEMING | Subsurface drainage was daylighting through the top of newly placed asphalt in a constructed fill embankment. No participant involved with the project was sure about the water source nor why it was day-lighting in these locations. It was stated that nearby cross drains were placed at the cut / fill intersection but were ineffective (no water flowing out) in addressing the daylighting problem. | Four inch underdrains were installed at the precise locations where the water was daylighting. These underdrains captured the water and day-lighted it to the roadway ditches thus correcting the issue. Another potential solution could have been to use an asphalt drainage blanket.
2016-03-01 | Geotechnical | Cut-Slope | NEW ROUTE(O) | 9 | FLEMING | The plans called for drainage blankets and aggregate at several locations where embankment benches were to be cut. However, these areas were found not to have subsurface water as anticipated. | A decision, as recommended by geotech, was made NOT to add drainage blanket and aggregate to those locations where dry conditions were found.
2016-03-01 | Design | Drainage | NEW ROUTE(O) | 9 | FLEMING | It was not feasible to use an existing drainage system as called for in the plans. This was due to existing corroded CMPs that were to be “tied into” as part of the median drainage control system. It was stated that CMPs are subject to a reduced life span due to increasing use of snow and ice removal chemicals. | The re-design and construction in these areas addressed the drainage by removal of the raise median which provided for proper sheet flow drainage. Headwalls, Junction Boxes & Pipe extensions were not installed and eliminated via change order from the contract. In the design phase, examination of existing pipe(s) with camera would have revealed pipe corrosion whereby other viable design concepts could have been developed.
2016-03-01 | Utilities | Communication | NEW ROUTE(O) | 9 | FLEMING | There was no utility line casing (for future expansion) included in the original contract because at the time of plan development, the City of Flemingsburg’s expressed no desire for their installation. After the contract was let, the city changed their position and requested casing be installed before road construction proceeded. | Being “good stewards”, District 9 decided to grant the city’s request, particularly considering their municipal utility company status (i.e. non-profit company.) A change order was written to install the casing.
2016-03-01 | Utilities | Delays | NEW ROUTE(O) | 9 | FLEMING | A project extension was needed due to a delay in relocation of electric lines, which in turn created a negative situation with the contractor. Many times a utility company will not relocate lines until road construction is underway, thereby increasing the prospects of road construction delays that lead to cost overruns. | KYTC could create a branch or dedicated design group whose sole responsibility is to design utility relocation plans that would provide for timely relocation of said features prior to road construction. Laws governing utility work need to be examined and revised to require companies to relocate lines promptly before road construction begins.
2016-03-01 | Design | Shelved Plans | NEW ROUTE(O) | 9 | FLEMING | At the time of plan development, the policy was ambiguous on whether rumble strips were a pay item. Subsequently the consultant who was working for the district was instructed not to include any rumble strips in the plans. | A change order was written to have sawed rumble strips included in the project. More attention is needed in regards to the latest rumble strip specification as to when they are to be paid for and where and how they are to be installed. This policy needs to be understood and consistently implemented by all professionals working for KYTC.
2016-02-12 | Design | Railroads | MAJOR WIDENING(O) | 7 | FAYETTE | AAs the project was near letting and final design preparations were being performed, Norfolk Southern (NS) was contracted and an agreement was reached to build a temporary cofferdam to support Pier 1 only. However, by the time the contractor approached NS to construct the cofferdam, NS's standard had been revised (over just a few months’ time) and they demanded supports for Piers 1 and 2. Although there was documentation regarding the initial agreement, NS would not honor it. | A change order was written for the increase supports (cofferdams) as requested by NS. Perhaps more binding agreements may be considered regarding arrangement with 3rd party companies.
2016-02-12 | Design | Communication | NEW ROUTE(O) | 7 | FAYETTE | No quantities of aggregate and filter fabric were included in the bid package for temporary construction entrances that were needed on the project. At the approximate letting time, a Temporary Construction Entrance & Erosion Control Blanket memo (CM 01-13) was issued directing construction entrances to be compensated for their installation. This memo was issued in January 2013 approximately 3 months before the project was let. As stated in the memo, KYTC had been inconsistent in use and payment of temporary construction entrances and erosion control blanket; this memo's intent is to provide guidance and understanding regarding use and payment of these features. | A decision was made by the district to compensate the contractor for materials used (aggregate & filter fabric) for temporary construction entrance installation. Better communication between the designer and Division of Construction may have alerted them to this revision and therefore the quantities could have been included.
2016-02-12 | Design | Striping | BYPASS(O) | 7 | SCOTT | There were fourteen skips (dashed lines) that were initially installed in the merge lane that had to be removed. The striping plan depicted them but it was incorrect based on the newer standard. The standard states to drop the skips when transitioning in a merge lane. It was stated that this is a routine problem on many jobs but many times the plan error is discovered prior to installation. | A change order was issued to have them removed. Better communication between design and traffic could have alerted them to this error in the drawings.
2016-02-12 | Design | Omission | NEW ROUTE(O) | 7 | FAYETTE | Not all of the temporary and permanent striping quantities needed were setup although there was a significant quantity of both included. The designer noted, that some of the additional quantities needed were add-ons and not missed. | A change order was issued for the needed quantities. Better QA/QC may have discovered the need for more of these items prior to bid letting.
2016-02-12 | Design | Omission | NEW ROUTE(O) | 7 | FAYETTE | Not all of the temporary and permanent striping quantities needed were setup although there was a significant quantity of both included. The designer noted, that some of the additional quantities needed were add-ons and not missed. | A change order was issued for the needed quantities. Better QA/QC may have discovered the need for more of these items prior to bid letting.
2016-02-12 | Utilities | Relocation | BYPASS(O) | 7 | SCOTT | A utility relocation delay caused a delay in the construction of a permanent school entrance. A KU utility pole prevented the permanent entrance from being constructed before school started in the fall. | A change order was written to include materials to construct a temporary entrance to accommodate school traffic. Improved project forecasting will allow for more time for relocation efforts; this may reduce the amount of construction delays. Other mechanisms (e.g. contractual agreements) to encourage utility companies to address relocations more expediently may need to be examined.
2016-02-12 | Design | Omission | BYPASS(O) | 7 | SCOTT | Undercutting of unsuitable material was required but this work was not accounted for in the plans. Many times Geotech gives a recommendation for undercutting but did not for this project. No quantity bid items were setup. | A change order was issued to address this effort under an existing Embankment In Place bid item. The rate had to be negotiated. Design and Geotech should review procedures regarding the inclusion of undercutting and its estimate. The project manager should consider including a bid item in order to gate a unit cost in the bid.
2016-02-12 | Design | Communication | NEW ROUTE(O) | 7 | FAYETTE | No quantities of aggregate and filter fabric were included in the bid package for temporary construction entrances that were needed on the project. At the approximate letting time, a Temporary Construction Entrance & Erosion Control Blanket memo (CM 01-13) was issued directing construction entrances to be compensated for their installation. This memo was issued in January 2013 approximately 3 months before the project was let. As stated in the memo, KYTC had been inconsistent in use and payment of temporary construction entrances and erosion control blanket; this memo's intent is to provide guidance and understanding regarding use and payment of these features. | A decision was made by the district to compensate the contractor for materials used (aggregate & filter fabric) for temporary construction entrance installation. Better communication between the designer and Division of Construction may have alerted them to this revision and therefore the quantities could have been included.
2016-02-12 | Design | Communication | BYPASS(O) | 7 | SCOTT | The sound wall was also to serve as a retaining wall with the design of it performed by a subcontractor. Panels on the sound barrier wall began to crack to due pressure from soil backfill. The wall was not designed or approved by KYTC as a retaining structure, although the Bristol Group who designed it was informed (by profiles/cross sections) that soil backfill was to be placed behind it. | An "In House" structural design review of the wall and proposed installation parameters (i.e. soil backfill) would have alerted KYTC personnel to its limitations.
2016-02-12 | Design | Quantities | BYPASS(O) | 7 | SCOTT | The sinkhole that was to be filled, was much larger than depicted on the plans. Conversely there was not enough quantities (concrete, & rebar) setup for proper closure. | A change order was issued for an increase in the required quantities. Site investigation during the planning stages with excavating equipment would have alerted the designers to the approximate size and provided for a more accurate closure estimate.
2016-02-12 | Design | Omission | MAJOR WIDENING(O) | 7 | FAYETTE | Not all of the temporary and permanent striping quantities needed were setup although there was a significant quantity of both included. The designer noted, that some of the additional quantities needed were add-ons and not missed. | A change order was issued for the needed quantities. Better QA/QC may have discovered the need for more of these items prior to bid letting.
2016-02-12 | Design | Railroads | NEW ROUTE(O) | 7 | FAYETTE | AAs the project was near letting and final design preparations were being performed, Norfolk Southern (NS) was contracted and an agreement was reached to build a temporary cofferdam to support Pier 1 only. However, by the time the contractor approached NS to construct the cofferdam, NS's standard had been revised (over just a few months’ time) and they demanded supports for Piers 1 and 2. Although there was documentation regarding the initial agreement, NS would not honor it. | A change order was written for the increase supports (cofferdams) as requested by NS. Perhaps more binding agreements may be considered regarding arrangement with 3rd party companies.
2016-02-12 | Design | Railroads | NEW ROUTE(O) | 7 | FAYETTE | AAs the project was near letting and final design preparations were being performed, Norfolk Southern (NS) was contracted and an agreement was reached to build a temporary cofferdam to support Pier 1 only. However, by the time the contractor approached NS to construct the cofferdam, NS's standard had been revised (over just a few months’ time) and they demanded supports for Piers 1 and 2. Although there was documentation regarding the initial agreement, NS would not honor it. | A change order was written for the increase supports (cofferdams) as requested by NS. Perhaps more binding agreements may be considered regarding arrangement with 3rd party companies.
2016-02-12 | Design | Grade | NEW INTERCHANGE(O) | 7 | CLARK | A 300-foot constructed roadway section was designed without proper drainage. This was discovered only after the base course was placed which was causing water to pond. | Additional asphalt was approved by change order to increase the superelevation allow for the proper roadway drainage. Better QA/QC may have caught this error prior to bid letting.
2016-02-12 | Design | Omission | NEW INTERCHANGE(O) | 7 | CLARK | An existing barn was in the way of construction had to be demolished but was not in the plans. The caption notes should have had this in there as a required effort. | A change order was written for its removal. Better QA/QC could have prevented this from being left off.
2016-02-12 | Design | Evaluations | BYPASS(O) | 7 | SCOTT | It was not realized in the design phase that an existing traffic pole’s based was 2 feet below the proposed final grade of the new highway; the pole's base needed to remain exposed to prevent corrosion. | It was decided to construct a concrete wall around the base to keep the base exposed; a change order was written for this work. This also eliminated the need to adjust the location of the other signal poles.
2016-02-12 | Geotechnical | Unsuitable Material | NEW INTERCHANGE(O) | 7 | CLARK | Ramp B embankment failed as it was nearly complete due to an unsuitable subgrade located over an existing pond. The subgrade excavation was followed as called for in the plans (i.e. undercut 3 feet deep) but during construction a request was made to central office to over excavate (i.e. undercut more than 3 feet deep) due to the “mucky & soupy” nature of the material. Although the construction liaison was in favor, the request was denied. | Additional earthwork effort was approved by a change order after the initial failure of Ramp B. This change order allowed for reconstruction of Ramp B as well as the subgrade to be excavated down to bedrock. The material was taken to an adjacent waste area outside of the constructed roadway. Geotech standards and guidelines may need to reviewed/revised.
2016-02-12 | Design | Communication | MAJOR WIDENING(O) | 7 | FAYETTE | No quantities of aggregate and filter fabric were included in the bid package for temporary construction entrances that were needed on the project. At the approximate letting time, a Temporary Construction Entrance & Erosion Control Blanket memo (CM 01-13) was issued directing construction entrances to be compensated for their installation. This memo was issued in January 2013 approximately 3 months before the project was let. As stated in the memo, KYTC had been inconsistent in use and payment of temporary construction entrances and erosion control blanket; this memo's intent is to provide guidance and understanding regarding use and payment of these features. | A decision was made by the district to compensate the contractor for materials used (aggregate & filter fabric) for temporary construction entrance installation. Better communication between the designer and Division of Construction may have alerted them to this revision and therefore the quantities could have been included.
2016-02-12 | Design | Guardrail | NEW INTERCHANGE(O) | 7 | CLARK | While in construction, it was decided to replace guardrail in three locations (not on the plans) to meet the existing standards for guardrail which require 29 inch height (existing was 27”) and wood/composite spacer blocks (existing was steel.) This was seen as a positive revision to do while on site for the sake of public safety; however, plans did not call for this to be done. | A change order was written for the installation of the guardrail. Better communication between the designers and construction may lead to “positive revisions” in the plans prior to bid lettings.
2016-02-12 | Geotechnical | Unsuitable Material | NEW INTERCHANGE(O) | 7 | CLARK | At Ramp B, the material was undercut by 3 feet as called for in the plans based on geotechnical guidelines; by design, this material was to be used in as embankment fill. However, the material was not suitable which led to an earthwork cost increase. | The material was hauled off and placed in an adjacent waste area. Additional material from the project was brought in and used in its place.
2016-02-12 | Utilities | Delays | NEW ROUTE(O) | 7 | FAYETTE | The AT&T fiber optic line was not moved in time, causing delays to the contractor and resulted in cost increases. | A change order was granted for the more expensive method of excavation around this area. This allowed the project to continue onward without any significant delays. In the future better coordination with the utility companies regarding relocation of lines could eliminated the need for changes.
2016-02-12 | Geotechnical | Unsuitable Material | NEW INTERCHANGE(O) | 7 | CLARK | The plan’s estimate for excavation/embankment quantities were too low for proper roadway construction. Additional excavation was required to undercut and remove New Albany shale and other unclassified materials that were not suitable for roadway construction which lead to increase earthwork costs. | Additional excavation was approved to remove unsuitable materials; these materials were wasted in an adjacent waste area and not in the construction roadway embankment areas.
2016-02-12 | Design | Drainage | MAJOR WIDENING(O) | 7 | FAYETTE | Pipe elevation was wrong at the intersection and could not be installed as called for in the plans. This caused the need to re-route drainage to a nearby proposed ditch. | More detailed detail plans (than what’s currently required by KYTC) at intersections may have eliminated the pipe elevation problem. The consultant stated that years ago bubble diagrams have been used but KYTC has moved away from doing them.
2016-02-12 | Design | Drainage | NEW ROUTE(O) | 7 | FAYETTE | Pipe elevation was wrong at the intersection and could not be installed as called for in the plans. This caused the need to re-route drainage to a nearby proposed ditch. | More detailed detail plans (than what’s currently required by KYTC) at intersections may have eliminated the pipe elevation problem. The consultant stated that years ago bubble diagrams have been used but KYTC has moved away from doing them.
2016-02-12 | Design | Drainage | NEW ROUTE(O) | 7 | FAYETTE | Pipe elevation was wrong at the intersection and could not be installed as called for in the plans. This caused the need to re-route drainage to a nearby proposed ditch. | More detailed detail plans (than what’s currently required by KYTC) at intersections may have eliminated the pipe elevation problem. The consultant stated that years ago bubble diagrams have been used but KYTC has moved away from doing them.
2016-02-12 | Utilities | Communication | NEW ROUTE(O) | 7 | FAYETTE | At the proposed bridge location, KU power lines were not energized for approximately two weeks to allow for KU to build the new towers. This de-energized period also allowed for a window for the piles to be set before the new lines became energized as required. However this 2 week "non-energized window" did not allow enough time to install the bridge piles with the in situ embankment fill. | Granular Embankment was added to the contract via a change order. This allowed the piles to be driven within the two week window. This was much faster than the proposed dirt fill. (It was also noted by the district that more time to install the piles would have been fine had this "time frame issue" not existed.) To facilitate quicker piling installation, limestone screenings were used so they could be set within the 2 week window.
2016-02-12 | Utilities | Relocation | NEW ROUTE(O) | 7 | FAYETTE | The Contractor had planned to use a large crane to build the bridge based on an assumption that utility lines would be out of the way. Because the utility lines were not moved in time, the Contractor needed to use two smaller cranes (presumably with shorter booms), to stay a safe distance (20 feet) from the overhead high voltage transmission lines. | A change order was written for additional compensation for the operation of two smaller cranes. A more descriptive note in the plans may have alerted the Contractor and others to this potential restriction and therefore may have eliminated the need for this change order.
2016-02-12 | Design | Omission | MAJOR WIDENING(O) | 7 | FAYETTE | There were several perforated pipe underdrains included in the design that were not included in the summary sheet and therefore not part of the contract. | Better QA/QC in the design phase could have prevented this omission. Better letting forecasts may have also reduce the chance of this omission from happening. A change order was written to include the required pipes as depicted in the design drawings. (The designer did state that the project was approximately 20 years old and had been on hold for a long period of time they didn't even know if it would get built.) Then on fairly short notice was ask to submit the plans quickly.)
2016-02-12 | Utilities | Communication | NEW ROUTE(O) | 7 | FAYETTE | At the proposed bridge location, KU power lines were not energized for approximately two weeks to allow for KU to build the new towers. This de-energized period also allowed for a window for the piles to be set before the new lines became energized as required. However this 2 week "non-energized window" did not allow enough time to install the bridge piles with the in situ embankment fill. | Granular Embankment was added to the contract via a change order. This allowed the piles to be driven within the two week window. This was much faster than the proposed dirt fill. (It was also noted by the district that more time to install the piles would have been fine had this "time frame issue" not existed.) To facilitate quicker piling installation, limestone screenings were used so they could be set within the 2 week window.
2016-02-12 | Design | Omission | NEW ROUTE(O) | 7 | FAYETTE | There were several perforated pipe underdrains included in the design that were not included in the summary sheet and therefore not part of the contract. | Better QA/QC in the design phase could have prevented this omission. Better letting forecasts may have also reduce the chance of this omission from happening. A change order was written to include the required pipes as depicted in the design drawings. (The designer did state that the project was approximately 20 years old and had been on hold for a long period of time they didn't even know if it would get built.) Then on fairly short notice was ask to submit the plans quickly.)
2016-02-12 | Utilities | Communication | MAJOR WIDENING(O) | 7 | FAYETTE | At the proposed bridge location, KU power lines were not energized for approximately two weeks to allow for KU to build the new towers. This de-energized period also allowed for a window for the piles to be set before the new lines became energized as required. However this 2 week "non-energized window" did not allow enough time to install the bridge piles with the in situ embankment fill. | Granular Embankment was added to the contract via a change order. This allowed the piles to be driven within the two week window. This was much faster than the proposed dirt fill. (It was also noted by the district that more time to install the piles would have been fine had this "time frame issue" not existed.) To facilitate quicker piling installation, limestone screenings were used so they could be set within the 2 week window.
2016-02-12 | Design | Omission | NEW ROUTE(O) | 7 | FAYETTE | There were several perforated pipe underdrains included in the design that were not included in the summary sheet and therefore not part of the contract. | Better QA/QC in the design phase could have prevented this omission. Better letting forecasts may have also reduce the chance of this omission from happening. A change order was written to include the required pipes as depicted in the design drawings. (The designer did state that the project was approximately 20 years old and had been on hold for a long period of time they didn't even know if it would get built.) Then on fairly short notice was ask to submit the plans quickly.)
2016-02-12 | Design | Evaluations | NEW ROUTE(O) | 7 | FAYETTE | To serve the traveling public better and open the road quicker, the contractor proposed changing from lime stabilization to geogrid (w/DGA base). | A change order was written to switch materials from lime stabilization to geogrid/DGA with no increase in cost for this particular project. This provided for speed of construction which thereby allowed for roadway to be potentially opened quicker (as is turned out, the road was not opened quicker due to other utility issues not related to this topic.) Also this change better accommodated construction entrances construction.
2016-02-12 | Design | Evaluations | NEW ROUTE(O) | 7 | FAYETTE | To serve the traveling public better and open the road quicker, the contractor proposed changing from lime stabilization to geogrid (w/DGA base). | A change order was written to switch materials from lime stabilization to geogrid/DGA with no increase in cost for this particular project. This provided for speed of construction which thereby allowed for roadway to be potentially opened quicker (as is turned out, the road was not opened quicker due to other utility issues not related to this topic.) Also this change better accommodated construction entrances construction.
2016-02-12 | Design | Evaluations | MAJOR WIDENING(O) | 7 | FAYETTE | To serve the traveling public better and open the road quicker, the contractor proposed changing from lime stabilization to geogrid (w/DGA base). | A change order was written to switch materials from lime stabilization to geogrid/DGA with no increase in cost for this particular project. This provided for speed of construction which thereby allowed for roadway to be potentially opened quicker (as is turned out, the road was not opened quicker due to other utility issues not related to this topic.) Also this change better accommodated construction entrances construction.
2016-02-12 | Utilities | Delays | MAJOR WIDENING(O) | 7 | FAYETTE | The AT&T fiber optic line was not moved in time, causing delays to the contractor and resulted in cost increases. | A change order was granted for the more expensive method of excavation around this area. This allowed the project to continue onward without any significant delays. In the future better coordination with the utility companies regarding relocation of lines could eliminated the need for changes.
2016-02-12 | Utilities | Relocation | MAJOR WIDENING(O) | 7 | FAYETTE | The Contractor had planned to use a large crane to build the bridge based on an assumption that utility lines would be out of the way. Because the utility lines were not moved in time, the Contractor needed to use two smaller cranes (presumably with shorter booms), to stay a safe distance (20 feet) from the overhead high voltage transmission lines. | A change order was written for additional compensation for the operation of two smaller cranes. A more descriptive note in the plans may have alerted the Contractor and others to this potential restriction and therefore may have eliminated the need for this change order.
2016-02-12 | Utilities | Relocation | NEW ROUTE(O) | 7 | FAYETTE | The Contractor had planned to use a large crane to build the bridge based on an assumption that utility lines would be out of the way. Because the utility lines were not moved in time, the Contractor needed to use two smaller cranes (presumably with shorter booms), to stay a safe distance (20 feet) from the overhead high voltage transmission lines. | A change order was written for additional compensation for the operation of two smaller cranes. A more descriptive note in the plans may have alerted the Contractor and others to this potential restriction and therefore may have eliminated the need for this change order.
2016-02-12 | Utilities | Delays | NEW ROUTE(O) | 7 | FAYETTE | The AT&T fiber optic line was not moved in time, causing delays to the contractor and resulted in cost increases. | A change order was granted for the more expensive method of excavation around this area. This allowed the project to continue onward without any significant delays. In the future better coordination with the utility companies regarding relocation of lines could eliminated the need for changes.
2016-02-02 | Design | Evaluations | RECONSTRUCTION(O) | 4 | HARDIN | The excavated material from the 3 sediment ponds were intended to be used for road embankment construction. However, during construction activities it was determined to be unsuitable for embankment material (it was described to be "topsoil" material.) While additional geotech may have determined this prior to construction, the cost/benefit would have been negligible. | A change order was written to use aggregate that was brought in from an off-site quarry to use as embankment fill.
2016-02-02 | Design | Radius | RECONSTRUCTION(O) | 4 | HARDIN | The entrance detail used on this project (as let) was already contrary to the standard detail. The construction personnel in D4 felt that it was too difficult to turn into from the highway; A vehicle must slow down too much to turn in at a 10 feet radius so they were increased to 15 feet. It should be noted that some have voiced concern that allowing cars to turn in too fast may lead to an increased safety risk to the pedestrians that traverse the driveways. | Consider a change in the standard drawings (RPM-150 AND RPM-152) to better address the rational for this possible revision.
2016-02-02 | Design | Quantities | RECONSTRUCTION(O) | 4 | HARDIN | There was an insufficient amount of sod included in the design to sod the complete R/W area; construction stated there was more area disturbed than what was intended to be as depicted in the design plans. Furthermore, they stated the sod was the most prudent revegetation method for residential areas; it establishes quickly and is most suitable to property owners. | A change order was written to increase the quantity of sod. Solution would be to include sufficient sod quantities (disturbed areas and/or full area within RW/Easements) for residential areas in as-bid plans
2016-02-02 | Design | Quantities | RECONSTRUCTION(O) | 4 | HARDIN | There was not enough striping setup for all of the traffic management during construction; there was more re-striping needed was anticpated for a project of this size. It was stated that striping quantities are a very unpredictable for any project. | A change order was written to increase the quantity of striping. Consider multimple pavement lifts when estimating striping quantity
2016-02-02 | Design | Safety | NEW ROUTE(O) | 4 | HARDIN | Crashes at intersection of Deckard School Road. | Design could have also included sight distances above and beyond ‘minimum’ standard and/or additional signage/rumble striping/etc for the stop controlled approaches. A general solution would simply be to give extra consideration during design to new route intersections with existing roadways as they are historically problematic.
2016-02-02 | Drainage | Drop Box Inlets | RECONSTRUCTION(O) | 4 | HARDIN | The drop box as desgined in the standard drawings does not allow enough room for a I beam as required for under support of the chamber. | A revision to allow for approximatley 2" in the lower chamber would allow room for the I beam to be installed as needed without field revisions. If additional height in chamber is difficult to achieve (i.e. – controlled by outlet elevation downstream) then reinforced cap or other consideration should be given in design.
2016-02-02 | Design | Omission | NEW ROUTE(O) | 4 | HARDIN | Due to realignment of parts of KY 313 as called for in the plans, embankment of material was required. However there was no bid item setup for embankment efforts. | A change order was issued to include "Embankment in Place" as a pay item.
2016-02-02 | Design | Communication | RECONSTRUCTION(O) | 4 | HARDIN | The “Disturbed Limit” definition is misunderstood by some highway professionals. | The “Disturb Limit” is intended only to represent the edge of required earthwork only and is the only thing feasible to model in design. RW/Easement limits are set back from the disturb limits to account for the true work/revegetation limits.
2016-02-02 | Design | Omission | NEW ROUTE(O) | 4 | HARDIN | "Clean sinkholes" bid item was not included. | A change order was issued to include this item.
2016-02-02 | Drainage | Sheet Flow | NEW ROUTE(O) | 4 | HARDIN | During construction an addition was made to install wedge curbs to prevent erosion on fill slope. | A design change should be considered to add wedge curbs to prevent erosion on fill slope. Open discussions between design and construction professionals should be performed to determine a precise technical / emperical rational as to there use.
2016-02-02 | Design | Grade | RECONSTRUCTION(O) | 4 | HARDIN | Profile grade didn't allow for building ADA ramps at 2% maximum cross slopes. | Additional layout and modeling during design and/or a revision of standard details to account for greater range of field conditions are two possible solutions.
2016-02-02 | Drainage | Sheet Flow | NEW ROUTE(O) | 4 | HARDIN | DGA median was washing out from runoff. | Recommend chip & seal of full DGA median width instead of only 2’ down from slope break as is current standard practice.
2016-02-02 | Design | Quantities | RECONSTRUCTION(O) | 4 | HARDIN | The was not enough crush stone (CSB) base setup to meet all of the construction needs. There were numerous areas that had yielding areas at subgrade level that needed excavated and filled. The also needed more space to accommodate for a reasonable slope in MOT phasing. | A change order was written to increase the amount of CSB needed for proper subgrade strength. Solution would be to include an additional quantity of CSB for areas expected to be a poor soil quality (i.e. existing ditchlines) as well wedging/MOT considerations above and beyond calculated quantities based on sections.
2016-02-02 | Utilities | Communication | NEW ROUTE(O) | 4 | HARDIN | The 4 pole traffic signal system had to be revised due to a conflict with an existing transmission line. Division of Traffic Operations was not aware of the transmission line. | A change order was issued to revise the installation of this feature. This included a bore and jack in the main line and reducing the number of poles from 4 to 3. Development staff should communicate utility design constraints to signal designers.
2016-02-02 | Utilities | Relocation | RECONSTRUCTION(O) | 4 | HARDIN | There were many areas were the utilities were not relocated in the proper spots which contributed to additional efforts during construction. | The contractor had to move around the project in several times to allow for relocation of utilities. It was mentioned that the KYTC personnel could oversee & document (i.e. inspection of work) utitlities when the are actually being relocated; subsequently, the plans could be rechecked prior to letting for possible utility conflicts. Need a set of "as-builts" plans that have field verified x,y, & z locations. Still this solution is limited by staffing levels and project schedule concerns
2016-02-02 | Design | Omission | NEW ROUTE(O) | 4 | HARDIN | To construct a depressed median as designed, an existing raised median (with curb & gutter) had to be removed but no bid items were setup for this effort. | A change order was issued to include "Remove Curb & Gutter", "Remove Pipe" and "Remove Intergral Curb and Replace" as a pay items.
2016-01-26 | Utilities | Omission | SPOT IMPROVEMENTS(O) | 10 | ESTILL | Unknown utilities (water line) location was discovered during construction. To construct the spot improvements as designed, replacement/relocation of this feature had to be addressed. | A change order was written to relocate this line. For this project & future projects, field walks, speaking with nearby residences and the utility companies may reduce the number of unknown utilities that may be encountered.
2016-01-26 | Design | Omission | RECONSTRUCTION(O) | 10 | MENIFEE | Although there was # 2 Stone setup for the bridge end embankments, the quantity setup was insuffienct due to incorrect estimate calculation of the actual geometric parameters in the field. Designer noted that it was his first design project and the "inexperience factor" was the reason for the quantity shortage. The quantity was calculated using the average end area method, but was not properly implemented (i.e. it was zerod out too quickly) | A change order was written to allow for the needed quanitites to complete the work as designed. Average End Area method is an acceptable mechanism to calculate quantities such as these when implemented properly. Additional independent review may have caught this error.
2016-01-26 | Utilities | Omission | SPOT IMPROVEMENTS(O) | 10 | ESTILL | Unknown utilities (water line) location was discovered during construction. To construct the spot improvements as designed, replacement/relocation of this feature had to be addressed. | A change order was written to relocate this line. For this project & future projects, field walks, speaking with nearby residences and the utility companies may reduce the number of unknown utilities that may be encountered.
2016-01-26 | Design | Evaluations | SPOT IMPROVEMENTS(O) | 10 | ESTILL | There was no guardrail setup for the traffic diversion that had a drop off on the outslope side. Based on reasonable transportation practice, guardrails should always be placed where roadway outslopes are 3:1 or greater. In this instance, the outslope became steeper than originally designed because additional excavation/cribbing removal was required to address the poor subgrade conditions. | A change order was written for the required guardrail.
2016-01-26 | Design | Evaluations | RECONSTRUCTION(O) | 10 | MENIFEE | At the beginning of the project, where new road construction transitioned to the existing road a change was made from lime stablization to grandular stabilzation. This was needed as the existing road rock base was "bleeding water" into the new road construction. | Due to the saturated subsurface conditions, a decision was made in construction to switch from lime stabilization to grandular stabilization for about 200 feet. The switch to grandular was done to provide for a more stable roadbed than what could be achieved with lime stabilization.
2016-01-26 | Design | Striping | SPOT IMPROVEMENTS(O) | 10 | ESTILL | Thermoplastic crossing hatching was not part of the orginal design plans. At the time the plans were completed, the former Branch Manager's professional preference (for reasons not explained) was to use paint instead of use of this item. | At the time the project was constructed, new leadership, both in design and construction perferred using thermoplastic. A change order was done to include thermo cross hatching. Compared to painted sufaces, it lasts much longer (perhaps years) & and is easier to retrace. In short, much less maintenance effort is associated with this product vs painted.
2016-01-26 | Design | Evaluations | SPOT IMPROVEMENTS(O) | 10 | ESTILL | The existing rail cribbing held water beneath the existing roadway and planned traffic diversion area. Due to this area being saturated a base failure occurred and had to be address during construction. | A change order was written to address additional excavation and embankment work in this area to properly support the new road alignment and temporary traffic diversion area. Additional core drilling may have alerted design to the subsurface saturation that existed in this area.
2016-01-26 | Construction | Revisions | RECONSTRUCTION(O) | 10 | MENIFEE | During construction, it was decided to use an adjacent area (previous lumber mill location) owned by KYTC for borrow material. This area was transformed into a Menifee Maintenance Garage seat and this was the objective of this revision. Some of the material from borrowed from this area was not suitable for roadway embankment fill but needed to be excavated to get the proper grade for the maintenance lot and roadway embankment needs. | A change order was written to include this area for excavation and subsequent embankment yardage. It is noted that material which was not suitable for roadway embankment was placed outside the road construction area. It was paid for at a $0.25/CY less rate than the material used in the roadway embankment
2016-01-26 | Geotechnical | Investigation | SPOT IMPROVEMENTS(O) | 10 | ESTILL | There was not enough durable rock exacavated during roadway alignment construction efforts. It was anticpated that more durable rock would be on site that could be used for road embankment construction. This was based one core sample. | A change order was written for additional quarried rock to be delivered to the site and used for embankment construction. During design/geotechnical phase of the project, taking more core samples may have provided a more accurate estimate of durable rock actually available. Utimately, cost wise it did not make any difference as the quarried rock was needed for proper construction anyway. Still, from a design prespective, a more accurate estimate may have been developed with more geotech information.
2016-01-26 | Geotechnical | Investigation | SPOT IMPROVEMENTS(O) | 10 | ESTILL | There was not enough durable rock exacavated during roadway alignment construction efforts. It was anticpated that more durable rock would be on site that could be used for road embankment construction. This was based one core sample. | A change order was written for additional quarried rock to be delivered to the site and used for embankment construction. During design/geotechnical phase of the project, taking more core samples may have provided a more accurate estimate of durable rock actually available. Utimately, cost wise it did not make any difference as the quarried rock was needed for proper construction anyway. Still, from a design prespective, a more accurate estimate may have been developed with more geotech information.
2016-01-26 | Design | Evaluations | SPOT IMPROVEMENTS(O) | 10 | ESTILL | The existing rail cribbing held water beneath the existing roadway and planned traffic diversion area. Due to this area being saturated a base failure occurred and had to be address during construction. | A change order was written to address additional excavation and embankment work in this area to properly support the new road alignment and temporary traffic diversion area. Additional core drilling may have alerted design to the subsurface saturation that existed in this area.
2016-01-26 | Design | Evaluations | SPOT IMPROVEMENTS(O) | 10 | ESTILL | There was no guardrail setup for the traffic diversion that had a drop off on the outslope side. Based on reasonable transportation practice, guardrails should always be placed where roadway outslopes are 3:1 or greater. In this instance, the outslope became steeper than originally designed because additional excavation/cribbing removal was required to address the poor subgrade conditions. | A change order was written for the required guardrail.
2016-01-26 | Design | Drainage | RECONSTRUCTION(O) | 10 | MENIFEE | Per construction personnel, erosion control blanket (ECB) installation is not a reialble erosion control mechanism at corner of embankment fill slopes slopes and ditch lines on steep (actual % grade undefined) fill slopes therefore Class III Channel was used in its place. This was contrary to the design plans with depicted ECB. | A change order was written for additional channel lining needed to be placed in these areas in lieu of ECB.
2016-01-26 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 10 | MENIFEE | Water line from adjacent road project was relocated and crossed alignment of this one. It was not reflected in the the plans because because this design had been completed before unknown utilities (water lines / firehydrant) were discovered during construction at several locations. To construct the road as designed, relocation and replacement of these feature had to be addressed. Calling 811 did provide some valuable information by identifiying utility locations in the area, location of the underground lines are still not reiable. This is due to a historical lack of accurate record keeping by utility companies. | A change order was written for the utilities to be moved to facilitate the construction of the roadway as designed. When projects have a large gap between design and construction a field walk and/or survey can identify critical site changes. Contacting nearby residences and the utility companies may reduce the number of unknown underground utilities that will be encoutered.
2016-01-26 | Design | Striping | SPOT IMPROVEMENTS(O) | 10 | ESTILL | Thermoplastic crossing hatching was not part of the orginal design plans. At the time the plans were completed, the former Branch Manager's professional preference (for reasons not explained) was to use paint instead of use of this item. | At the time the project was constructed, new leadership, both in design and construction perferred using thermoplastic. A change order was done to include thermo cross hatching. Compared to painted sufaces, it lasts much longer (perhaps years) & and is easier to retrace. In short, much less maintenance effort is associated with this product vs painted.
2016-01-26 | Drainage | Pipe Sizing | RECONSTRUCTION(O) | 10 | MENIFEE | The roadway embankment from Sta 229+50 to 243+00 was constructed in a valley shaped drain. Because of more saturated conditions, it was determined during construction that a 6" dia. pipe rather than the 4" dia. pipe, would be needed to carry the existing volume of water. | A change order was written for the 6" larger pipe. During the design phase, a field walk determined the size of pipe needed to properly carry the volume would need to be larger.
2016-01-13 | Utilities | Coordination | MAJOR WIDENING(O) | 3 | SIMPSON | Abandoned pipes had to be removed to facilitate construction/installation of the RCBC and excavation backslopes. The pipes were determined to be "Abestos Cement" and therefore were much more expensive to remove. This material was not identified by the utility section & project manager during the initial phase of this project. | A change order was written for the proper removal and disposal. In the future, better identification during initial phases of a project will reduce unknowns discovered on projects and provide for better estimating.
2016-01-13 | Design | Omission | NEW ROUTE(O) | 3 | BARREN | A sewer line force main needed to be relocated to facilitate the construction of a field entrance. | A change order was submitted to relocate the force main at a lower elevation thereby allowing the field entrance to be constructed in an approximate 25 foot cut. It was a five year period between the time the project had been design and subsquently constructed. A QA/QC review of the plans and recent non highway related construction adjacent to the right of way may have revealed this issue prior to highway construction work commencing.
2016-01-13 | Proposal | Quantities | MAJOR WIDENING(O) | 3 | SIMPSON | Although there was enough asphalt setup on the completed design plans & documents, the entire quantity needed was not reflected in the contruction procument documents. | A change order was written to include the required amount as designed. Recently a check list from the designer to Plan Processing is required and may eliminate (or at least reduce the chance of) bid items being inaverdently revised during the transfer processs. Still it is the strict responsibility of Plan Processing and Construction Procurement that all bid items be accurately stated as received from Design.
2016-01-13 | Design | Erosion Control | NEW ROUTE(O) | 3 | BARREN | The turf reinforcement mat (TRM) lined ditches as designed continued to wash out during construction. It was decided to lined them with Class III channel lining at steep locations where wash outs were occuring. It should be noted that in July 2009 the central office was advocating the use of this product. By the time the project was let, in September 2012 not enough emperical data regarding the effectiveness of the product existed. | A change order was issued for the appropriate amount of channel lining needed to line the washed out areas. Designers need to be mindful on steep slopes that turf reinforced ditches are hard to get established. Many times aggregate lined ditches are needed based on field conditions. (As of early 2016, feedback from District 3 suggests using the product very limited way for reasons stated herein.)
2016-01-13 | Design | Omission | NEW ROUTE(O) | 3 | BARREN | There was no Mountable Median in the quantities documents. It was shown on the plan sheet but not included in the quantities. | A change order was issued to include the construction of it. A QA/QC review of the plans may have prevented this omission.
2016-01-13 | Design | Survey | MAJOR WIDENING(O) | 3 | SIMPSON | Additional Pipe had to be placed due as the pipe as designed was daylighting; the existing drainage easement was too high, efforts failed to negotiate to expand the easement. | A change order was written for additional pipe to elminate the need to expand the drainage easement. This allowed roadway drainage to properly flow to a location further south. Field investigation and surveying to verify conditions of old plans is recommended.
2016-01-13 | Design | Coordination | MAJOR WIDENING(O) | 3 | SIMPSON | More DGA was required to construct the subbase to properly support, the curb, concrete entrance and wedge out areas. This was done to keep design consistancy in KY & Tenn. | A change order was written for additional DGA. Tolerances within the survey areas are not accurate enough. Road work of this magnitude could begin adding an additional 5% over what the geometric calculation yield.
2016-01-13 | Design | Quantities | NEW ROUTE(O) | 3 | BARREN | The design plans called for Granular Embankment & Granular Pile Core for stability under both Bridge End Bents. These were needed for stability at these locations to support the bridge ends but were not setup in the contract. | A change order was written to increase the quanitites of granular backfill. A QA/QC review of the plans and quantities prior to letting may have caught this error.
2016-01-13 | Design | Coordination | MAJOR WIDENING(O) | 3 | SIMPSON | Dense Grade Aggregate (DGA) was used in place of Crushed Stone Base (CSB) as orginally setup for the Tennessee transition part of the roadway. Construction perferred the use of DGA in the transition area to eliminate a bid item and reduce costs. Since the area was to be reworked by TDOT in the near future, it was less expensive to place DGA yet served the purpose for short term needs. It should be pointed out, the KYTC design guildlines call for CSB due to its increased drainage capacity in situations where no underdrains are being place--as was the case for the transition area. The designer(s) did coordinate with TDOT and were aware that the transition area would be reworked in the near future. | A change order was written to trade these materials out. Coordination between Design and Construction to find ways to combine bid items for better prices may have prevented this need to swap out materials as a cost saving measure.
2016-01-13 | Design | Coordination | NEW ROUTE(O) | 3 | BARREN | It was decided during construction activities, that concrete approach slabs were needed to prevent settlement at the bridge approaches. | A change order was written to include concrete and reinforcement steel to construct the slabs. More coordination/understanding is needed between design and construction as to what is required to prevent settlement at embankments that meet bridge approaches. Studys have been conducted by both KYTC and the transportation center regarding approach slabs and there effective but no consensus has been reached.
2016-01-13 | Proposal | Quantities | MAJOR WIDENING(O) | 3 | SIMPSON | Although the Signing Plans were included by design and in the record set when sent to construction procurement, the Signing bid item did not make it into the proposal. | A change order was written for sign installation performed by the contractors. Recently a check list from the designer to Plan Processing is required and may eliminate (or at least reduce the chance of) bid items being inaverdently dropped during the transfer processs. Still it is the strict responsibility of Plan Processing and Construction Procurement that all bid items be included as received from Design.
2016-01-13 | Design | Omission | MAJOR WIDENING(O) | 3 | SIMPSON | A water well was discovered within the construction area and needed to be plugged for roadway embankment stability and sidewalk intigrity. | A change order was written to plug the well off. During the preliminary design phase, field walks and discussions with nearby property owners can be performed to better identify such quasi unseen features.
2016-01-13 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 3 | BARREN | There were restrictions for oversized loads on this project that were not observed. | In the plans include appropriate advanced signage for width restrictions and indicate those in the maintenance of traffic plans (MOT). This may be considered a way to reduce the occurance of this problem. Other possible ways to reduce or perhaps elminate this problem are outside of the design-construction realm.
2014-01-10 | Geotechnical | Embankment Stabilization | BRIDGE REPLACEMENT(P) | 6 | GRANT | During construction a combination of heavy precipitation and poor soils caused the excavated walls and slopes leading to the end bents to become saturated and slide into the pier footing excavation. The geotech report indicated that the foundation consi | To stabilize the area, the excavated pits for the pier footings were cleaned out and backfilled with #2 stone. Footing drains were installed to drain water away from the pier footings since the bottom of the footing excavations were lower than the ditch
2014-01-10 | Construction | Delays | BRIDGE REPLACEMENT(P) | 6 | PENDLETON | Before the project was completed a routine bridge inspection of the existing bridge found section loss in several floor beams. The weight limit was reduced to 3 tons from 15 tons. The detour around the bridge was 30 miles. The contractor would no longe | KYTC decided that it would be more beneficial to reinforce the existing bridge for a short time than to have a long delay on the project. They drilled holes and put in plates on critical members of the bridge. There may not be a way to avoid this issue
2014-01-10 | Pavement | Approaches | BRIDGE REPLACEMENT(P) | 6 | GRANT | The newly constructed profile from US 25 to the new Stringtown bridge was on a down grade. When the radius was marked in the field it was discovered that it would result in a very steep turning approach to the bridge. | The newly constructed roadway alignment from US 25 to the new Stringtown Rd Bridge was raised in elevation to prevent the steep turning approach. Occasionally development sheets are needed, even on a rural roadway project to fully understand how an appro
2014-01-10 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 6 | GRANT | The contractor discovered a sewer leak during construction. While benching the roadway the contractor got within a few inches of the force main. The force main was on the plans and located. It was not cut, but equipment got close enough that the weigh | A small portion of force main was relocated and a new casing was installed under the roadway to fix the problem. It’s important for designers to consider constructability when working near existing utilities.
2014-01-10 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 6 | PENDLETON | An existing sanitary sewer line was discovered in the intended path of the 18” storm sewer. | Since there were space limitations and there was a minimal slope in the gravity sewer line it was decided to reinstall the storm sewer 1.5 feet from the initial design. The only solution for such instances is more thorough subsurface investigations and “
2014-01-10 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 6 | GRANT | The contractor was significantly delayed by the railroad on the demolition of old Stringtown Bridge. Granted track time was considerably less than planned and often was changed at the last minute without reasonable notification. | An Administrative Settlement was paid to the contractor for labor and equipment cost resulting from railroad delays.
2014-01-10 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 6 | PENDLETON | During the relocation of the water main at KY 159 a sanitary Sewer service (4”PVC) was discovered under the road within the construction area Further investigation determined that the line did not meet current regulations. | KYTC and the city reached an agreement to add the sewer line to the project. An 8” sewer line was run out to connect it.
2014-01-10 | Utilities | Communication | BRIDGE REPLACEMENT(P) | 6 | GRANT | The project was let and awarded without having final approved plans from the railroad. Upon final review by the railroad several revisions were made. The time needed to redesign the crash walls and bridge resulted in significant delays to the start of t | Good communication can help to minimize project schedule disruptions. Early and consistent communication is critical to successful railroad coordination.
2014-01-10 | Geotechnical | Embankment Stabilization | BRIDGE REPLACEMENT(P) | 6 | PENDLETON | The embankment on the approach on the East side of the bridge demonstrated yielding subgrade. The embankment material chosen by the contractor was installed with > 95% compaction of the proctor and within tolerance of the optimum moisture, but there were | KYTC Geotech recommended two feet of crushed aggregate no.2 with type IV geotextile fabric and under drains to stabilize the embankment. A post construction review attendee recommended providing a quantity of material to mechanically stabilize the subg
2014-01-10 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 6 | GRANT | Saturated subgrade material was discovered when existing pavement was removed in order to connect the new Stringtown Rd alignment. | The poor material was removed. Geogrid reinforcement, #2 stone and geotextile fabric was used to establish a suitable subgrade to place new pavement. Provisions for subgrade are often necessary when disturbing existing roadbeds.
2014-01-09 | Structures | Communication | RECONSTRUCTION(O) | 6 | BOONE | A retaining wall was constructed adjacent to a church with an approximate 10 ft. wall height. This presents a hazard to individuals near the wall. The fence was mentioned in a roadway plan sheet note and depicted on the cross sections, however, it was n | A change order was written to include the fencing on the project. Better coordination must occur to ensure that work items are uniformly represented on the plan sets and included in the project totals. Additionally, a standard drawing that could be made
2014-01-09 | Design | Elevations | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The existing roadway elevations did not match the plan set, thus causing the planned elevations to be unachievable when attempting to maintain a minimum overlay thickness. This caused significant overrun of the asphalt bondbreaker | On the second half of the project extensive redesign of the profile was performed and was coupled with milling to help achieve more consistent overlay depths.
2014-01-09 | Design | Elevations | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The existing roadway elevations did not match the plan set, thus causing the planned elevations to be unachievable when attempting to maintain a minimum overlay thickness. This caused significant overrun of the asphalt bondbreaker | On the second half of the project extensive redesign of the profile was performed and was coupled with milling to help achieve more consistent overlay depths.
2014-01-09 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | In overlay sections the roadway elevations become higher and cause shoulder rework. Given the rework necessary and the proximity of the roadway ditch it became impossible to properly construct the shoulder widening for the Guardrail End Treatment Ty 4A. | The end treatments on the project were almost completely changed to Guardrail End Treatment Ty 1. When determining guardrail end treatment types, it's important to consider not only the perceived safest option but also the site conditions and the practica
2014-01-09 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | When the existing shoulders were removed the existing subgrade was not suitable for pavement construction. When placed, the asphalt would not bridge the tenderness of the saturated subgrade. Time was of the essence for this project, not allowing time for | The Contractor and KYTC agreed to stablize the existing shoulder subgrade with cement stablization. When time is of the essence, it's important for Project Development staff to fully investigate existing conditions and make provisions to accommodate site
2014-01-09 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | When the existing shoulders were removed the existing subgrade was not suitable for pavement construction. When placed, the asphalt would not bridge the tenderness of the saturated subgrade. Time was of the essence for this project, not allowing time for | The Contractor and KYTC agreed to stablize the existing shoulder subgrade with cement stablization. When time is of the essence, it's important for Project Development staff to fully investigate existing conditions and make provisions to accommodate site
2014-01-09 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | In overlay sections the roadway elevations become higher and cause shoulder rework. Given the rework necessary and the proximity of the roadway ditch it became impossible to properly construct the shoulder widening for the Guardrail End Treatment Ty 4A. | The end treatments on the project were almost completely changed to Guardrail End Treatment Ty 1. When determining guardrail end treatment types, it's important to consider not only the perceived safest option but also the site conditions and the practica
2014-01-09 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | In overlay sections the roadway elevations become higher and cause shoulder rework. Given the rework necessary and the proximity of the roadway ditch it became impossible to properly construct the shoulder widening for the Guardrail End Treatment Ty 4A. | The end treatments on the project were almost completely changed to Guardrail End Treatment Ty 1. When determining guardrail end treatment types, it's important to consider not only the perceived safest option but also the site conditions and the practica
2014-01-09 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | In overlay sections the roadway elevations become higher and cause shoulder rework. Given the rework necessary and the proximity of the roadway ditch it became impossible to properly construct the shoulder widening for the Guardrail End Treatment Ty 4A. | The end treatments on the project were almost completely changed to Guardrail End Treatment Ty 1. When determining guardrail end treatment types, it's important to consider not only the perceived safest option but also the site conditions and the practica
2014-01-09 | Design | Intersection | RECONSTRUCTION(O) | 6 | BOONE | Development sheets weren't supplied in the plan set thus causing construction of an intersection with mainline and approach road difficult. Curb & Gutter were present on the project. | A change order was written to reconstruct the radius and provide a drainage structure. Development sheets are encouraged for mainline and approach roads as well as large entrances to assist in accurately constructing the intersection, especially on urban
2014-01-09 | Maintenance of Traffic | Safety | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The original MOT plan did not allow for an acceleration lane for on ramps creating serious opportunity for conflict. | The Contractor and KYTC constructed a longer slip ramp to allow a short acceleration and improve safety for motorists on the project.
2014-01-09 | Structures | Retaining Walls/MSE | RECONSTRUCTION(O) | 6 | BOONE | At the end of the retaining walls the wall height was terminated at 6 ft. This presents a problem when the wall is adjacent to sidewalk causing sheet flow at the end of the wall to spill onto the sidewalk and create a hazard in freezing temperatures. | A change order was written to extend the retaining wall down to a much shorter height and tie a paved ditch into a nearby drainage box.
2014-01-09 | Maintenance of Traffic | Safety | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The original MOT plan did not allow for an acceleration lane for on ramps creating serious opportunity for conflict. | The Contractor and KYTC constructed a longer slip ramp to allow a short acceleration and improve safety for motorists on the project.
2014-01-09 | Construction | Coordination | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | This project was not entered in SiteManager, KYTC's construction documentation software, for an extended period of time causing backup of documentation. This software processes information to generate Contractor pay estimates. | Expedited entry of projects of this size and nature into SiteManager are critical for sucessful project documentation by KYTC's Construction staff.
2014-01-09 | Design | Drainage | RECONSTRUCTION(O) | 6 | BOONE | When constructing the urban typical on this project the subsurface drainage became trapped with little opportunity for outletting. | A change order was written and KYTC requested edge drains be constructed and outletted to curb box inlets. Subsurface drainage consideration is very important especially in areas with significant grade or in cut areas on urban templates.
2014-01-09 | Construction | Coordination | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | This project was not entered in SiteManager, KYTC's construction documentation software, for an extended period of time causing backup of documentation. This software processes information to generate Contractor pay estimates. | Expedited entry of projects of this size and nature into SiteManager are critical for sucessful project documentation by KYTC's Construction staff.
2014-01-09 | Structures | Retaining Walls/MSE | RECONSTRUCTION(O) | 6 | BOONE | The 4" weep holes that are usually cast into retaining walls were intentionally omitted on this project. Installation of the weep holes adjacent to sidewalk could potentially cause seepage onto the walk and during freezing temperatures cause a hazard. | A change order was written to provide for drainage of the retaining wall backfill via a french drain including a perforated pipe and outletted into a ditch with a perforated pipe headwall. Weep holes can cause seepage and isolated slick spots during peri
2014-01-09 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 6 | BOONE | The planned locations of traffic signal strain poles @ the intersection of US 42, Pleasant Valley Rd. & Gunpowder Rd. interfere with the locations of existing utilities. | The signals had to be relocated to avoid the utility. Thorough investigation of existing utilities is important when planning construction activity.
2014-01-09 | Pavement | Design | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | Due to the variation of depth of bondbreaker, conventional anchoring of load transfer assemblies became difficult. Ordinary nails used to anchor assemblies into existing concrete were not effective on areas with substantial asphalt bond breaker. | It's important for designers to consider site conditions and recommend appropriate materials when possible. When anchoring load transfer assemblies all fasteners and methods are not equal and perform differently in asphalt versus concrete.
2014-01-09 | Pavement | Design | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | Due to the variation of depth of bondbreaker, conventional anchoring of load transfer assemblies became difficult. Ordinary nails used to anchor assemblies into existing concrete were not effective on areas with substantial asphalt bond breaker. | It's important for designers to consider site conditions and recommend appropriate materials when possible. When anchoring load transfer assemblies all fasteners and methods are not equal and perform differently in asphalt versus concrete.
2014-01-09 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 6 | BOONE | Bridge deck overlays were added to the scope of this project but the duration of time needed for the work was not provided in the MOT plan. | It's important for designers to fully consider the items of work and the duration necessary. When scope is expanded and work types unique to roadway projects are included, it's important to discuss their features with professionals familiar with the work
2014-01-09 | Pavement | Joint Sealing | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The Contractor and the KYTC had various construction related issues using silicon joint sealing on this project due to the sensitivity of the effectiveness of the product with regard to constructability. | The Contractor and KYTC in District 6 recommend the use of hot poured asphalt joint sealer based on their experience from both a constructability and a long-term maintenance aspect.
2014-01-09 | Utilities | Relocation | RECONSTRUCTION(O) | 6 | BOONE | An overhead utility pole was relocated within the cut limits necessary to construct the retaining wall. | The pole had to be relocated outside the limits of the excavation for installation of the wall and then relocated again upon completion of the wall. With better communication, it may have been possible to provide a temporary relocation of the pole until c
2014-01-09 | Design | Survey | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The existing roadway elevations did not match the plan set, thus causing the planned elevations to be unachievable when attempting to maintain a minimum overlay thickness. The survey work originally consisted of obtaining measurements along key locations | The designer utilized mobile LiDAR to obtain a more accurate survey with which to produce achievable grades for the pavement. When traffic congestion will not allow for conventional survey methods to occur safely, LiDAR is a solution that exists and can h
2014-01-09 | Drainage | Retention Basin | RECONSTRUCTION(O) | 6 | BOONE | Existing drainage from an off R/W detention base overflow outlet caused washing on R/W. No plan provisions were made to accommodate the drainage from the retention basin. | A change order was written and the Contractor constructed a paved ditch to intercept this drainage and direct it to a drop box inlet. Examination of existing drainage patterns both within the R/W footprint and beyond is critical to successfully accommoda
2014-01-09 | Maintenance of Traffic | Clearances | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | One phase of the MOT plan opened a traffic lane adjacent to a pier cap without adequate vertical clearance, thus creating a dangerous situation. | The Contractor and KYTC closed the lane leaving only one lane of traffic open for several weeks. It's important for designers to consider site conditions thoroughly when developing MOT plans.
2014-01-09 | Maintenance of Traffic | Clearances | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | One phase of the MOT plan opened a traffic lane adjacent to a pier cap without adequate vertical clearance, thus creating a dangerous situation. | The Contractor and KYTC closed the lane leaving only one lane of traffic open for several weeks. It's important for designers to consider site conditions thoroughly when developing MOT plans.
2014-01-09 | Design | Lighting | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The location of the installed light poles are located within the clear zone. | The Contractor installed guardrail to shield the obstacle. It's important for designers to exclude obstacles from the clear zone unless constraints don't allow and shielding should then be considered.
2014-01-09 | Design | Plans | RECONSTRUCTION(O) | 6 | BOONE | Plans give the impression and grades to indicate a cut along US 42 and reconstruct the intersection. This would cause significant MOT difficulty and user delay. | A Construction Revision was generated to revise grades along KY 237 to tie into the existing grades to US 42.
2014-01-09 | Design | Lighting | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The location of the installed light poles are located within the clear zone. | The Contractor installed guardrail to shield the obstacle. It's important for designers to exclude obstacles from the clear zone unless constraints don't allow and shielding should then be considered.
2014-01-09 | Pavement | Joint Sealing | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The Contractor and the KYTC had various construction related issues using silicon joint sealing on this project due to the sensitivity of the effectiveness of the product with regard to constructability. | The Contractor and KYTC in District 6 recommend the use of hot poured asphalt joint sealer based on their experience from both a constructability and a long-term maintenance aspect.
2014-01-09 | Utilities | Delays | RECONSTRUCTION(O) | 6 | BOONE | This project was let prior to all utility agreements being in place with no relocations completed to utilize funding that was set to expire. | No viable solution is available for this situation, short of delaying project letting to allow time for utility agreements/relocations to take place and applying impact notes detailing an expected clearance date.
2014-01-09 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 6 | BOONE | Weathered rock was encountered near footing elevation for a 3-sided culvert to be constructed. Manufacturer's recommendations required 2 ft. embedment of the footings into rock. | A change order was written to provide mass concrete to increase the depth of the footing down to unweathered rock elevation and provide scour protection for the footing. It's important that thorough investigations be made of existing conditions to set fo
2014-01-09 | Structures | Plans | RECONSTRUCTION(O) | 6 | BOONE | Due to the given foundation elevation for the retaining wall, in many locations several feet of retaining wall was buried. | The Post Construction Review attendees recommended stepping the foundation or providing a gradual rise to reduce the cost of the wall, by reducing the area of retaining wall necessary.
2014-01-09 | Structures | Quantities | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The latex overlay overrun significantly due to the depth of existing foreign overlay being substantially more than that indicated on the plans. | A change order was written to increase the quantity of the latex overlay material. It's important to investigate existing conditions thoroughly when estimating overlay quantities to avoid potential delays and costly change orders.
2014-01-09 | Structures | Quantities | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The latex overlay overrun significantly due to the depth of existing foreign overlay being substantially more than that indicated on the plans. | A change order was written to increase the quantity of the latex overlay material. It's important to investigate existing conditions thoroughly when estimating overlay quantities to avoid potential delays and costly change orders.
2014-01-09 | Design | Survey | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The existing roadway elevations did not match the plan set, thus causing the planned elevations to be unachievable when attempting to maintain a minimum overlay thickness. The survey work originally consisted of obtaining measurements along key locations | The designer utilized mobile LiDAR to obtain a more accurate survey with which to produce achievable grades for the pavement. When traffic congestion will not allow for conventional survey methods to occur safely, LiDAR is a solution that exists and can h
2014-01-09 | Design | Borrow/Waste | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The Contractor and KYTC agreed to allow the use of recycled concrete to replace DGA Base on the shoulders of the pavement to reduce waste of the existing concrete in the full depth pavement reconstruction areas. | This innovation reduced waste on the project and the Contractor and local KYTC personnel were very satisfied with the performance of the concrete, which was crushed, graded to DGA standards and pugged for placement. All parties recommended this concept on
2014-01-09 | Design | Borrow/Waste | PAVEMENT REHAB-INT(P) | 6 | CAMPBELL | The Contractor and KYTC agreed to allow the use of recycled concrete to replace DGA Base on the shoulders of the pavement to reduce waste of the existing concrete in the full depth pavement reconstruction areas. | This innovation reduced waste on the project and the Contractor and local KYTC personnel were very satisfied with the performance of the concrete, which was crushed, graded to DGA standards and pugged for placement. All parties recommended this concept on
2014-01-09 | Design | Drainage | RECONSTRUCTION(O) | 6 | BOONE | When medians were constructed for this project the area was excavated to earth subgrade adjacent to the existing pavement structure. Subsequently, drainage from below the existing pavement migrated to the CSB placed under the new median and seeped from th | A change order was written and underdrains were strategically placed to remove drainage from the subbase aggregate layer of the median. When widening pavements, it's important for designers to fully consider subgrade drainage and provide accommodations.
2013-11-07 | Design | Adjacent Projects | I-CHANGE RECONST(O) | 5 | JEFFERSON | This project provided for some widening on I-265 via improvement of the acceleration lane of US 60 to I-265. However, it did not extend to I-64. Future plans for work on the I-64/ I-265 interchange provided a an additional lane between the two interchan | A change order was written to include this lane extension work in the US 60/ I-265 project to achieve the improved capacity at a much quicker date in time. It’s important for designers to consider the long term planning for an area when determining the
2013-11-07 | Design | Adjacent Projects | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | This project provided for some widening on I-265 via improvement of the acceleration lane of US 60 to I-265. However, it did not extend to I-64. Future plans for work on the I-64/ I-265 interchange provided a an additional lane between the two interchan | A change order was written to include this lane extension work in the US 60/ I-265 project to achieve the improved capacity at a much quicker date in time. It’s important for designers to consider the long term planning for an area when determining the
2013-11-07 | Right-of-Way | Communication | I-CHANGE RECONST(O) | 5 | JEFFERSON | When the interchange improvements were made on US 60 a non-mountable median was constructed and changed access to a parcel from unrestricted to a right-in and right-out. The property owner was not informed of or compensated for this change. | A change order was written to construct an entrance for the parcel off of an adjacent local road to provide safe and efficient access. It’s important for project managers to ensure that affected property owners (not simply those who have acquisitions) a
2013-11-07 | Right-of-Way | Communication | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | When the interchange improvements were made on US 60 a non-mountable median was constructed and changed access to a parcel from unrestricted to a right-in and right-out. The property owner was not informed of or compensated for this change. | A change order was written to construct an entrance for the parcel off of an adjacent local road to provide safe and efficient access. It’s important for project managers to ensure that affected property owners (not simply those who have acquisitions) a
2013-11-07 | Construction | Method/Innovation | I-CHANGE RECONST(O) | 5 | JEFFERSON | On US 60 some minor widening occurred with curb and gutter installed leaving a small space between the gutter and the existing pavement. The plans indicated placing asphalt in this area but no sufficient compaction equipment can work in this small space | A change order was written to provide concrete to refill this space which will prevent settlement concerns. Designers are encouraged to consider constructability when designing minor widening and seek input from the local KYTC Construction staff regardi
2013-11-07 | Construction | Method/Innovation | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | On US 60 some minor widening occurred with curb and gutter installed leaving a small space between the gutter and the existing pavement. The plans indicated placing asphalt in this area but no sufficient compaction equipment can work in this small space | A change order was written to provide concrete to refill this space which will prevent settlement concerns. Designers are encouraged to consider constructability when designing minor widening and seek input from the local KYTC Construction staff regardi
2013-11-07 | Structures | Bridge Deck | I-CHANGE RECONST(O) | 5 | JEFFERSON | The concrete latex overlay overrun considerably due to existing conditions not matching the depth directed in the plans. | A change order was written to add quantity of latex for the additional work to be done. It’s important for designers to carefully review existing conditions to establish a reasonable quantity of work items.
2013-11-07 | Utilities | Inaccurate Location | I-CHANGE RECONST(O) | 5 | JEFFERSON | When performing work the Contractor hit some conduit for street lighting. The plans did not accurately display the location of the conduit. | A change order was written to repair/reinstall the damaged conduit. It’s important for survey crews to accurately pickup locations of underground facilities to prevent delay and extra cost to the project.
2013-11-07 | Utilities | Inaccurate Location | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | When performing work the Contractor hit some conduit for street lighting. The plans did not accurately display the location of the conduit. | A change order was written to repair/reinstall the damaged conduit. It’s important for survey crews to accurately pickup locations of underground facilities to prevent delay and extra cost to the project.
2013-11-07 | Design | Omission | I-CHANGE RECONST(O) | 5 | JEFFERSON | An intersection was rehabilitated with asphalt surfacing and signal reconstruction. This is considered an alteration and therefore ADA requirements had to be met. | A change order was written to reconstruct the sidewalk ramps to meet ADA requirements. It’s important for designers to understand that KYTC has a responsibility to bring sidewalk ramps into compliance with ADA when work is done adjacently to the ramp pe
2013-11-07 | Design | Omission | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | An intersection was rehabilitated with asphalt surfacing and signal reconstruction. This is considered an alteration and therefore ADA requirements had to be met. | A change order was written to reconstruct the sidewalk ramps to meet ADA requirements. It’s important for designers to understand that KYTC has a responsibility to bring sidewalk ramps into compliance with ADA when work is done adjacently to the ramp pe
2013-11-07 | Drainage | Curb Box Inlets | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | A Curb Box Inlet Ty A was constructed in the radius of curb and gutter section. The lid was driven over and crushed. | A change order was written repair the curb box. Designers should be very careful when placing Curb Box Inlet Ty A’s in radiuses. The lids are often damaged by off tracking of trucks. Even with large radius intersections often trucks will damage them in
2013-11-07 | Drainage | Curb Box Inlets | I-CHANGE RECONST(O) | 5 | JEFFERSON | A Curb Box Inlet Ty A was constructed in the radius of curb and gutter section. The lid was driven over and crushed. | A change order was written repair the curb box. Designers should be very careful when placing Curb Box Inlet Ty A’s in radiuses. The lids are often damaged by off tracking of trucks. Even with large radius intersections often trucks will damage them in
2013-11-07 | Structures | Bridge Deck | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The concrete latex overlay overrun considerably due to existing conditions not matching the depth directed in the plans. | A change order was written to add quantity of latex for the additional work to be done. It’s important for designers to carefully review existing conditions to establish a reasonable quantity of work items.
2013-11-07 | Design | Omission | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | When resurfacing a portion of US 60 a substandard sidewalk ramp was discovered, not meeting Americans with Disabilities Act (ADA) requirements. | A change order was written to remove and reconstruct the sidewalk ramp. It’s important for designers to understand that KYTC has a responsibility to bring sidewalk ramps into compliance with ADA when work is done adjacently to the ramp per FHWA.
2013-11-07 | Design | Omission | I-CHANGE RECONST(O) | 5 | JEFFERSON | When resurfacing a portion of US 60 a substandard sidewalk ramp was discovered, not meeting Americans with Disabilities Act (ADA) requirements. | A change order was written to remove and reconstruct the sidewalk ramp. It’s important for designers to understand that KYTC has a responsibility to bring sidewalk ramps into compliance with ADA when work is done adjacently to the ramp per FHWA.
2013-09-05 | Design | Plans | MAJOR WIDENING(O) | 2 | HANCOCK | Just beyond the project limits was an existing mountable median that caused confusion for road users and became dangerous as the motorists would drive the wrong way in a left turn lane to access a Dollar General store. | A change order was written to remove the mountable median and restripe the area as a two-way-left-turn-lane. This fell just beyond the original project limits but within the scope of work of the project to improve safety along the corridor. It's importa
2013-09-05 | Erosion Control Plan | Quantities | MAJOR WIDENING(O) | 2 | HANCOCK | Insufficient quantity of Erosion Control Blanket (ECB) was setup. | The ECB was overrun significantly to accommodate a need in the field to utilize ECB for slope protection. In District 2 , it's preferred to account for ECB on any slope greater than 3:1 as the soils have little cohesion and erode easily under any signif
2013-09-05 | Drainage | Headwalls | MAJOR WIDENING(O) | 2 | HANCOCK | On this project double pipes were necessary to facilitate flow under the roadway. Double pipe culvert headwalls without aprons were utilized just beyond the clear zone. From a maintenance perspective this can be undesirable. Historically this headwall t | A possible solution to this problem is to separate the pipes and utilize individual headwalls or use a double headwall that has an apron.
2013-09-05 | Design | Guardrail | MAJOR WIDENING(O) | 2 | HANCOCK | As slopes were widened and pipes were extended on the improved westbound lanes the median ditch was relocated. In some locations , especially near pipes on skews , the front slope on the median side of the existing , unimproved eastbound lanes was inc | A change order was written to include additional guardrail in these areas where guardrail became warranted. It's important that designers consider the effects our work may have on existing conditions.
2013-09-05 | Design | Guardrail | MAJOR WIDENING(O) | 2 | HANCOCK | As slopes were widened and pipes were extended on the improved westbound lanes the median ditch was relocated. In some locations , especially near pipes on skews , the front slope on the median side of the existing , unimproved eastbound lanes was inc | A change order was written to include additional guardrail in these areas where guardrail became warranted. It's important that designers consider the effects our work may have on existing conditions.
2013-09-04 | Right-of-Way | CAP | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Communicating All Promises (CAP) agreements were in place on this project. However , the proposal didnÖt include the CAP's. | It's important that CAP agreements are included in the proposal so that they become a contractual agreement with the Contractor and not simply a promise to the property owner.
2013-09-04 | Right-of-Way | CAP | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Communicating All Promises (CAP) agreements were in place on this project. However , the proposal didnÖt include the CAP's. | It's important that CAP agreements are included in the proposal so that they become a contractual agreement with the Contractor and not simply a promise to the property owner.
2013-09-04 | Geotechnical | Sinkhole | SAFETY(P) | 2 | CHRISTIAN | A sinkhole developed near an existing structure that was widened. | A change order was written to provide reinforced bridging of the sinkhole allowing for the new wing of the abutment to be constructed. It's important for designers to thoroughly investigate existing site conditions and address them accordingly.
2013-09-04 | Geotechnical | Sinkhole | I-CHANGE RECONST(O) | 2 | CHRISTIAN | A sinkhole developed near an existing structure that was widened. | A change order was written to provide reinforced bridging of the sinkhole allowing for the new wing of the abutment to be constructed. It's important for designers to thoroughly investigate existing site conditions and address them accordingly.
2013-09-04 | Maintenance of Traffic | Quantities | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Insufficient quantity of Traffic Bound Base (TBB) was incorporated into the project for maintenance of traffic (MOT). | The quantity of TBB was overrun significantly. Designers should consult with construction personnel to help determine an ample quantity of aggregate for MOT. Small quantities of MOT aggregate are often bid over the average unit bid price. Depending on
2013-09-04 | Maintenance of Traffic | Quantities | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Insufficient quantity of Traffic Bound Base (TBB) was incorporated into the project for maintenance of traffic (MOT). | The quantity of TBB was overrun significantly. Designers should consult with construction personnel to help determine an ample quantity of aggregate for MOT. Small quantities of MOT aggregate are often bid over the average unit bid price. Depending on
2013-09-04 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Decorative light poles in the downtown area were in the disturb limits of the project. However , the original plan set didn't account for their removal and resetting. | A change order was written to include removeing and resetting the light poles. It's important for designers to closely investigate any utilities located within the disturb limits of the project and their potential conflict.
2013-09-04 | Erosion Control Plan | Quantities | I-CHANGE RECONST(O) | 2 | CHRISTIAN | Insufficient quantity of Erosion Control Blanket (ECB) was established to protect slopes from erosion and promote vegetation growth. | The item ECB was overrun significantly to accommodate placement on slopes. In general , District 2 has silty , sandy soils that have little cohesion providing an opportunity for significant erosion. As a rule , they prefer to utilize ECB on 3:1 or gr
2013-09-04 | Erosion Control Plan | Quantities | SAFETY(P) | 2 | CHRISTIAN | Insufficient quantity of Erosion Control Blanket (ECB) was established to protect slopes from erosion and promote vegetation growth. | The item ECB was overrun significantly to accommodate placement on slopes. In general , District 2 has silty , sandy soils that have little cohesion providing an opportunity for significant erosion. As a rule , they prefer to utilize ECB on 3:1 or gr
2013-09-04 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Decorative light poles in the downtown area were in the disturb limits of the project. However , the original plan set didn't account for their removal and resetting. | A change order was written to include removeing and resetting the light poles. It's important for designers to closely investigate any utilities located within the disturb limits of the project and their potential conflict.
2013-09-04 | Pavement | Design | SAFETY(P) | 2 | CHRISTIAN | The JPC Pavement-6 In in the southbound lane of US 41A was constructed as a mill and inlay but now is showing cracking due to yielding subgrade. | The Post Construction Review group recommends that the pavement design be reviewed and approved by the Pavement Design Branch , especially on projects that are unique in nature , and a thorough review of the existing pavement and subgrade should be perf
2013-09-04 | Pavement | Design | I-CHANGE RECONST(O) | 2 | CHRISTIAN | The JPC Pavement-6 In in the southbound lane of US 41A was constructed as a mill and inlay but now is showing cracking due to yielding subgrade. | The Post Construction Review group recommends that the pavement design be reviewed and approved by the Pavement Design Branch , especially on projects that are unique in nature , and a thorough review of the existing pavement and subgrade should be perf
2013-09-04 | Utilities | Inaccurate Location | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | An existing fiberoptic line shown on the plans was in conflict with the location of the proposed storm sewer pipe. This project utilized Subsurface Utility Engineering (SUE) in the Phase 1 design stage. At that time SUE was performed the typical section | A change of the storm sewer design had to be made and significant delay was encountered. The post construction review meeting attendees preferred that SUE be completed during phase 2 design so that conflict points are known and can be specifically invest
2013-09-04 | Utilities | Inaccurate Location | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | An existing fiberoptic line shown on the plans was in conflict with the location of the proposed storm sewer pipe. This project utilized Subsurface Utility Engineering (SUE) in the Phase 1 design stage. At that time SUE was performed the typical section | A change of the storm sewer design had to be made and significant delay was encountered. The post construction review meeting attendees preferred that SUE be completed during phase 2 design so that conflict points are known and can be specifically invest
2013-09-04 | Drainage | Omission | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | The existing template of the roadway was rural and this project changed the template to urban including curb & gutter. On one location a building on a property may not have taken water on during rainfall events did so after construction. Water appears t | A drop box inlet was placed in the entrance pavement and drained to a nearby pipe network via change order. A simple solution for original design may have been slotted drain pipe. It's important for designers to closely examine proposed drainage pattern
2013-09-04 | Drainage | Omission | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | The existing template of the roadway was rural and this project changed the template to urban including curb & gutter. On one location a building on a property may not have taken water on during rainfall events did so after construction. Water appears t | A drop box inlet was placed in the entrance pavement and drained to a nearby pipe network via change order. A simple solution for original design may have been slotted drain pipe. It's important for designers to closely examine proposed drainage pattern
2013-09-04 | Traffic | Coordination | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Mast arm traffic signal poles were utilized on this project for signalization at the intersection. However , the intersection isn't truly perpendicular and the plans didn't indicate the angle necessary for construction of the mast arm poles. This led t | A change order was written to have the pole bases modified and the mast arm poles rotated to be properly oriented. On intersections with angles other than 90 degrees it's important that the angles be spelled out in the contract.
2013-09-04 | Traffic | Coordination | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Mast arm traffic signal poles were utilized on this project for signalization at the intersection. However , the intersection isn't truly perpendicular and the plans didn't indicate the angle necessary for construction of the mast arm poles. This led t | A change order was written to have the pole bases modified and the mast arm poles rotated to be properly oriented. On intersections with angles other than 90 degrees it's important that the angles be spelled out in the contract.
2013-09-04 | Structures | Quantities | I-CHANGE RECONST(O) | 2 | CHRISTIAN | An insufficient quantity of Bridge End Connector Ty A was setup for the existing conditions. | A change order was written to accommodate the existing conditions. Designers are encouraged thoroughly review existing conditions to ensure adequate quantities of work items are provided.
2013-09-04 | Structures | Quantities | SAFETY(P) | 2 | CHRISTIAN | An insufficient quantity of Bridge End Connector Ty A was setup for the existing conditions. | A change order was written to accommodate the existing conditions. Designers are encouraged thoroughly review existing conditions to ensure adequate quantities of work items are provided.
2013-09-04 | Utilities | Communication | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | The utility relocation plans were completed independently from the roadway plans. A lack of communication and/or implementation of the roadway plans into the utility relocation plans caused several conflicts of the new storm sewer facility with the propos | A change order was written to include additional quantities for the utility relocation as well as a time adjustment to the contract.
2013-09-04 | Utilities | Communication | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | The utility relocation plans were completed independently from the roadway plans. A lack of communication and/or implementation of the roadway plans into the utility relocation plans caused several conflicts of the new storm sewer facility with the propos | A change order was written to include additional quantities for the utility relocation as well as a time adjustment to the contract.
2013-09-04 | Right-of-Way | Communication | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Slopes extending from the sidewalk onto adjacent properties where pavement existed originally caused concern with the property owners. The property owners lost some functionally of their property due to loss of pavement , which was replaced with vegetat | A change order was written to install Standard Header Curb which was used to separate the vegetation & slope from the paved area , allowing the slope to still tie down nicely while maintaining the original area of pavement on the propery owner.
2013-09-04 | Right-of-Way | Communication | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Slopes extending from the sidewalk onto adjacent properties where pavement existed originally caused concern with the property owners. The property owners lost some functionally of their property due to loss of pavement , which was replaced with vegetat | A change order was written to install Standard Header Curb which was used to separate the vegetation & slope from the paved area , allowing the slope to still tie down nicely while maintaining the original area of pavement on the propery owner.
2013-09-04 | Construction | Revisions | SAFETY(P) | 2 | CHRISTIAN | Due to an adjacent property owner being unwilling to sign an agreement for right-of-way (ROW) and in the interest of advancing the project , a revision had to be made to a proposed gabion retaining wall . | The proposed gabion retaining wall dimensions didn't allow room for itself and a proposed ditch in the area with constrained ROW. A reinforced concrete channel was designed and constructed via change order to provide support for the roadway embankment a
2013-09-04 | Construction | Revisions | I-CHANGE RECONST(O) | 2 | CHRISTIAN | Due to an adjacent property owner being unwilling to sign an agreement for right-of-way (ROW) and in the interest of advancing the project , a revision had to be made to a proposed gabion retaining wall . | The proposed gabion retaining wall dimensions didn't allow room for itself and a proposed ditch in the area with constrained ROW. A reinforced concrete channel was designed and constructed via change order to provide support for the roadway embankment a
2013-09-04 | Maintenance of Traffic | Changes | I-CHANGE RECONST(O) | 2 | CHRISTIAN | The lane closures associated with closure of the ramps on I-24 were changed to a weekday closure instead of a weekend closure. | Traffic counts yielded information that weekend traffic is higher for the ramps than weekdays. The project team should thoroughly investigate existing traffic patterns to determine the least invasive time to close the roadway.
2013-09-04 | Traffic | Quantities | SAFETY(P) | 2 | CHRISTIAN | The plans omitted the removal and replacement of 4 lighting structures that existed within the disturb limits of the project. | A change order was written to add pay items to accommodate the work. It's important that designers thoroughly check existing site conditions to ensure that existing features are picked up and adequate quantities are established to perform the work when r
2013-09-04 | Utilities | Inaccurate Location | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | An existing waterline was shown on the plans to be under the existing roadway. However , in the field the water line was encountered on the side of the roadway in conflict with the alignment with the proposed storm sewer. This caused a minor delay to th | A change order was written to include relocation of the water line. Accurate survey of existing utilities is essential to the success of a project.
2013-09-04 | Utilities | Inaccurate Location | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | An existing waterline was shown on the plans to be under the existing roadway. However , in the field the water line was encountered on the side of the roadway in conflict with the alignment with the proposed storm sewer. This caused a minor delay to th | A change order was written to include relocation of the water line. Accurate survey of existing utilities is essential to the success of a project.
2013-09-04 | Drainage | Quantities | SAFETY(P) | 2 | CHRISTIAN | The widening of the shoulder along US 41A caused existing drainage structures to be too short. | A change order was written to add culvert pipe and new headwalls for the necessary pipe extensions due to the widening. Designers are encouraged to carefully review the effects widening has on the existing drainage facilities.
2013-09-04 | Maintenance of Traffic | Changes | SAFETY(P) | 2 | CHRISTIAN | The lane closures associated with closure of the ramps on I-24 were changed to a weekday closure instead of a weekend closure. | Traffic counts yielded information that weekend traffic is higher for the ramps than weekdays. The project team should thoroughly investigate existing traffic patterns to determine the least invasive time to close the roadway.
2013-09-04 | Construction | Contracts | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Insufficient contract time was provided to complete the project based on the amount of work to be performed , especially given the utility work included. | Projects with utility relocation included in the roadway contract should be given a conservative amount of contract time to complete the project.
2013-09-04 | Drainage | Quantities | I-CHANGE RECONST(O) | 2 | CHRISTIAN | The widening of the shoulder along US 41A caused existing drainage structures to be too short. | A change order was written to add culvert pipe and new headwalls for the necessary pipe extensions due to the widening. Designers are encouraged to carefully review the effects widening has on the existing drainage facilities.
2013-09-04 | Traffic | Quantities | I-CHANGE RECONST(O) | 2 | CHRISTIAN | The plans omitted the removal and replacement of 4 lighting structures that existed within the disturb limits of the project. | A change order was written to add pay items to accommodate the work. It's important that designers thoroughly check existing site conditions to ensure that existing features are picked up and adequate quantities are established to perform the work when r
2013-09-04 | Construction | Contracts | SPOT IMPROVEMENTS(O) | 2 | MUHLENBERG | Insufficient contract time was provided to complete the project based on the amount of work to be performed , especially given the utility work included. | Projects with utility relocation included in the roadway contract should be given a conservative amount of contract time to complete the project.
2013-08-15 | Erosion Control Plan | Quantities | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | Temporary mulch overrun significantly on the project. The disturbed areas on the project were covered when the construction season closed as the project extended through the winter. | When projects are expected to extend through multiple construction seasons due to project schedule length , anticipated letting date , etc. designers should consider including a significant amount of temporary mulch or temporary seeding to accommodate t
2013-08-15 | Structures | Handrail | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Several miscellaneous metals were setup as galvanized steel material. This presented an opportunity for galvonic corrosion to occur. | A change order was written to change said miscellaneous metals to weathering steel components. It's important for designers to communicate with the Division of Structural Design to gain perspective with regards to use of galvanized steel for various compo
2013-08-15 | Drainage | Existing Pipe | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | An existing drainage network including drop boxes and piping on the southwest corner of Fairview Dr./Trade Ave. was discovered. It was silted over and interfered with effectiveness of planned drainage improvements. Replacement of the drainage network wo | A change order was written to install curb & gutter to carry surface water from the intersection to newly construction drainage piping. Designers are encouraged to ensure that existing drainage structures and their condition are considered while planning
2013-08-15 | Structures | Communication | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Hundreds of submittals were transmitted from the Contractor , KYTC personnel , consultant designers etc. In this case , the parties worked well with regards to turnaround on approvals , reqeusts for information , commenting etc. Good communication w | On future projects it may be worthwhile to consider a formal process to set forth guidelines of expections with regard to processing submittals. It may save thousands of dollars and considerable time if potential claims are filed on projects where commu
2013-08-15 | Drainage | Sheet Flow | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Due to wide pavements and superelevation of the pavement runoff gained velocity and caused rills to occur in the fill slope. | A change order was written to provide the items Special Header Curb and Flume Inlet Type 2 to protect the slopes from washing. When wide pavements with steep profiles and/or large superelevations exist designers should consider how sheet flow may affect
2013-08-15 | Structures | Dimensions | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | New utility access boxes were constructed under the bridge deck to access conduits that were suspended under the deck for the length of the bridge for future utility expansion. The boxes were constructed per plan to an elevation that forced the tops of t | The boxes were modified to accommodate the stay-in-place forms by shifting the boxes down. A change order was written to make payment for the modification.
2013-08-15 | Traffic | Omission | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Concrete Median Barrier Wall was constructed on the bridge and lighting was included. However , no Pole Base in Median Wall was included. | The item was added via change order. Designers should check plans to ensure constructability of the plans produced , confirming that all necessary work items are included to complete construction of the proposed structure.
2013-08-15 | Structures | Granular Pile Core | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | No Granular Pile Core was set up originally for pile driving for the Integral End Bent (IEB) #2 on the Livingston County side. This side had Granular Embankment established as fill material for the embankment in the area of the IEB , making pile driving | The granular pile was setup via change order. It's important that designers consider fill conditions and constructibility carefully when piling is utilized for support of the substructure.
2013-08-15 | Maintenance of Traffic | Entrances | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | A temporary entrance was detailed to be constructed onto Fairview Ave. Doing so would have required continuous maintenance due to its' proximity of the widening work being performed along Fairview Ave. | The temporary entrance was constructed with a tie-in to US 62. This allowed for one initial installation and very little subsequent maintenance. Designers are encouraged to carefully consider placement of temporary entrances in relation to permanent con
2013-08-15 | Construction | Contracts | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | The structural steel on this project was set up as one lump sum pay item and this created problems with SiteManager , KYTC's construction project documentation software. As stockpiled materials were paid initially , and subsequent payments were made for | A change order was written to change the original lump sum item for Structural Steel into smaller lump sum items associated with the structural steel. When large lump sum items are considered for use on a project and may be subjected to stockpiled paymen
2013-08-15 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Temporary striping was not setup on the project originally. | A change order was written to include temporary striping for use in the MOT phasing. Designers are encouraged to include all necessary items of work to properly control MOT.
2013-08-15 | Structures | Specifications | BRIDGE REPLACEMENT(P) | 1 | HICKMAN | One lump sum pay item Dynamic Pile Testing was established for each pipe pile tested per the contract. However , the special note in the proposal indicated that two payments for each pipe pile tested be made. | A change order will be written to establish additional quantity for the Dynamic Pile Testing pay item. Follow up conversation with the Geotechnical Branch yielded the current process of payment for dynamic pile testing which incorporates two uniquely ide
2013-08-15 | Drainage | Existing Pipe | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | An existing pipe was incorrectly sized on the project plans. Therefore , an incorrect size pipe was setup to extend the pipe for the purpose of widening the roadway.
2013-08-15 | Utilities | Conflicting Information | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | The information given by the local water company was incorrect in regards to depth and location , therefore , the plans incorrectly identified existly utilility locations. | A change order was written to include utility relocation items and a time adjustment in the construction contract. Better communication between utility owners and survey crews may help facilitate better identification of existing utilities in the project
2013-08-15 | Traffic | Coordination | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | The density of lighting poles on the bridge was less than that on the lighting plan for the roadway. | A change order was written to accommodate addional lighting on the bridge to create consistency. It's important that bridge features are checked to ensure consistency and compatibility with roadway features.
2013-08-15 | Structures | Handrail | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | The steel safety cable specified in the project plans was too large to make small radius turns during installation. A new smaller diameter cable had to be used and this cable had to be removed without being able to return. | A change order was written to add the additional smaller diameter cable. It's important for designers to consider the material specified and its' capabilities from a constructability standpoint.
2013-08-14 | Drainage | Error | MINOR WIDENING(O) | 1 | LYON | Insufficient quantity of Channel Lining Class II established for armored ditches. A typographical error designated that much quantity was necessary. | The quantity of Channel Lining Class II was overrun. Designers are encouraged to check calculated quantities and minimze typographical errors.
2013-08-14 | Utilities | Inaccurate Location | MINOR WIDENING(O) | 1 | LYON | An overhead utility pole had to be relocated for construction of the new facility. However , while performing grading , it was observed that the utility pole had been relocated into the location of a new ditch. | The ditch had to be adjusted to prevent delay that would be caused by a subsequent relocation. It's important for project managers to ensure that utility relocations are performed with accuracy to prevent multiple relocations of those facilities and likel
2013-08-14 | Erosion Control Plan | Quantities | MINOR WIDENING(O) | 1 | LYON | Insufficient quantity of Erosion Control Blanket (ECB)established. | The ECB was overrun to accommodate warranted site conditions. It's important that designers consider not only ditches for areas to include quantity for ECB but also steep slopes (> 3:1) or areas of concentrated flows (i.e. fill slopes on the low side of
2013-08-14 | Structures | Alignment | MINOR WIDENING(O) | 1 | LYON | This structure was constructed within the tangent run out and the run off portion of the horizontal transition into a curve due to R/W constraints , thereby preventing a different horizontal alignment consideration. | When possible , it's important for designers to consider the difficulty of construction of structures that require skews or horizontal curve transitions. This difficulty leads to increased project duration and increased costs.
2013-08-14 | Design | Guardrail | MINOR WIDENING(O) | 1 | LYON | Insufficient quantity of Guardrail Steel W Beam S-Face was established in the project plans due to multiple entrance locations (radius rail paid at 1.3 times the length measured) and existing site conditions warranted additional guardrail. | The pay item for the guardrail was overrun to accommodate the field installation. Designers are encouraged to closely consider site conditions and to shield roadside hazards as detailed in the Roadside Design Guide. Additionally , its important to cons
2013-08-14 | Design | Guardrail | MINOR WIDENING(O) | 1 | LYON | Insufficient quantity of Guardrail Steel W Beam S-Face was established in the project plans due to multiple entrance locations (radius rail paid at 1.3 times the length measured) and existing site conditions warranted additional guardrail. | The pay item for the guardrail was overrun to accommodate the field installation. Designers are encouraged to closely consider site conditions and to shield roadside hazards as detailed in the Roadside Design Guide. Additionally , its important to cons
2013-05-23 | Design | CAP | BRIDGE REPLACEMENT(P) | 11 | CLAY | A field entrance wasn't picked up on the original survey but a Communicating All Promises (CAP) agreement was in place with the property owner to construct an entrance and was published in the contract proposal. No quantity was setup for this work. | A change order was written to include items to construct the entrance including an entrance pipe. When preparing proposals , it's important to ensure that applicable items of work are included for prescribed work as well as for CAP agreements.
2013-05-23 | Structures | Plans | BRIDGE REPLACEMENT(P) | 11 | CLAY | This project was designed/constructed prior to policy and formal guidance being established for 3 sided structures. This project solely utilized Foundation Preparation for all excavation work. | The policy now clearly identifies the excavation process which utilizes Foundation Preparation along with Structure Excavation Solid Rock to make bidding of said structures more finite.
2013-05-23 | Construction | Contracts | BRIDGE REPLACEMENT(P) | 11 | CLAY | The Contract included a construction time allotment of 28 calendar days , however , it didn't include a primary completion date. | A change order was written to include a primary completion date. When utilizing a specific number of calendar days to complete a project , it's important to also include the primary completion date.
2013-04-30 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 10 | ESTILL | Unsuitable , saturated material was encountered in several instances while excavating the trench for culvert pipe construction. | The Section Supervisor advised to undercut all culvert pipe trenches by 1 ft. and refill with shot rock if available or crushed aggregate no. 2 wrapped with geotextile fabric.
2013-04-30 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 10 | ESTILL | An existing water main conflicted with the open channel flow line feeding a newly constructed reinforced concrete box culvert. | The Contractor relocated the water main utilizing existing work items.
2013-04-30 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 10 | PERRY | The shoulders were originally set up with only one course of asphalt base. KYTC was concerned that while traffic utilized the paved shoulders with inadequate pavement depth for movement during construction , failures would occur and subsequent repair wou | Designers are encouraged to consider the condition of shoulders , both existing & proposed , when utilizing them for the purpose of maintenance of traffic (MOT). If traffic will utilize the shoulder for an extended time period full depth pavement is str
2013-04-30 | Maintenance of Traffic | Quantities | RECONSTRUCTION(O) | 10 | ESTILL | Not enough temporary striping quantity was called out in the plans due to switching traffic and maintaining motorists on the final asphalt base course prior to surfacing. This was partially due to a switch in MOT phasing. | The temporary striping was overrun to accommodate the motorists using the new mainline. Designers are encouraged to consider the likelihood of switching traffic onto the completed asphalt base course prior to surfacing while establishing quantities for MO
2013-04-30 | Design | Guardrail | RECONSTRUCTION(O) | 10 | PERRY | The trailing end of multiple guardrail installations called out end treatment Type 1's. A median barrier wall separated traffic , thus eliminating the likelihood of a strike. | KYTC wrote a change order to establish end treatment Type 2A. Designers are encouraged to consider the functionality of end treatments and consider the need of the situation that they utilized.
2013-04-30 | Design | Guardrail | RECONSTRUCTION(O) | 10 | PERRY | The trailing end of multiple guardrail installations called out end treatment Type 1's. A median barrier wall separated traffic , thus eliminating the likelihood of a strike. | KYTC wrote a change order to establish end treatment Type 2A. Designers are encouraged to consider the functionality of end treatments and consider the need of the situation that they utilized.
2013-04-30 | Traffic | Omission | RECONSTRUCTION(O) | 10 | ESTILL | Milled rumble strips weren't included on the original contract but are currently policy for a road given certain criteria. | KYTC wrote a change order to include rumble strips on this project.
2013-04-30 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 10 | PERRY | The use of the pay item Law Enforcement Officer was not effective on this project. The Contractor attempted to utilize local law enforcement but was unsuccessful due to infrequent issue of citations when speeding occurred. Therefore , local motorists did | During the project KYTC began to solicit the Ky. State Police (KSP) for law enforcement presence and the effectiveness increased. A change order was written to add funding for KSP presence and they were compensated from contract funding. When local motori
2013-04-30 | Erosion Control Plan | Seeding | RECONSTRUCTION(O) | 10 | ESTILL | The significant presence of non-durable shales created difficulty establishing vegetation on cut slopes. | KYTC wrote a change order to place topsoil on certain cut slopes and increase the quantity of erosion control blanket so that it may be placed on slopes greater that 2:1 to manage erosion and support vegetation growth. Designers are encouraged to consider
2013-04-30 | Right-of-Way | Coordination | RECONSTRUCTION(O) | 10 | ESTILL | The existing portion of KY 89 left in place was turned over to the county. The contract didn't specify that the portion left in place be resurfaced. | The existing KY 89 was resurfaced by overrunning existing asphalt items. Project managers are encouraged to coordinate this process prior to final plans so that the paving can be incorporated into the project.
2013-04-30 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 10 | ESTILL | A few existing overhead power lines didn't provide vertical clearance above the newly constructed roadway. | The local power utility set new poles to provide necessary vertical clearan ce. Project Teams are encouraged to evaluate existing overhead utilities early in the design process to ascertain whether or not relocation may be necessary upon completion of the
2013-04-30 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 10 | PERRY | Unsuitable material was encountered due to improper drainage of the subgrade. | A series of perforated pipes was used to provide drainage to the subgrade.
2013-04-30 | Design | Omission | RECONSTRUCTION(O) | 10 | ESTILL | An approaching county road lost an existing access point when mainline was re-constructed leaving only one access to mainline , which frequently flooded. | KYTC wrote a change order to add a suitable access point to the county road with adequate drainage capability. Designers are encouraged to survey the impact the project has to adjacent infrastructure.
2013-04-30 | Traffic | Markings | RECONSTRUCTION(O) | 10 | PERRY | The contract established 4 inch permanent striping which is contradictory to standard practice for parkways. | Designers are encouraged to investigate standard practice for roadway markings regarding a particular roadway.
2013-04-30 | Traffic | Omission | RECONSTRUCTION(O) | 10 | ESTILL | No thermoplastic markings were setup for stop bars or combination arrows necessary to permanently control traffic. | KYTC wrote a change order to include these markings.
2013-04-30 | Traffic | Quantities | RECONSTRUCTION(O) | 10 | ESTILL | An insufficient quantity of signs were available on the project to sign a directed detour. | KYTC wrote a change order to increase the quantity of signs. Designers are encouraged to cross check sign quantities established versus standard drawings and directed diversions/detours.
2013-04-30 | Structures | Retaining Walls/MSE | RECONSTRUCTION(O) | 10 | PERRY | The original retaining wall horizontal location was called out as an offset to the centerline. At this location the roadway alignment was curved , thus detailing a curved wall which is difficult to construct. | The Contractor built the wall in a straight line manner to ease construction. Designers are encouraged to consider the constructability of a structure when calling out its' location.
2013-04-30 | Design | Shelved Plans | RECONSTRUCTION(O) | 10 | ESTILL | A road closure and lengthy detour of a minor approach road caused sincere frustration to affected residents and road users. Their primary frustration was due to the lack of advace notice. This detour was addressed with the public in the project developmen | The Section Engineer recommends that a public information distribution be performed , particularly with projects with shelved plans , so that affected residents will be once again reminded of the inconveniences that will be necessary during construction
2013-04-30 | Design | Omission | RECONSTRUCTION(O) | 10 | PERRY | This project had ride quality requirements , however , the contract didn't provide a method of payment (deduction). | Designers are encouraged to include bid items for all aspects of the work so that change orders for such may be avoided.
2013-04-30 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 10 | ESTILL | A property owner of a residence located near the R/W line on the top of a rock cut slope expressed concern about the danger of falling over the rock slo pe. Original plans indicated a guardrail but no fencing. | KYTC wrote a change order to install a chain link fence adjacent to the top of the rock cut slop e. Project Teams are encouraged to consider the safety of residents in regards to the new topography of the constructed roadway.
2013-04-30 | Construction | Method/Innovation | RECONSTRUCTION(O) | 10 | PERRY | The mainline widening was originally setup as approximately 2' widening. The Contractor contended that they would have difficulty gaining specified density with conventional paving equipment , therefore potentially causing premature future maintenance ac | Designers are encouraged to consider constructability when designing pavement widening with regard to conventional paving equipment as the use of non-conventional procedures can lead to higher bid costs and premature future maintenace.
2013-04-30 | Design | Entrance | RECONSTRUCTION(O) | 10 | ESTILL | One entrance was granted for two schools located adjacently to utilize for access. This resulted in congestion issues at the school entrance during peak hour use and a request from the school system for 2 access points. | One entrance was granted for two schools located adjacently to utilize for access. This resulted in congestion issues at the school entrance during peak hour use and a request from the school system for 2 access points.
2013-04-30 | Structures | Quantities | RECONSTRUCTION(O) | 10 | PERRY | An error was made regarding quantity of concrete in the pier caps. | KYTC wrote a change order to provide payment for the extra concrete that was needed for the pier caps. Designers are encouraged to thoroughly check dimensions & quantities on plans.
2013-04-30 | Traffic | Omission | RECONSTRUCTION(O) | 10 | PERRY | No thermoplastic markings were set up for this project to be used for gore markings and stop bars. | Designers are encouraged to investigate standard practice for roadway markings regarding a particular roadway.
2012-12-05 | Design | Safety | NEW ROUTE(O) | 3 | BARREN | In an effort to improve safety and provide positive separation of the left turn movements at Lohden Road Approach and to meet recommendations set forth in a 2009 Design Memo , the left turn lanes were designed to be separated from the through traffic of | On projects let subsequently , the District has designed a configuration which provides positive separation with an offset left turn lane and flush median accompanied by appropriate island striping. The left turning lane is more centered in the median a
2012-12-05 | Design | Plans | NEW ROUTE(O) | 3 | BARREN | Lt Sta 286+00 near Ramp 4 , a natural spring was purchased as right of way from Parcel 266. On plan sheets R11 and R26 , the right of way line was designated as Prop. R/W & C/A Line. On sheet R26 , the plans depicted two separate alignments for Prop | The section office was directed to fence a line that represented a compromise between the two lines shown on the plans. Additionally , the area outside of the newly placed fence was left undisturbed in and around the natural spring. Project Delivery an
2012-12-05 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 3 | BARREN | The proposed RCBC at Sta. 51+63 was constructed in two phases. It was determined in the field that barrier wall was needed for safety reasons in order to complete the installation. | Barrier wall should be a design consideration on projects involving phased construction of large structures in close proximity to traffic.
2012-12-05 | Construction | Damages | NEW ROUTE(O) | 3 | BARREN | The Parkway had been recently resurfaced , but the new surface was damaged due to the barrier wall settling into the pavement due to the duration of the closure along with the extreme heat. | The section office decided to repair the damaged pavement through this area.
2012-12-05 | Traffic | Lighting | NEW ROUTE(O) | 3 | BARREN | The plans for the high mast lighting detailed 100 amp service. The contractor determined that it required 200 amp service. | The modification in the service requirement was approved in the electrical submittals.
2012-12-05 | Traffic | Markings | NEW ROUTE(O) | 3 | BARREN | Normal paint striping was set up on the contract on all radii and bull-noses. The maintenance of striping in these areas is difficult because the striping has to be filled in after the straight sections are complete. | The section office decided to apply thermo in these areas to increase durability. This should be considered by the project development team with an emphasis on PD&P and Support Branch involvement.
2012-12-05 | Traffic | Omission | NEW ROUTE(O) | 3 | BARREN | The plans indicated removing an existing signal at Scotty Drive; however , a new signal was not included in the contract. | A new signal was installed as well as a right turn lane at the request of the City of Glasgow.
2012-12-05 | Drainage | Elevation | NEW ROUTE(O) | 3 | BARREN | In two separate locations , the outfall ditch that was shown on the pipe sheets did not daylight as indicated in the plans. One issue occurred at Sta. 109+60 with a 48 cross drain on Sheet R82. | The section office received permission from the adjoiner to excavate the ditch out across affected property until it would daylight properly. Designers should validate the aerial photography on projects with actual field shots to determine correct design
2012-12-05 | Design | Excavation | NEW ROUTE(O) | 3 | BARREN | Along the Parkway near End Bent 1 , the existing rock cut protruded beyond the 2:1 slope under the bridge. | The section office decided to lay these slopes back to provide a smooth transition through the bridge. This is an area that was not included on cross sections because no work was being performed on the Parkway , so the grading issue was not evident unti
2012-12-05 | Construction | Contracts | NEW ROUTE(O) | 3 | BARREN | The project was let to contract with pavement alternates. A bid item for Pavement Adjustment was used to account for life cycle cost. This adjustment was used for determining low bid , but was not to be left in the final contract amount. The item was | The item Pavement Adjustment was removed via change order. The Cabinet needs to ensure that this item is removed prior to award the final contract amount.
2012-12-05 | Traffic | Markings | NEW ROUTE(O) | 3 | BARREN | Normal paint striping was set up on the contract on all radii and bull-noses. The maintenance of striping in these areas is difficult because the striping has to be filled in after the straight sections are complete. | The section office decided to apply thermo in these areas to increase durability. This should be considered by the project development team with an emphasis on PD&P and Support Branch involvement.
2012-12-05 | Design | Quantities | NEW ROUTE(O) | 3 | BARREN | The contract plans showed clearing disturbed areas only in the gore areas of the Parkway. The consultant had originally submitted a grading plan for the gore areas and the decision was made by the Cabinet that it was not needed. | The section office directed the Contractor to clear all trees in the gore area for sight distance as well as for maintenance reasons.
2012-12-05 | Utilities | Omission | NEW ROUTE(O) | 3 | BARREN | Utility Relocation was included in this contract. As per note on Sheet U3 , the existing fire hydrants and gate valves were to be removed and delivered to the City of Glasgow Water District facility; however , appropriate bid items were not included in | Utility notes should be checked closely to ensure all bid items are included as indicated in the scope of work.
2012-12-05 | Construction | Contracts | NEW ROUTE(O) | 3 | BARREN | The project was let to contract with pavement alternates. A bid item for Pavement Adjustment was used to account for life cycle cost. This adjustment was used for determining low bid , but was not to be left in the final contract amount. The item was | The item Pavement Adjustment was removed via change order. The Cabinet needs to ensure that this item is removed prior to award the final contract amount.
2012-12-05 | Design | Quantities | NEW ROUTE(O) | 3 | BARREN | Geotechnical note 18 directed the Contractor to remove any saturated or soft areas and replace with Granular Embankment. Only 200 tons were set up on the contract. | The unit price for Granular Embankment was reasonable , so the quantity was adjusted to the actual amount used. 14 , 800 cu yds were added in Change Order 4.
2012-12-05 | Design | Omission | NEW ROUTE(O) | 3 | BARREN | Several areas of existing pavement outside of the disturbance limits were indicated as Remove Pavement; however , no bid item was established in the contract documents. | Remove Pavement bid item was added to the contract.
2012-12-05 | Erosion Control Plan | Channel Lining | NEW ROUTE(O) | 3 | BARREN | During project development , several of the ditches that were designed initially with Class II and III Channel Lining were changed to Turf Reinforcement Mat as directed by Central Office Drainage. After installation and prior to vegetative growth , hea | The section office decided to use Class III Channel Lining in lieu of Turf Reinforcement Mat. The Section Office has been more successful using regular EC Blanket and vegetation than with TRM. Designers are encouraged to strongly consider the application
2012-12-05 | Design | Quantities | NEW ROUTE(O) | 3 | BARREN | Geotechnical note 18 directed the Contractor to remove any saturated or soft areas and replace with Granular Embankment. Only 200 tons were set up on the contract. | The unit price for Granular Embankment was reasonable , so the quantity was adjusted to the actual amount used. 14 , 800 cu yds were added in Change Order 4.
2012-12-05 | Utilities | Relocation | NEW ROUTE(O) | 3 | BARREN | Due to the construction revision introducing the offset left turn lanes at US 31E , a gas line was encountered that featured a special station where ownership switched from Texas Gas to City of Glasgow Gas. | The affected gas line was relocated due to a lack of cover in the ditchline. When Construction Revisions occur , utility coordination may be necessary and should be considered.
2012-12-05 | Erosion Control Plan | Quantities | NEW ROUTE(O) | 3 | BARREN | This contract was set up with individual erosion control bid items; however , at the time , Central Office was supporting Lump Sum Erosion Control in an effort to shift more responsibility to the Contractor. | A reasonable lump sum price was obtained from the Contractor for erosion control. In District 3 , PD&P I prefers lump sum erosion control , while PD&P II prefers individual bid items.
2012-12-05 | Traffic | Omission | NEW ROUTE(O) | 3 | BARREN | High mast lighting was omitted from the contract for the ramps at the Parkway Interchange. The plans were being developed while the project was being let to contract. | Continued improvement is needed in the timing and coordination of traffic , signal , and lighting plan submittals during project development.
2012-12-05 | Drainage | Elevation | NEW ROUTE(O) | 3 | BARREN | In two separate locations , the outfall ditch that was shown on the pipe sheets did not daylight as indicated in the plans. One issue occurred at Sta. 109+60 with a 48 cross drain on Sheet R82. | The section office received permission from the adjoiner to excavation the ditch out across affected property until it would daylight properly. Designers should validate the aerial photography on projects with actual field shots to determine correct desi
2012-12-05 | Geotechnical | Sinkhole | NEW ROUTE(O) | 3 | BARREN | During construction , a large open sinkhole was discovered while excavating a rock cut. | This area was treated with Fabric and Rock in order to stabilize the natural void and allow drainage.
2012-12-05 | Design | Safety | NEW ROUTE(O) | 3 | BARREN | In an effort to improve safety and provide positive separation of the left turn movements at Lohden Road Approach and to meet recommendations set forth in a 2009 Design Memo , the left turn lanes were designed to be separated from the through traffic of | On projects let subsequently , the District has designed a configuration which provides positive separation with an offset left turn lane and flush median accompanied by appropriate island striping. The left turning lane is more centered in the median a
2012-12-05 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 3 | BARREN | An insufficient quantity of Relocate Temp Barrier Wall was established in the contract to match the MOT phasing. | The contractor is compensated for relocating temporary wall even if it is moved a small distance , since the item involves similar equipment and workflow.
2012-12-05 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 3 | BARREN | The rock line encountered in the cut near the creek was approximately 10' lower than expected. Also , the slope was composed of unsuitable material and could not be constructed as planned. | The decision was made to lay the slope back farther to reduce slope failure potential.
2012-12-04 | Design | Omission | NEW ROUTE(O) | 3 | WARREN | A traffic counting station was disturbed during construction. The plans did not address replacing the station. | The Division of Planning requested that the station be replaced by the Contractor. The Division of Planning should be consulted during project development as a check for possible conflicts with existing counting stations.
2012-12-04 | Erosion Control Plan | Retention Basin | NEW ROUTE(O) | 3 | WARREN | The drainage leaving right of way in the area between the interstate and interchange was causing some erosion issues on an adjoining field. | The Section Office decided to dig several small retention basins at the outlets of the pipes as an energy dissipater. The solution has seemingly reduced the erosion problem and should be considered when directing pipe flow into an open field , especiall
2012-12-04 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 3 | BUTLER | Removing and resetting guardrail included the end treatments; however , new end treatments for the entire length of the project were included in the contract. | These bid items were not needed on the project. The funding was needed for overrunning other items to avoid change orders.
2012-12-04 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 3 | BUTLER | Removing and resetting guardrail included the end treatments; however , new end treatments for the entire length of the project were included in the contract. | These bid items were not needed on the project. The funding was needed for overrunning other items to avoid change orders.
2012-12-04 | Structures | Omission | NEW ROUTE(O) | 3 | WARREN | While pouring the bridge deck over the steel beams , the beams rotated and twisted. | Additional bracing was required to hold the beams in the correct position until the concrete deck cured. 4 x 4 wood members were bolted together to form X bracing at 15' spacing between all the steel beams. Also , 4 x 4 wood members were placed on the
2012-12-04 | Geotechnical | Cut-Slope | RELOCATION(O) | 3 | MONROE | On the right side of the project , the geotechnical recommendation was to bench the rock cut; however , the material encountered was not solid enough to bench. | The decision was made to lay the slope back on a 2.5:1 within the right of way.
2012-12-04 | Geotechnical | Cut-Slope | RELOCATION(O) | 3 | MONROE | On the right side of the project , the geotechnical recommendation was to bench the rock cut; however , the material encountered was not solid enough to bench. | The decision was made to lay the slope back on a 2.5:1 within the right of way.
2012-12-04 | Design | Coordination | PAVEMENT REHAB-PRK(P) | 3 | BUTLER | Just prior to this project being let , a guardrail rehab project was completed and overlapped some of the guardrail on this section. | Due to the overlay , the new guardrail was removed and reset. Design and Maintenance need to better coordinate project scope and timing to reduce overlapping items and ultimately costs. The District was unaware that the Rehab project would be let soon
2012-12-04 | Maintenance of Traffic | Phasing | NEW ROUTE(O) | 3 | WARREN | SB ramp from I-65 to WH Natcher Parkway had to be paved using a piecemeal approach due to the contract not allowing for a ramp closure. This led to a construction joint in the surface in the middle of the ramp which is not ideal. | Due to the rideability and durability issues , the ramp was repaired in several locations. The Cabinet and FHWA could consider ramp closure for short durations ( 12 hour night time only ) , so that a better product could be achieved during construction
2012-12-04 | Maintenance of Traffic | Phasing | RELOCATION(O) | 3 | MONROE | The Pebble Brook Road Approach was initially set up to be completed on the Surfacing Contract due to access issues with the property owner. | The contractor proposed completing this road approach on the grade contract in order to reduce hauling costs. Traffic Bound Base was used to maintain property access. The owner was consulted prior to the change and agreed to accept the modification. Th
2012-12-04 | Design | Elevations | PAVEMENT REHAB-PRK(P) | 3 | BUTLER | The curb box inlets at the bridge ends over Green River were not included in the project scope because grades were not adjusted in this area; however , a drop off condition did exist at the boxes either from settlement or a previous overlay or combinatio | The boxes were field adjusted and paid for as Flumes.
2012-12-04 | Design | Guardrail | NEW ROUTE(O) | 3 | WARREN | The bridge piers on the C-D were designed to be protected by Type IX Crash Cushions , which adequately meet safety standards at a cheaper cost than other solutions. | With the likelihood of impact in this location and the subsequent need of repair , it was decided to install Type VI Class C TL 3-1 Crash Cushion's. This type is considered a severe use crash cushion as indicated in the STD DWG RBE-060-13.
2012-12-04 | Design | Guardrail | NEW ROUTE(O) | 3 | WARREN | The bridge piers on the C-D were designed to be protected by Type IX Crash Cushions , which adequately meet safety standards at a cheaper cost than other solutions. | With the likelihood of impact in this location and the subsequent need of repair , it was decided to install Type VI Class C TL 3-1 Crash Cushion's. This type is considered a severe use crash cushion as indicated in the STD DWG RBE-060-13.
2012-12-04 | Construction | Revisions | NEW ROUTE(O) | 3 | WARREN | The Contractor submitted a Value Engineering Proposal to substitute Hybrid PCI Beams for the Steel Beams in the original plans. | The VECP was accepted due to the savings and the safety advantages during installation. The Hybrid PCI Beams were a specialty item and were not on the approved list during project development.
2012-12-04 | Maintenance of Traffic | Phasing | RELOCATION(O) | 3 | MONROE | The Pebble Brook Road Approach was initially set up to be completed on the Surfacing Contract due to access issues with the property owner. | The contractor proposed completing this road approach on the grade contract in order to reduce hauling costs. Traffic Bound Base was used to maintain property access. The owner was consulted prior to the change and agreed to accept the modification. Th
2012-12-04 | Design | Median | NEW ROUTE(O) | 3 | WARREN | The typical section directed day lighting DGA into the median which left a very narrow strip of soil to maintain. | The Section Office decided to use DGA with Chip/Seal for the entire width of the median due to maintenance concerns.
2012-12-04 | Environmental | Landscaping | RELOCATION(O) | 3 | MONROE | Trees were set up on the contract to be planted; however , the station limits actually included part of the adjoining section. Additionally , the trees were noted to be planted along the meander of the existing stream. Part of the meandering was repla | If tree planting is required on projects , additional checks should be made to ensure that the location and amount are feasible and appropriate. A portion of the plantings on this project could not be complete as noted.
2012-12-04 | Drainage | Culvert | RELOCATION(O) | 3 | MONROE | After the project let and prior to installation , Central Office Drainage Section realized that some of the watershed had not be included in the analysis of the proposed 20x6 RCBC. | Construction Revision No. 1 involved upgrading the 20x6 RCBC to a Triple 10x5 RCBC.
2012-12-04 | Drainage | Culvert | RELOCATION(O) | 3 | MONROE | After the project let and prior to installation , Central Office Drainage Section realized that some of the watershed had not be included in the analysis of the proposed 20x6 RCBC. | Construction Revision No. 1 involved upgrading the 20x6 RCBC to a Triple 10x5 RCBC.
2012-12-04 | Traffic | Lighting | NEW ROUTE(O) | 3 | WARREN | The Contractor experienced difficulty placing the electrical along the ramps for lighting because of the narrow shoulder and the presence of guardrail. | One suggested alternative to this constructability issue is providing a wider shoulder on the ramp typical. A greater level of coordination is needed regarding the electrical and roadway plans.
2012-12-04 | Geotechnical | Elevations | RELOCATION(O) | 3 | MONROE | Rock was encountered at a much higher elevation than expected in the cut sections which created a greater quantity of usable rock material than indicated by the geotechnical investigation. | The Contractor submitted a proposal to use Rock Roadbed for the majority of the project. The rock roadbed was placed for approximately 88% of the project. The estimated savings realized was approximately $270 , 000.
2012-12-04 | Geotechnical | Elevations | RELOCATION(O) | 3 | MONROE | Rock was encountered at a much higher elevation than expected in the cut sections which created a greater quantity of usable rock material than indicated by the geotechnical investigation. | The Contractor submitted a proposal to use Rock Roadbed for the majority of the project. The rock roadbed was placed for approximately 88% of the project. The estimated savings realized was approximately $270 , 000.
2012-12-04 | Environmental | Landscaping | RELOCATION(O) | 3 | MONROE | Trees were set up on the contract to be planted; however , the station limits actually included part of the adjoining section. Additionally , the trees were noted to be planted along the meander of the existing stream. Part of the meandering was repla | If tree planting is required on projects , additional checks should be made to ensure that the location and amount are feasible and appropriate. A portion of the plantings on this project could not be complete as noted.
2012-12-04 | Structures | Omission | RELOCATION(O) | 3 | MONROE | Granular pile core was specified on the contract plans; however , the no bid items were included in the contract. | An appropriate bid item was added via change order.
2012-12-04 | Structures | Retaining Walls/MSE | NEW ROUTE(O) | 3 | WARREN | The MSE wall on the project did not include perforated pipe for drainage behind the wall. | The District felt that the pipe was needed to provide positive drainage from behind the wall as well as a redundant system with the #57 backfill.
2012-12-04 | Construction | Contracts | NEW ROUTE(O) | 3 | WARREN | The prime contractor requested to revise the contract time for CID 091310 and CID 111012 so that both projects had the same completion date of October 29 , 2011. | The Cabinet and FHWA agreed that moving to one completion date was advantageous to all parties as well as the traveling public since the project would be open to traffic sooner. This agreement additionally resolved an issue with CID 091310 not being comp
2012-12-04 | Construction | Subsurface | RELOCATION(O) | 3 | MONROE | A significant amount of subsurface drainage was encountered on the project which continually produced seepage in the embankments. | A French drain was installed with fabric , stone , and pipe. Water has been noticed continually flowing from the pipe and it appears that the solution was appropriate. Due to using some Rock Roadbed on the project , perforated pipe was also installed
2012-12-04 | Construction | Subsurface | RELOCATION(O) | 3 | MONROE | A significant amount of subsurface drainage was encountered on the project which continually produced seepage in the embankments. | A French drain was installed with fabric , stone , and pipe. Water has been noticed continually flowing from the pipe and it appears that the solution was appropriate. Due to using some Rock Roadbed on the project , perforated pipe was also installed
2012-12-04 | Structures | Omission | RELOCATION(O) | 3 | MONROE | Granular pile core was specified on the contract plans; however , the no bid items were included in the contract. | An appropriate bid item was added via change order.
2012-12-04 | Design | Entrance | RELOCATION(O) | 3 | MONROE | On John Eaton Road in the area of a 30' cut , the entrance grade to the property owner was extremely steep and tied in about 3' from the front of his storage building. | There was another entrance to this property , so the Section Office opted to eliminate the steep entrance with the permission of the owner and modified the other entrance to access the side of his building. The owner moved the main garage door to the si
2012-12-04 | Construction | Contracts | PAVEMENT REHAB-PRK(P) | 3 | BUTLER | The bid item Clean Slope was used in this project to address some sluffing rock cut issues along the parkway. The unit used for this item was LF. The item was difficult for the Contractor to bid because of the lack of definition and detail. | Designers are encouraged to present a clearly defined scope for items that are measured by LF.
2012-12-04 | Construction | Revisions | RELOCATION(O) | 3 | MONROE | The connector presented on the roadway plans included a superelevated curve on the mainline. Installation of the superelevation by design would have resulted in milling the super during the construction phase of the next section. | The decision was made by the Section Office to essentially build the connector curve without the superelevation to assist in the MOT phasing on the adjoining section and eliminate the need for piecemealing the pavement section. The speed limit on the con
2012-12-04 | Construction | Revisions | NEW ROUTE(O) | 3 | WARREN | The project was initially designed with a Concrete Barrier wall between the mainline and the C-D. Due to cost saving measures , the wall was eliminated and replaced with crash cushions at the bridge piers. Since the project opened to traffic , safety | After considering a Concrete Barrier wall , it was decided to place guardrail along the C-D to provide protection throughout not only at the bridge piers as a cost effective safety enhancement.
2012-12-04 | Design | Entrance | RELOCATION(O) | 3 | MONROE | On John Eaton Road in the area of a 30' cut , the entrance grade to the property owner was extremely steep and tied in about 3' from the front of his storage building. | There was another entrance to this property , so the Section Office opted to eliminate the steep entrance with the permission of the owner and modified the other entrance to access the side of his building. The owner moved the main garage door to the si
2012-11-15 | Traffic | Coordination | RELOCATION(O) | 12 | MARTIN | The contractor presented a proposal to install 3 1/2 PVC conduit in lieu of Steel for the conduit encapsulated in concrete on the bridge. | The Division of Traffic accepted the proposal for the change in material type which resulted in a significant reduction in price. Designers should consult with the Division of Traffic about the possibility of using PVC on the plans for conduit encapsulat
2012-11-15 | Drainage | Quantities | SAFETY(P) | 12 | LETCHER | The quantity on the pipe drainage summary did not match the plan sheet from Sta 104+48 - Sta 105+92. | The quantity of Storm Sewer Pipe - 18 inch was adjusted on Change Order #2.
2012-11-15 | Maintenance of Traffic | Safety | SAFETY(P) | 12 | LETCHER | The proximity of the traffic signal to the bridge caused concerns during the phasing changes. | The stop bars were relocated to enhance the safety of the traveling public.
2012-11-15 | Design | Guardrail | SAFETY(P) | 12 | LETCHER | Normal guardrail posts could not be used at the bridge ends due to the sidewalk location. | The Steel Post Type 2 item was added via change order.
2012-11-15 | Structures | Handrail | SAFETY(P) | 12 | LETCHER | Due to the widening on the bridge , the proposed handrail on one side would not have matched the old handrail. | After discussions with Central Office and FHWA , the decision was made to remove , store , and reinstall the existing handrails on the widened portion of the bridge to match the other side.
2012-11-15 | Erosion Control Plan | Channel Lining | RELOCATION(O) | 12 | MARTIN | The confluence of Cold Water Fork and Black Log Creek is approximately 50 feet upstream of Pier III. At this location , Cold Water Fork makes nearly a 90 degree turn. This area was grubbed during construction increasing erosion potential. | The decision was made to install Class III Channel Lining for slope protection.
2012-11-15 | Maintenance of Traffic | Omission | SAFETY(P) | 12 | LETCHER | The contract documents did not include a bid item for black temporary paint for shifting traffic on the bridges during construction. | The bid item was added via change order.
2012-11-15 | Design | Guardrail | SAFETY(P) | 12 | LETCHER | Normal guardrail posts could not be used at the bridge ends due to the sidewalk location. | The Steel Post Type 2 item was added via change order.
2012-11-15 | Utilities | Existing Utilities | SAFETY(P) | 12 | LETCHER | Due to the acceleration of the project , the planned utility relocations were not complete prior to letting. The conflicting utilities were primarily telephone and sewer. | At the direction of the Cabinet , the contractor coordinated directly with the subject utility companies in order to expedite the relocations. The contractor paid the utility companies and received reimbursement from the Cabinet.
2012-11-15 | Construction | Coordination | RELOCATION(O) | 12 | MARTIN | The contractor intended to gain access to Piers 1 & 2 by an apparent public road. The Section Office received complaints about the contractor using a private road. District 12 legal staff advised of ongoing litigation over the ownership of the road. | The Cabinet directed the contractor to construct a temporary access road along the fill slope of existing Ramp C , which resulted in removing and reinstalling 187.5 LF guardrail along the ramp. Supplemental pricing was provided by the contractor.
2012-11-15 | Structures | Quantities | RELOCATION(O) | 12 | MARTIN | The quantity presented for the bid item for Class AA Concrete was significantly too high leading to an underrun. | An agreement was reached with the contractor for revised pay quantity.
2012-11-15 | Geotechnical | Slides | RELOCATION(O) | 12 | MARTIN | An existing slide was encountered near existing KY 40 between Sta 1+040 and Sta 1+100. The plans indicated removal of material to stabilize the area; however , the slide expanded prior to construction which extended past the plan clearing limits. | The Cabinet directed the contractor to completely remove the slide. The compensation for this work included overhaul.
2012-11-15 | Traffic | Signals | SAFETY(P) | 12 | LETCHER | One of the traffic signal poles was installed very close to the shoulder at Rt Sta 115+35 due to the proximity of the rock cut. There was very little space in this area to adjust the pole to a safer location. | Guardrail was extended to protect the pole for safety reasons.
2012-11-15 | Traffic | Omission | SAFETY(P) | 12 | LETCHER | On the bridges , the new lane lines did not match the old lane lines. The plans did not address the method of removing the old pavement striping. | The Section Office decided to use Water Blasting as the preferred method of striping removal on the bridge.
2012-11-15 | Structures | Quantities | SAFETY(P) | 12 | LETCHER | There was an insufficient amount of common excavation established for the bridge. One apparent cause was a mound of soil that was left in the area of one of the piers , which appeared to be a utility relocation. The 1.5 feet limit around pier and abutm | Additional quantity of common excavation was necessary to adequately compensate the contractor.
2012-11-15 | Maintenance of Traffic | Omission | SAFETY(P) | 12 | LETCHER | Due to the required shifting of traffic for the various phases of this project , temporary striping tape was needed but was not included in the contract documents as a bid item. | A bid item for temporary tape was added. Designers are encouraged to set up quantities for temporary tape especially when bridge phasing is required.
2012-11-15 | Design | Omission | SAFETY(P) | 12 | LETCHER | The removal of existing guardrail was included in the plans; however , the appropriate bid item was omitted from the contract. | The bid item for guardrail removal was added via change order.
2012-11-15 | Construction | Contracts | RELOCATION(O) | 12 | MARTIN | Incorrect wage rates were provided in the proposal. | A change order was created to adjust the wage rates.
2012-11-15 | Design | Quantities | RELOCATION(O) | 12 | MARTIN | The Roadway Excavation quantity as presented in the bid documents did not include Embankment Benching. | Adjustments were made to compensate the contractor for this yardage.
2012-11-15 | Structures | Elevation Difference | SAFETY(P) | 12 | LETCHER | As the contractor prepared to construct the widened portion of the short bridge deck , it was determined that the elevations were higher than the existing bridge deck. | The lack of positive drainage and safety concerns at the joint led to the decision to remove the overlay from the old bridge deck and install a new overlay that matched the new deck elevations.
2012-11-15 | Maintenance of Traffic | Omission | RELOCATION(O) | 12 | MARTIN | A pipe transverse to existing KY 40 was replaced according to plans; however , asphalt quantities were not established in the contract documents to replace the pavement structure. | The Section Office coordinated obtaining a load of asphalt using a Maintenance Agreement and the contractor agreed to place it at no additional cost to the Cabinet. With the small quantity , it could have been challenging to agree to a reasonable price
2012-11-15 | Structures | Reinforcement Steel | SAFETY(P) | 12 | LETCHER | The steel reinforcement on the bridge sidewalks and walls was detailed incorrectly and dimensionally would not fit with the required cover. | The Cabinet directed the contractor to reorder the steel with corrected dimensions and paid for the excess steel that was delivered to the KYTC Letcher County Maintenance facility.
2012-11-15 | Construction | Method/Innovation | SAFETY(P) | 12 | LETCHER | The original design called for placing asphalt treated drainage blanket in an area where 4 inch perforated pipe was also located. The temperature at placement would have damaged the plastic pipe. | #57 stone was used around the pipe to protect it prior to placing the drainage blanket.
2012-11-14 | Design | Excavation | RELOCATION(O) | 12 | PIKE | The contractor provided evidence that several areas on the project had overhanging rocks that were not shown on the cross sections and therefore were not included in the yardage in the plans. | These areas required step drilling prior to excavation. A fall bench was constructed in order to protect the homes located below the cut. The contractor was compensated for the additional quantity of Roadway Excavation.
2012-11-14 | Drainage | Culvert | RELOCATION(O) | 12 | PIKE | A Value Engineering Change Proposal had been submitted by the contractor and was rejected by the Cabinet. KYTC did however accept a part of the proposal to change the proposed RCBC to an 84 Concrete Pipe. | This solution resulted in a savings to the Cabinet; however , the Division of Maintenance and District 12 do not support this practice. Designers should continue specifying RCBC's for larger culvert situations (cast in place only).
2012-11-14 | Drainage | Ditches | RELOCATION(O) | 12 | PIKE | A storm sewer system was installed on this project along the roadside to reduce the amount of excavation in an effort to reduce overall project cost. The storm sewer has already experienced clogging due to debris from the cut. | The Division of Maintenance does not support this practice. Designers are encouraged to use open channels in these instances.
2012-11-14 | Geotechnical | Mine | RELOCATION(O) | 12 | PIKE | The item Pneumatic Backstowing had been established in this contract for mine openings encountered in the rock cuts; however , the quantity was insufficient. Also , the contract did not address drainage for these situations. | Additional backstowing was needed as well as a bid item for PVC Pipe - 4 inch to drain the mine openings. In some instances , Gabion Retaining Walls were used to shore up the area around the openings.
2012-11-14 | Erosion Control Plan | Seeding | RELOCATION(O) | 12 | PIKE | The contractor cleared an area for excavation which was larger than allowed and part of the area lay dormant for approximately 30 days without disturbance. During this time frame , the project was sited by the KY Division of Water. | The Cabinet directed the contractor to temporary seed these areas. Even though this activity was not the fault of the Cabinet , the decision was made by Central Office to reimburse the contractor for the additional seeding.
2012-11-14 | Utilities | Existing Utilities | RELOCATION(O) | 12 | PIKE | Equitable Gas Company experienced difficulty accessing the relocation site Lt Sta 495+00. | The Cabinet coordinated the construction of an access road built by our contractor for the benefit of Equitable Gas Company in their relocation efforts.
2012-11-14 | Geotechnical | Slides | RELOCATION(O) | 12 | PIKE | Several areas on the project involved transitioning from a large rock cut into a steep hollow. The material encountered in these hollows is typically poor quality. Also , slides commonly form on the side hills after the toe of the slope is removed for | District 12 recommends purchasing extra Right of Way in these areas to account for the possible failure of the resulting slopes.
2012-11-14 | Structures | Retaining Walls/MSE | RELOCATION(O) | 12 | PIKE | During construction , a slide formed Rt Sta 799+15 to Sta 803+50. This slide impacted a nearby stream and a residence. | A Sierrascape MSE retaining wall system was installed as slope protection. The Cabinet specified the use of quarried limestone as a backfill material (Select Fill) which contributed to an expensive solution. Sandstone from the project would have been a
2012-11-14 | Structures | Dimensions | RELOCATION(O) | 12 | PIKE | The plan dimensioning did not allow for proper clearance of the steel reinforcement Type B bars on the RCBC. | Additional Class A Concrete was placed to accomplish the proper clearance.
2012-11-14 | Construction | Revisions | RELOCATION(O) | 12 | PIKE | The letting for the adjoining section 8B of US 460 was delayed. This would have led to paying substantial in lieu fees for out of season clearing (Indiana Bat). | In order to avoid the in lieu fees , tree cutting was added to the scope of work on this contract.
2012-11-14 | Construction | Safety | RELOCATION(O) | 12 | PIKE | The section of Wolfpit Road leading to the project site had two bridges (MP 0.45 & MP 0.75) that were not sufficient to handle trucks carrying equipment and material. This created an inaccessibility issue for the contractor. | It was decided to upgrade the bridges in order to provide better access to the project for equipment and material. The solution to the bridge at MP 0.45 involved driving piles , fabricating a new cap , and placing new steel beams with an 8 concrete dec
2012-11-14 | Construction | Safety | RELOCATION(O) | 12 | PIKE | The property owner on Parcel 740 complained during construction about their personal safety. The property was located near the bridge on Beaver Creek. | Parcel 740 was purchased by the contractor and the Cabinet reimbursed the contractor for a total take on the property due to constructability and safety issues.
2012-11-14 | Geotechnical | Piling/Drilled Shaft | RELOCATION(O) | 12 | PIKE | The design for the piles on Drawing No. 26067 stated that the design of the wall was invalid if the elevation of the top of the rock socket was below 999.0. The actual elevation encountered in the field during drilling was 996.0. | The Division of Structural Design directed the Section Office to place Class B Concrete to an elevation of 1007.0. The bid item quantities for Class B Concrete and Piles-Steel W14x211 were adjusted on Change Order 6.
2012-11-14 | Geotechnical | Unsuitable Material | RELOCATION(O) | 12 | PIKE | Unsuitable material was encountered while excavating several of the pier footings to solid rock. Weathered rock was part of the issue as well as over drilling by the contractor. | Mass concrete was used to replace the unsuitable material and to extend the footing down to solid rock. Designers are currently providing Geotech the footprint of the footing instead of only the center which allows drilling at the outer edges of the foot
2012-11-08 | Geotechnical | Piling/Drilled Shaft | MINOR WIDENING(O) | 6 | KENTON | Following the completion of seven drilled shafts at Retaining Wall C , Central Office Geotech determined the sand elevation was lower than anticipated leading to a decreased capacity. Boring investigation was limited on this parcel due the lack of permi | Central Office Geotechnical Branch recommended 5 additional drilled shafts. The contractor remobilized the 36 shaft tooling , re-excavate spoils left from the additional shafts , and re-form the Retaining Wall. Building rubble and debris were encounte
2012-11-08 | Traffic | Markings | MINOR WIDENING(O) | 6 | KENTON | The contract plans did not indicate that the pavement used at the pedestrian crosswalks should be colored red as required in an MOA between the KYTC and the City of Covington. | A supplemental item for JPC Pavement 10 in - Color addition was necessary to add integral red coloring and red surface hardener to the Stamped Concrete - 10 in. Simply specifying stamped and stained red crosswalks is inadequate. The integral feature of
2012-11-08 | Traffic | Signals | MINOR WIDENING(O) | 6 | KENTON | The project signal system was set up for loops to be installed at each signalized intersection. Due to the paving stone roadway , multiple loops had to be eliminated. | Cameras were installed to serve the function of the loops.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | It was determined that the 4 inch Expansion Joints were failing at Piers 6 , 12 , 23 , and 40 on the SB Deck of the Brent Spence Bridge. | The expansion joints were replaced along with the seal. The armored edges were eliminated and the joint was sealed using a non-preformed sealant.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | It was determined that the 4 inch Expansion Joints were failing at Piers 6 , 12 , 23 , and 40 on the SB Deck of the Brent Spence Bridge. | The expansion joints were replaced along with the seal. The armored edges were eliminated and the joint was sealed using a non-preformed sealant.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | It was determined that the 4 inch Expansion Joints were failing at Piers 6 , 12 , 23 , and 40 on the SB Deck of the Brent Spence Bridge. | The expansion joints were replaced along with the seal. The armored edges were eliminated and the joint was sealed using a non-preformed sealant.
2012-11-08 | Design | Omission | MINOR WIDENING(O) | 6 | KENTON | Sheet R13 of the plans indicated that cellar openings in the sidewalk on Madison Avenue were to be removed and the voids filled with flowable fill; however , no bid items were included for blocking of the foundation or backfilling the voids. | Appropriate bid items were established via change order.
2012-11-08 | Construction | Revisions | MINOR WIDENING(O) | 6 | KENTON | Handicap access was not provided to Parcel #71. The owner was compensated appropriately during the Right of Way negotiation process. The owner complained during construction about the lack of handicap access. | The District agreed to add handicap access at this parcel.
2012-11-08 | Construction | Public Relations | PAVEMENT REHAB-INT(P) | 6 | KENTON | The goal initially on this project was to use the 511 system as the primary way to communicate with the public. As the project developed , it was determined that the 511 system was not an effective media outlet for the Cabinet's construction projects. | For future projects , designers should not rely on 511 as the primary outlet for media blitzes.
2012-11-08 | Construction | Public Relations | PAVEMENT REHAB-INT(P) | 6 | KENTON | The goal initially on this project was to use the 511 system as the primary way to communicate with the public. As the project developed , it was determined that the 511 system was not an effective media outlet for the Cabinet's construction projects. | For future projects , designers should not rely on 511 as the primary outlet for media blitzes.
2012-11-08 | Construction | Public Relations | PAVEMENT REHAB-INT(P) | 6 | KENTON | The goal initially on this project was to use the 511 system as the primary way to communicate with the public. As the project developed , it was determined that the 511 system was not an effective media outlet for the Cabinet's construction projects. | For future projects , designers should not rely on 511 as the primary outlet for media blitzes.
2012-11-08 | Structures | Approaches | MINOR WIDENING(O) | 6 | KENTON | Approach slabs were not included in the design plans for this project. These slabs are typically used to reduce the impact of bridge end settlement. | District 6 personnel determined the addition of approach slabs on both the East and West sides of the new bridge were warranted due to bridge end settlement being likely. Quantity adjustments for contract items JPC Pavement - 10 in , Concrete - Class AA
2012-11-08 | Structures | Beams | MINOR WIDENING(O) | 6 | KENTON | The Camber Table on Sheet S41 of the Structural Design Plans included a column titled Total Camber; however , the calculation only reflected the deflection portion with no accommodation for the vertical curve. The fabricated beams did not have the requi | The Division of Construction coordinated with the Division of Structural Design to provide a revised Camber Table to the fabricator. The fabricator achieved the necessary camber by heat bending the steel beams. An administrative settlement agreement was
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | The quantity for the item Approach Slab at the Pike Street to NB I-75 Ramp over 9th street was insufficient compared to the limits of the existing approach slab. | Additional quantity of Approach Slab was established via change order.
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | The quantity for the item Approach Slab at the Pike Street to NB I-75 Ramp over 9th street was insufficient compared to the limits of the existing approach slab. | Additional quantity of Approach Slab was established via change order.
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | The quantity for the item Approach Slab at the Pike Street to NB I-75 Ramp over 9th street was insufficient compared to the limits of the existing approach slab. | Additional quantity of Approach Slab was established via change order.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | Several of the existing expansion joints that were set up to be removed and replaced appeared to be in good condition except the joint seal. Also , the armored edges at each approach slab were determined to be acceptable in condition. | It was decided to leave the joint in place and replace the joint sealant.
2012-11-08 | Structures | Communication | MINOR WIDENING(O) | 6 | KENTON | An agreement was entered into between KYTC and the City of Covington which included using Arch Bridge Rail Form liners for all barrier walls on the bridge; however , the contract plans indicated using Jersey Face on the North barrier of the EB bridge. T | Appropriate quantity adjustments were made to the contract items of Concrete - Class AA , Steel Reinforcement - Epoxy Coated , and Rail System Type III.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | Several of the existing expansion joints that were set up to be removed and replaced appeared to be in good condition except the joint seal. Also , the armored edges at each approach slab were determined to be acceptable in condition. | It was decided to leave the joint in place and replace the joint sealant.
2012-11-08 | Structures | Expansion Joints | PAVEMENT REHAB-INT(P) | 6 | KENTON | Several of the existing expansion joints that were set up to be removed and replaced appeared to be in good condition except the joint seal. Also , the armored edges at each approach slab were determined to be acceptable in condition. | It was decided to leave the joint in place and replace the joint sealant.
2012-11-08 | Design | Omission | MINOR WIDENING(O) | 6 | KENTON | The roadway excavation between stations 38+00 and 40+00 left of CL included the removal of a substantial concrete wall. | Removal of this wall should typically be considered a separate item of work. An appropriate bid item was established.
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | Some of the ramp approach slabs appeared to be in good condition. | It was decided to only replace the exiting end of the approach slab at B00088 (Exit Ramp to 5th Street from NB I-75 over ramp from Pike Street to NB I-75 which resulted in a savings to the department.
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | Some of the ramp approach slabs appeared to be in good condition. | It was decided to only replace the exiting end of the approach slab at B00088 (Exit Ramp to 5th Street from NB I-75 over ramp from Pike Street to NB I-75 which resulted in a savings to the department.
2012-11-08 | Structures | Approaches | PAVEMENT REHAB-INT(P) | 6 | KENTON | Some of the ramp approach slabs appeared to be in good condition. | It was decided to only replace the exiting end of the approach slab at B00088 (Exit Ramp to 5th Street from NB I-75 over ramp from Pike Street to NB I-75 which resulted in a savings to the department.
2012-11-08 | Design | Omission | MINOR WIDENING(O) | 6 | KENTON | Due to the grading between the bridges at each abutment , the center retaining wall created the possibility of a drop off hazard for pedestrians. | The lower portion of the retaining wall was raised to the top of the inner barrier wall on the lower bridge.
2012-11-08 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 6 | KENTON | There was a significant amount of erosion at Rt Sta 484 where an existing curb experienced failure. | A gravity retaining wall was constructed to provide a permanent solution to the drainage problem at this location.
2012-11-08 | Maintenance of Traffic | Quantities | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the volume of traffic that passes through the project , and the traffic that accesses the project from adjoining interstates , additional Portable Changeable Message Boards were needed. | A total of six PCMS were added to the project with change orders.
2012-11-08 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 6 | KENTON | There was a significant amount of erosion at Rt Sta 484 where an existing curb experienced failure. | A gravity retaining wall was constructed to provide a permanent solution to the drainage problem at this location.
2012-11-08 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 6 | KENTON | There was a significant amount of erosion at Rt Sta 484 where an existing curb experienced failure. | A gravity retaining wall was constructed to provide a permanent solution to the drainage problem at this location.
2012-11-08 | Structures | Piling/Drilled Shaft | MINOR WIDENING(O) | 6 | KENTON | During drilling at Shaft #17 at Pier 4 of the EB bridge , the drilling contractor encountered a large concrete structure. Two additional structures were encountered at Pier 4. | The drilling contractor was forced to relocate to a different shaft while the bridge contractor removed the structure and backfilled the resulting excavation with flowable fill for stability. The supplemental item Remove Structure - Pier 4 was added to t
2012-11-08 | Maintenance of Traffic | Phasing | MINOR WIDENING(O) | 6 | KENTON | Project traffic control plans did not include any information for the transition between adjacent projects. Coordination between projects was necessary to time the traffic switch from Phase 1 to Phase 2 properly. | Contractor on the adjacent project was forced to perform some work out of phase and schedule in order to provide sufficient area for transition.
2012-11-08 | Maintenance of Traffic | Striping | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the necessity to re-stripe after the diamond grinding operation , an insufficient quantity of temporary striping was established in the contract. | Temporary striping was added via change order.
2012-11-08 | Drainage | Headwalls | MINOR WIDENING(O) | 6 | KENTON | The drainage summary included headwalls paid as each as well as concrete and steel separately. | All items are being paid as presented in the contract. The contractor is likely receiving double compensation for the headwall items.
2012-11-08 | Maintenance of Traffic | Quantities | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the volume of traffic that passes through the project , and the traffic that accesses the project from adjoining interstates , additional Portable Changeable Message Boards were needed. | A total of six PCMS were added to the project with change orders.
2012-11-08 | Traffic | Signals | MINOR WIDENING(O) | 6 | KENTON | Temporary signals were designed with steel strain poles with concrete bases. | KYTC elected to install temporary wood poles at a reduced price.
2012-11-08 | Maintenance of Traffic | Quantities | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the volume of traffic that passes through the project , and the traffic that accesses the project from adjoining interstates , additional Portable Changeable Message Boards were needed. | A total of six PCMS were added to the project with change orders.
2012-11-08 | Maintenance of Traffic | Striping | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the necessity to re-stripe after the diamond grinding operation , an insufficient quantity of temporary striping was established in the contract. | Temporary striping was added via change order.
2012-11-08 | Maintenance of Traffic | Striping | PAVEMENT REHAB-INT(P) | 6 | KENTON | Due to the necessity to re-stripe after the diamond grinding operation , an insufficient quantity of temporary striping was established in the contract. | Temporary striping was added via change order.
2012-11-08 | Design | Safety | MINOR WIDENING(O) | 6 | KENTON | The noses for the raised grass medians were constructed per plan by carrying the curb and gutter section around. | This design feature could be a traffic hazard should the nose get struck by a motorist. The noses were reconstructed to match the nose for a Barrier Median (Std Dwg RPM-010-05).
2012-11-08 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-INT(P) | 6 | KENTON | During construction , it was decided to remove and replace the armored edge at Brent Spence Bridge Abutment no. 1 and C1 , C2 at Entrance ramp to NB I-75 from Fourth Street in Covington and SB at Exit 192 ramp to Fifth Street in Covington in accordance | Due to the replacement of the joints on the SB Brent Spence approach bridge (upper level) , lane closures were necessary directly below the work on NB Brent Spence approach bridge. The angle that the SB bridge transitions away from the NB bridge made it
2012-11-08 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-INT(P) | 6 | KENTON | During construction , it was decided to remove and replace the armored edge at Brent Spence Bridge Abutment no. 1 and C1 , C2 at Entrance ramp to NB I-75 from Fourth Street in Covington and SB at Exit 192 ramp to Fifth Street in Covington in accordance | Due to the replacement of the joints on the SB Brent Spence approach bridge (upper level) , lane closures were necessary directly below the work on NB Brent Spence approach bridge. The angle that the SB bridge transitions away from the NB bridge made it
2012-11-08 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-INT(P) | 6 | KENTON | During construction , it was decided to remove and replace the armored edge at Brent Spence Bridge Abutment no. 1 and C1 , C2 at Entrance ramp to NB I-75 from Fourth Street in Covington and SB at Exit 192 ramp to Fifth Street in Covington in accordance | Due to the replacement of the joints on the SB Brent Spence approach bridge (upper level) , lane closures were necessary directly below the work on NB Brent Spence approach bridge. The angle that the SB bridge transitions away from the NB bridge made it
2012-11-08 | Pavement | Repair | PAVEMENT REHAB-INT(P) | 6 | KENTON | Once construction commenced , it was determined that the existing pavement had deteriorated significantly since the assessment during project development. | An additional quantity of JPC pavement was required as the existing patches in the field were larger than the specified quantities in the project proposal.
2012-11-08 | Pavement | Repair | PAVEMENT REHAB-INT(P) | 6 | KENTON | Once construction commenced , it was determined that the existing pavement had deteriorated significantly since the assessment during project development. | An additional quantity of JPC pavement was required as the existing patches in the field were larger than the specified quantities in the project proposal.
2012-11-08 | Utilities | Existing Utilities | MINOR WIDENING(O) | 6 | KENTON | The intersection of Madison Avenue involved many conflicts with existing utilities. | Storm sewer pipe grades had to be adjusted throughout the project to work around utilities. A Type 16 DBI was added at Sta. 11+73. The CBI at Sta. 10+18 was changed to a Type 16 DBI. SUE should be considered during project development on downtown proje
2012-11-08 | Utilities | Existing Utilities | MINOR WIDENING(O) | 6 | KENTON | Though a portion of the electric relocation was to take place in conjunction with the contract , the overhead electric near the existing bridge was to be relocated prior to beginning work on the bridge. This line remained in conflict at the beginning of | The contractor was able and willing to work around the conflicts until relocation occurred. Utility impact notes should be included in the contract proposal if utility conflicts are expected to extend past the award to the contractor.
2012-11-08 | Pavement | Repair | PAVEMENT REHAB-INT(P) | 6 | KENTON | Once construction commenced , it was determined that the existing pavement had deteriorated significantly since the assessment during project development. | An additional quantity of JPC pavement was required as the existing patches in the field were larger than the specified quantities in the project proposal.
2012-11-08 | Design | Communication | MINOR WIDENING(O) | 6 | KENTON | The raised crosswalk near the Diocese of Covington was designed in a location that did not fit the existing pedestrian patterns very well and even though this was agreed to with the owner during project development , the owner complained during construct | At the request of the City of Covington and the Diocese , the location of the raised crosswalk was relocated to better suit the needs of the adjacent School. Pedestrian traffic from the school use the raised crosswalk to access the building directly acr
2012-11-08 | Design | Omission | MINOR WIDENING(O) | 6 | KENTON | Brick Pavers were specified for the sidewalks; however , the plans did not present a method to confine the pavers while placing Asphalt next to them. | It was necessary to add steel angles to the back of the brick paver sidewalks to confine the paving stones and prevent movement.
2012-11-08 | Utilities | Existing Utilities | MINOR WIDENING(O) | 6 | KENTON | The contract plans included storm sewers that involved connections to an existing combined sewer system. The Sanitation District informed the contractor that the pipe that was being installed did not meet their specifications. | Alternate pipe was required to meet the Sanitation District's specifications. PVC or ductile iron must be specified when connecting into combined sewer systems.
2012-11-08 | Design | Radius | MINOR WIDENING(O) | 6 | KENTON | The intersection radii at Madison Avenue was designed too tight considering the truck volumes on both routes. | The light poles on the SW and SE corners were impacted by traffic and were relocated behind the sidewalk. The curb box on the NW corner was destroyed by traffic and was rebuilt with modification to strengthen the top.
2012-11-08 | Traffic | Signals | MINOR WIDENING(O) | 6 | KENTON | The contract plans did not indicate that the signal poles , mast arms , and remaining components should be black as required by the MOA between KYTC and the City of Covington. | The Section Office negotiated an item Paint Signal System with the contractor. The original signal plans indicated black components; however , Central Office Traffic struck the term black prior to letting without notifying the District or the Design Con
2012-11-08 | Design | Special Note | MINOR WIDENING(O) | 6 | KENTON | Special Note for Excavation and Embankment 10Z was used on this project which directed the Section Engineer to compensate the contractor for both items. The original contract did not include a bid item for Embankment. | Embankment bid item was established via change order. Current policy directs designers to not use this Special Note on contracts.
2012-11-07 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 6 | HARRISON | Utility relocation plans that are designed by independent firms hired directly by the Utility Companies often detail utilities that do not reflect the best interest of their client or the Cabinet. A Sewer Main on this project was proposed to be located o | The Cabinet , contractor , and utility companies worked together to develop a common sense design based on field conditions. Early coordination efforts are encouraged. District 6 is currently implementing a pilot program to get utility relocation plan
2012-11-07 | Structures | Retaining Walls/MSE | BRIDGE REPLACEMENT(P) | 6 | HARRISON | The bridge end at IEB #1 experienced extensive settlement due to the lack of expansion joints. The MSE wall compounded the settlement issue because a gap formed between the wall and the abutment allowing fines to migrate out of the bridge backfill materi | A concrete curtain wall was installed to repair the gap between the wall and abutment. Also , grout was pumped into the voids at the bridge end and pavement wedges have been used on the approach on several occasions. Settlement continues to occur at th
2012-11-07 | Pavement | Quantities | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | Quantities for Leveling and Wedging were established but were not needed considering the type of rehabilitation in the project and the depth of the base layers. | Level and wedging was removed from the contract.
2012-11-07 | Pavement | Quantities | PAVEMENT REHAB-INT(P) | 6 | BOONE | Quantities for Leveling and Wedging were established but were not needed considering the type of rehabilitation in the project and the depth of the base layers. | Level and wedging was removed from the contract.
2012-11-07 | Maintenance of Traffic | Phasing | BRIDGE REPLACEMENT(P) | 6 | HARRISON | In order to construct Pier 8 , it was necessary to excavate 30' deep within about 10' of the existing end bent. This would have required an extensive amount of temporary shoring. | The contractor requested a road closure until traffic could be diverted to the new bridge. Because of the substandard sufficiency of the existing structure , truck traffic had already been detoured for approximately one year. The Cabinet coordinated wi
2012-11-07 | Design | Quantities | PAVEMENT REHAB-INT(P) | 6 | BOONE | The quantity established in the contract documents for Bridge End Digouts accounted for only for one direction. | Additional quantity was established with a change order.
2012-11-07 | Design | Quantities | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The quantity established in the contract documents for Bridge End Digouts accounted for only for one direction. | Additional quantity was established with a change order.
2012-11-07 | Drainage | Pipes | BRIDGE REPLACEMENT(P) | 6 | HARRISON | The entrance Lt Sta 60+20 was located in an area where the proposed ditchline was very flat. In addition to the lack of fall , a large concrete structure was encountered during excavation of the ditchline , so the plan elevations were not achieved. | The proposed 15 entrance pipe at Lt Sta 60+20 was replaced with a 15 equivalent pipe as a better fit considering field conditions encountered.
2012-11-07 | Design | Omission | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | Asphalt Seal Aggregate and Emulsified Asphalt RS-2 were omitted from the contract for the outside shoulders. | Appropriate quantities of both were added via change order.
2012-11-07 | Design | Omission | PAVEMENT REHAB-INT(P) | 6 | BOONE | Asphalt Seal Aggregate and Emulsified Asphalt RS-2 were omitted from the contract for the outside shoulders. | Appropriate quantities of both were added via change order.
2012-11-07 | Design | Quantities | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The blowup detail in the plans did not show the top layer of fabric and the quantity was omitted from the contract. | Extra fabric was established with a change order.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | BOONE | The Type 3 Guardrail End Treatments that were set up to replace existing Type 3's were not feasible based on field conditions. | All but one Type 3 End Treatment were modified to Type 1 End Treatments.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The Type 3 Guardrail End Treatments that were set up to replace existing Type 3's were not feasible based on field conditions. | All but one Type 3 End Treatment were modified to Type 1 End Treatments.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The Type 3 Guardrail End Treatments that were set up to replace existing Type 3's were not feasible based on field conditions. | All but one Type 3 End Treatment were modified to Type 1 End Treatments.
2012-11-07 | Design | Quantities | PAVEMENT REHAB-INT(P) | 6 | BOONE | The blowup detail in the plans did not show the top layer of fabric and the quantity was omitted from the contract. | Extra fabric was established with a change order.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | BOONE | The Type 3 Guardrail End Treatments that were set up to replace existing Type 3's were not feasible based on field conditions. | All but one Type 3 End Treatment were modified to Type 1 End Treatments.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The plans did not include enough guidance or detail for the connection between the bridge barrier retrofit and the bridge end connectors. | Field adjustments were necessary to make the connection meet safety standards.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | BOONE | The plans did not include enough guidance or detail for the connection between the bridge barrier retrofit and the bridge end connectors. | Field adjustments were necessary to make the connection meet safety standards.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The plans did not include enough guidance or detail for the connection between the bridge barrier retrofit and the bridge end connectors. | Field adjustments were necessary to make the connection meet safety standards.
2012-11-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 6 | BOONE | The plans did not include enough guidance or detail for the connection between the bridge barrier retrofit and the bridge end connectors. | Field adjustments were necessary to make the connection meet safety standards.
2012-11-07 | Environmental | Permitting | BRIDGE REPLACEMENT(P) | 6 | HARRISON | The Cabinet was issued a letter of concern by the EPA during construction. | The contractor addressed all of the concerns listed in a timely fashion. The District Environmental Coordinator proactively dealt with the letter of concern with response correspondence. The coordination efforts led to complete resolution.
2012-11-07 | Drainage | Existing Pipe | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | Several pipe repairs were set up on the contract; however , the section office identified many pipes and headwalls in the project limits in need of repair. Also , many of the headwall repairs did not address damaged pipe ends. | Additional quantities of the appropriate bid items were added via change order.
2012-11-07 | Construction | Revisions | PAVEMENT REHAB-INT(P) | 6 | BOONE | During construction , it was decided by the District to stripe 2 lanes on the ramp SB I-75 to I-71; however , the configuration that was striped did not completely meet design guidelines. | The ramp was re-striped with the original configuration until improvements were made that allowed for expansion to a 2 lane ramp. Traffic demands led to the decision and traffic flow has been enhanced with the modification.
2012-11-07 | Construction | Revisions | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | During construction , it was decided by the District to stripe 2 lanes on the ramp SB I-75 to I-71; however , the configuration that was striped did not completely meet design guidelines. | The ramp was re-striped with the original configuration until improvements were made that allowed for expansion to a 2 lane ramp. Traffic demands led to the decision and traffic flow has been enhanced with the modification.
2012-11-07 | Drainage | Existing Pipe | PAVEMENT REHAB-INT(P) | 6 | BOONE | Several pipe repairs were set up on the contract; however , the section office identified many pipes and headwalls in the project limits in need of repair. Also , many of the headwall repairs did not address damaged pipe ends. | Additional quantities of the appropriate bid items were added via change order.
2012-11-07 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 6 | HARRISON | Utilities relocations were designed on easements that were not purchased prior to letting. The utility coordination efforts were performed by District 9 Utilities. | The District decided to modify the utility relocations to be located on acquired R/W or easements. The Section Office coordinated with the Contractor and the modifications resulted in minimal cost increase to the Cabinet.
2012-11-07 | Maintenance of Traffic | Striping | PAVEMENT REHAB-INT(P) | 6 | GALLATIN | The original temporary paint quantities did not account for striping after the edge drain was removed and replaced and the second lift of base was placed. | Additional striping quantities were added to the contract.
2012-11-07 | Maintenance of Traffic | Striping | PAVEMENT REHAB-INT(P) | 6 | BOONE | The original temporary paint quantities did not account for striping after the edge drain was removed and replaced and the second lift of base was placed. | Additional striping quantities were added to the contract.
2012-11-07 | Construction | Inspection | BRIDGE REPLACEMENT(P) | 6 | HARRISON | Two major flood events occurred during construction. This led to problems with the storm sewer pipe filling with debris and failing the pipe video inspection. | The contractor complied with the specifications; however , they expressed concern over the Cabinet holding to strict adherence to the specs regarding pipe inspection after significant flood events.
2012-11-07 | Construction | Coordination | BRIDGE REPLACEMENT(P) | 6 | HARRISON | Piers 5 and 6 required coordination with CSX railroad in regards to temporary shoring. The standard note clearly stated that is was the contractor's responsibility. The time and effort needed to obtain approval from CSX for the shoring plan would likely | The contractor proposed modifying the piers by raising the footing in conjunction with installing piling into subsurface rock at no additional cost to the Cabinet. District 6 also prefers the cost of railroad flagging operations to be paid directly by th
2012-10-24 | Traffic | Lighting | RECONSTRUCTION(O) | 4 | MARION | The original plans did not address the roadway lighting north of Sta. 28+200. | Additional lighting was needed on I-75 northbound , I-75 southbound , Ramp 2 , Ramp 2a , Collector-Distributor , I-275 Ramps to Collector-Distributor , and I-75 northbound ramps to I-275.
2012-10-24 | Design | Intersection | RECONSTRUCTION(O) | 4 | MARION | The Contractor submitted a value engineering proposal for the southeast quadrant of the Donaldson Road Interchange that eliminated several items that they felt were unnecessary. | Their proposal was approved , which eliminated a portion of the roadway excavation , guardrail , and a headwall while maintaining proper grade , drainage , sound protection , and an aesthetically pleasing final product. Due to this proposal , 35 ,
2012-10-24 | Design | Omission | NEW ROUTE(O) | 4 | WASHINGTON | Delineators for guardrail were omitted from the contract. | The Section Office added these for a safety enhancement , which is currently standard design practice.
2012-10-24 | Structures | Quantities | NEW ROUTE(O) | 4 | WASHINGTON | On the structure plans , the notes for piling indicated that the concrete backfill in the rock sockets were to be paid as incidental to the socket on one hole but not the other. | Due to the inconsistency in the notes , the concrete was paid on all holes and an insufficient quantity was included in the contract.
2012-10-24 | Structures | Masonry Coating | RECONSTRUCTION(O) | 4 | MARION | It was determined by field inspection that the existing pier cap on the I-75 Northbound bridge over Donaldson Road was deteriorating and exposing rebar. | Masonry coating was necessary to repair the existing pier cap.
2012-10-24 | Design | Omission | RECONSTRUCTION(O) | 4 | MARION | Type VI D-1 Crash Cushion was setup on the plans , but there was no bid item for the Class £AA¥ concrete needed for the concrete pad as shown by the standard drawing RBE-060-10. | A price for the more recent NCHRP 350 compliant Crash Cushion Type VI D-1 was established.
2012-10-24 | Drainage | Ditches | RECONSTRUCTION(O) | 4 | MARION | The paved ditches along the Collector-Distributor were severely undermined at numerous locations. | The undermined paved ditches were replaced with Class III Channel Lining.
2012-10-24 | Design | Entrance | NEW ROUTE(O) | 4 | WASHINGTON | The entrances on the project were designed to be paved with like material to match existing. Several property owners complained that their driveways were not set up to be paved as part of the project. | The entrances were all paved with asphalt , which is standard District 4 design practice currently.
2012-10-24 | Traffic | Lighting | RECONSTRUCTION(O) | 4 | MARION | The plan sheets did not include all the necessary items for the proposed lighting installation on the I-75 median wall from Sta. 26+140 to Sta. 28+640. | PVC raceway pipe was added in order to install the lighting along the I-75 median wall.
2012-10-24 | Utilities | Existing Utilities | NEW ROUTE(O) | 4 | WASHINGTON | An existing utility was found to be in conflict with a proposed diversion. The utility relocation plans are typically developed at an early stage in project development sometimes prior to detailing final design features , such as diversions. This parti | The diversion was shifted slightly to avoid the conflict and potential delay. A final reviews needs to be performed on all utility plans to ensure relocations are adequate for all proposed design features , including temporary diversions. Cross Section
2012-10-24 | Design | Slopes | NEW ROUTE(O) | 4 | WASHINGTON | Several property owners complained about the steepness of the cut slopes in their front yard , specifically the 3:1 slopes. | District 4 PD & P recommends installing 4:1 or flatter slopes in front yards that will most likely be mowed by the adjoining property owner.
2012-10-24 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 4 | MARION | During Phase II construction , PDC video inspected the exiting pipe at Sta. 27+608 that drained from the I-75 median wall and Collector-Distributor wall to the west at a headwall. The inspection found the pipe was separating and deteriorating at several | A new system was installed to drain the Collector-Distributor wall and I-75 median wall to the east , while the existing pipe was safeloaded.
2012-10-24 | Pavement | Repair | RECONSTRUCTION(O) | 4 | MARION | The original contract called for Asphalt patching of the existing pavement on I-75/Collector-Distributor , but the Contractor had concerns about the cost and availability of Asphalt Surface Class I-20/30 PG64-22. | Asphalt patching was replaced with Mass Concrete Special (48 hour). Concrete patching was accepted as an alternative with a reduced price and greater availability. The 48-hour mass concrete was used to achieve the strength required for traffic in a shor
2012-10-24 | Geotechnical | Soils | RECONSTRUCTION(O) | 4 | MARION | Approach slabs were proposed for the I-75 NB/SB lanes of the Donaldson Bridge. The superstructure had to be removed in phases and upon removal of the approaches , silty sand was discovered. The plans called for the use of Structure Granular Backfill fo | From past experience with phase construction , it was felt that flowable fill would be the best backfill material for this type of work.
2012-10-24 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 4 | MARION | The Contractor requested and received approval from FHWA and the Department to alter the project phasing. | The change affected several ramps and ramp closures and expedited the project completion. The traffic phasing changed from six phases to four phases. A temporary ramp was constructed by the Contractor in order to achieve the modified traffic control. T
2012-10-24 | Traffic | Signs | RECONSTRUCTION(O) | 4 | MARION | Originally , the existing overhead signs on I-75 Southbound and the Collector-Distributor were to remain in place , but upon field inspection the signs were found to be worn and damaged prior to construction. | Eighty-four square meters of SBM Aluminum Panel Signs were added to replace existing overhead signs.
2012-10-24 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 4 | MARION | The type of fencing on the project was 1.8M Chain Link Fence , but bid items were setup for woven wire fence. | The Contractor submitted a price for the chain link fence that was installed.
2012-10-24 | Drainage | Edge Drains | RECONSTRUCTION(O) | 4 | MARION | It was decided to keep the existing subgrade drainage boxes for edge drains. | The boxes had to be cored in order to accommodate the proposed drainage pipe. Twenty core holes for 100mm pipe and forty core holes for 150mm pipe were performed.
2012-10-24 | Design | Quantities | NEW ROUTE(O) | 4 | WASHINGTON | The longitudinal edge key along existing pavement was omitted from the plans. | The longitudinal edge key item was added to reduce the potential for pavement failures especially in the driving lane. The edge key was utilized to remove the vertical face in the base layers in an attempt to provide a stronger connection to the existing
2012-10-24 | Drainage | Omission | RECONSTRUCTION(O) | 4 | MARION | The plans did not properly address how to connect existing and new piping to provide drainage along the Collector-Distributor Road from Left Sta. 27+800 to Sta. 28+560 and Donaldson Road from Right Sta. 0+759 to Sta. 0+860. The cross-drains from the main | Six Manholes Type £C¥ and Storm Sewer Pipe (375mm , 450mm , and 600mm) were necessary to connect existing and new piping from the mainline median and Showcase Cinema to the existing ditch line. Also , a new piping system was installed to ensure proper
2012-10-24 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 4 | MARION | The shoulders being utilized in the traffic phasing , contained drop box inlets. Additionally , the pavement shoulders along the Collector-Distributor wall and Ramp 2 wall were to remain in place. However , prior to construction the shoulders were da | The drop box inlet grates needed to be bolted down and an epoxy resin was utilized to repair the damaged areas.
2012-10-24 | Design | Evaluations | RECONSTRUCTION(O) | 4 | MARION | The plans showed an existing Crash Cushion was to be left in place , but upon a field inspection the existing crash cushion was determined to be unsafe , damaged , and unusable. | A new Crash Cushion was added via Change Order and installed in place of the damaged one.
2012-10-24 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 4 | MARION | There was insufficient erosion control provided to protect all the areas disturbed during construction. Specifically , the plan quantity was not enough to support the work in Kenton County. | Additional seeding and protection was established by Change Order.
2012-10-24 | Structures | Quantities | RECONSTRUCTION(O) | 4 | MARION | The plan quantity for texture was not enough to support all the concrete barrier structures throughout the project. | Additional texture was added for the concrete barrier structures throughout the project.
2012-10-24 | Design | Special Note | RECONSTRUCTION(O) | 4 | MARION | Due to local conditions , it was necessary to implement higher standards of quality control and quality assurance specifications for concrete acceptance in Boone and Kenton Counties. | It was necessary to utilize a special note of quality control and quality assurance specifications for concrete acceptance. The special note superseded the 1998 Standard Specifications for PCC pavement. The Contractor had the option of using #57 river g
2012-10-24 | Drainage | Existing Pipe | NEW ROUTE(O) | 4 | WASHINGTON | On Sheet R21 , the plans included replacing a 5' x 3' RCBC with a double 42 cross drain along with improving the outlet ditch downstream. The plans did not address an undersized 30 entrance pipe on the adjoiner directly downstream of the improvement. D | The Section Office agreed to improve the capacity of the entrance pipe by adding another 30 pipe and stabilized the entrance.
2012-10-24 | Design | Quantities | RECONSTRUCTION(O) | 4 | MARION | The plan quantity for pavement striping in Boone County exceeded what was needed while the plan quantity for Kenton County was insufficient. Overall , the total plan quantity was not enough to support all the required striping. Additionally , during r | Additional pavement striping throughout the project was provided through Change Order.
2012-10-24 | Design | Grade | NEW ROUTE(O) | 4 | WASHINGTON | The pavement tie-in at the bridge over Beech Fork became an issue. The existing approach slab did not have the same grade as the design profile. | The Section Office decided to use milling to allow for a pavement key-in that fit better. In these situations , designers should consider reconstructing the existing approach slab to match the proposed grade.
2012-10-24 | Drainage | Bridge Ends | RECONSTRUCTION(O) | 4 | MARION | There were concerns regarding potential drainage problems behind the proposed barrier wall under the I-75 bridge on Donaldson Road from Sta. 0+390 to Sta. 0+460 Lt. where the sidewalk was to be located. | A 6-inch curb was installed in lieu of the barrier wall on Donaldson Road under the I-75 bridge. The clearance from the curb to the bridge piers was field measured and determined to satisfy the roadside development guidelines.
2012-10-24 | Traffic | Lighting | RECONSTRUCTION(O) | 4 | MARION | The plans did not address the replacement of roadway lighting on the Turfway to I-75 NB ramp from Sta. 0+909 to Sta. 1+225 Rt. | The plans did not address the on the Turfway to I-75 NB ramp from Sta. 0+909 to Sta. 1+225 Rt. Numerous items needed to replace the roadway lighting had to be added through Change Order.
2012-10-24 | Maintenance of Traffic | Changes | RECONSTRUCTION(O) | 4 | MARION | Due to changes made in the traffic phasing , additional barrier wall was needed to provide safety for the workers and the public. | Additional quantities for relocating temporary concrete barrier wall were added to relocate temporary concrete barrier wall throughout the project.
2012-10-24 | Maintenance of Traffic | Quantities | RECONSTRUCTION(O) | 4 | MARION | There were insufficient Lane Closure quantities to allow the Contractor to safely perform work under traffic. | Additional Lane Closures had to be setup using Change Order to allow the Contractor to close lanes and properly perform work under traffic.
2012-10-24 | Geotechnical | Communication | NEW ROUTE(O) | 4 | WASHINGTON | Geotechnical note #5 on Sheet 84 directed the contractor to undercut rock cuts by 1 foot and to refill with compacted soil. The note also indicated that the payment for this operation be incidental to Roadway Excavation. A claim was brought by the contr | The Division of Construction in Central Office directed that this work be compensated by measurement of material removed and replaced which equaled 5 , 591 cubic yards of roadway excavation.
2012-10-24 | Design | Grade | NEW ROUTE(O) | 4 | WASHINGTON | The proposed design included some short cut to fill sections which tends to involve undercutting issues. | These areas were undercut as needed. Designer should consider profile adjustments to avoid thin cut/fill areas. If thin fill sections cannot be avoided , then profile benching should be used to account for subgrade stability issues.
2012-10-24 | Drainage | Pipes | RECONSTRUCTION(O) | 4 | MARION | The Contractor made a value engineering proposal involving a 750mm culvert pipe that was originally designed to be installed by boring under Donaldson Road. | The Contractor's value engineering proposed using an open cut , backfilling with flowable fill , and pavement restoration on Donaldson Road. This proposal eliminated the need to tunnel under Donaldson Road , which saved the Department $64 , 351.98.
2012-10-24 | Drainage | Cross Drains | NEW ROUTE(O) | 4 | WASHINGTON | A constructability issue concerning drainage pipes was encountered. The new pipe was not in line with the existing pipe which led to some erosion issues during the phase part width construction. | Designers need to be mindful of the alignment of proposed cross drains with the existing drainage pipes.
2012-10-24 | Traffic | Pedestrian Signals | RECONSTRUCTION(O) | 4 | MARION | The plans called for the Pedestrian Detector to be mounted to a strain pole adjacent to the sidewalk near the crossing area on Donaldson Road. After a field inspection and further evaluation , it was determined that the strain pole was too far from the | A pedestal was needed to properly install the pedestrian detector.
2012-10-24 | Design | Shoulders | RECONSTRUCTION(O) | 4 | MARION | The quantity of crushed stone base needed to shoulder the entire project was field calculated to be much greater than the plan quantity. | An additional 20 , 000 metric tons of CSB were needed.
2012-10-24 | Pavement | Approaches | RECONSTRUCTION(O) | 4 | MARION | Additional items not included in the plans were needed to tie the existing pavement to the proposed pavement at Donaldson Drive from Sta. 0+140 to Sta. 0+262 Rt. | Per Standard Drawing RPS-010-08 and 1998 Standard Specifications Section 512.01 , hook bolts with expansion anchors were added and utilized for the PCC pavement widening.
2012-10-24 | Drainage | Ditches | RECONSTRUCTION(O) | 4 | MARION | Traffic had to be moved to the mainline shoulder and proper drainage was critical. The existing ditches were clogged with silt debris , which caused severe ponding at the headwalls. | The existing ditch had to be cleaned and lowered on the I-75 NB/SB shoulders.
2012-10-24 | Structures | Approaches | RECONSTRUCTION(O) | 4 | MARION | Additional items not included in the plans were needed to transfer the load from existing pavement to the approach slab on the I-75 NB mainline and shoulders at Sta. 27+538 and Sta. 27+602 Rt. | Smooth dowel bars (1-3/4¥) were added to transfer the load from the pavement to the approach slab. The dowel bars were inserted on 12 inch center spacing in order to prevent differential settlement at the bride ends.
2012-10-24 | Pavement | Repair | RECONSTRUCTION(O) | 4 | MARION | The ramps located at I-75/71 SB to I-275 EB (Ramp D/E) and I-275 WB to I-75/71 NB (Ramp F) were severely cracked , settled , and shifted at numerous locations due to subgrade failure and pavement age. | Numerous items had to be added via Change Order to reconstruct the ramps.
2012-10-24 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 4 | MARION | Due to phasing , the shoulders were utilized for traffic. However , the elevations of existing Drop Boxes presented unsafe drop-offs within the temporary lanes on I-75 at Sta. 26+158 and on Ramp 2a at Sta. 0+659.6 and Sta. 0+719.6 Rt. | It was necessary to adjust the elevations of the Drop Boxes to eliminate drop-offs within the temporary lanes.
2012-10-24 | Traffic | Markings | RECONSTRUCTION(O) | 4 | MARION | Additional pavement markings at the Donaldson Road turning lanes were not addressed on the plans , but were deemed necessary upon field inspection. | Preformed thermo , £ONLY¥ pavement markings had to be installed at the Donaldson Road turning lanes.
2012-10-24 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 4 | MARION | The traffic control plan had an excessive number of traffic switches within phases , did not provide an adequate work zone area , and required a construction joint in the center of the southbound mainline. | An approved value engineering proposal for a revised traffic control plan that reduced the number of traffic switches within saved the Cabinet $100 , 817.50. Also , the quality of the final product was greatly improved by increasing the work zone area w
2012-10-24 | Structures | Erosion Control | RECONSTRUCTION(O) | 4 | MARION | The existing 150mm reinforced concrete slope wall was to remain in place and be extended on the northbound and southbound sides. However , it was determined that the slope wall would become damaged upon removal of the existing superstructure. Additiona | Replacement of the existing concrete slope wall was needed so the Contractor submitted a price for crushed aggregate slope protection and removed the concrete slope wall.
2012-10-24 | Design | Access | RECONSTRUCTION(O) | 4 | MARION | The plans did not address any sidewalk east of Sta. Lt. 0+895.64 , which was needed in order to connect the new sidewalk to the existing sidewalk. | Sidewalk excavation and grading was added to install sidewalk along Donaldson Road from Sta.0+896.64 to Lt. Sta. 0+954.
2012-10-24 | Drainage | Omission | NEW ROUTE(O) | 4 | WASHINGTON | Due to the geometric features near the beginning of the project , the proposed design caused subgrade drainage to be directed into the tie-in with existing pavement. | The Section Office used #2 stone to construct the subgrade adversely in this area to drain away from existing pavement.
2012-10-24 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 4 | MARION | Additional items were needed to tie the proposed pavement into the existing pavement as shown on the typical sections. An existing section of I-75 NB from Sta. Rt. 25+722 to Rt. 26+588 was widened to create a through lane for Turfway on the ramp entering | A longitudinal keyway was added through Change Order to tie the proposed pavement into the existing pavement because the original contract did not address the longitudinal keyway.
2012-10-24 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 4 | MARION | The temporary widening of I-75 and the disturbance of existing slopes created silt and debris runoff. | Temporary silt fence was added for the temporary erosion control during construction along I-75.
2012-10-24 | Pavement | Design | RECONSTRUCTION(O) | 4 | MARION | Originally , the subgrade design included wrapping filter fabric around the rock sub-base (top , bottom , and sides) which would have allowed a separation between the drainage blanket and the rock sub-base. | The design was revised to include installation of fabric under the sub-base and sides only , which reduced the quantity of fabric by 40%.
2012-10-24 | Drainage | Omission | RECONSTRUCTION(O) | 4 | MARION | The original plans did not address underdrain installation at several locations , including the outside shoulder of I-75 SB from Sta. 26+140 to Sta. 28+960 Lt. , I-75 NB to I-275 EB , I-275 WB ramps , and I-75 NB outside shoulder from Sta. 27+747 to S | Additional perforated pipe had to be set up on the project. Fifteen-hundred meters of 100mm perforated pipe along with 100mm Non-Perforated Pipe and 150mm Non-Perforated Pipe were necessary to construct an underdrain system along the I-75 ramps and Donal
2012-10-24 | Traffic | Signals | RECONSTRUCTION(O) | 4 | MARION | The existing signals on Donaldson Road were utilized per the plans. However the existing signals were not equipped to meet current standards. | Arrow lenses needed for the existing signals on Donaldson Road were added by Change Order.
2012-10-24 | Drainage | Omission | RECONSTRUCTION(O) | 4 | MARION | The original plans did not address the drainage from Sta. 27+182 to Sta. 28+955 along the median wall of I-75 in Kenton County. | The design consultant recommended adding extra median boxes along with making changes to other median boxes to ensure proper drainage with regards to the spread calculations. Eight Concrete Median Barrier Box Inlet Type 350 B2 along with Concrete Median
2012-10-24 | Drainage | Omission | RECONSTRUCTION(O) | 4 | MARION | The flow of water had increased substantially in the ditches after discovering several headwalls that were draining the mainline median and the Showcase Cinema. | Additional Class III Channel lining had to be set up to control the runoff drainage at the headwalls and the ditches.
2012-10-24 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 4 | WASHINGTON | The MOT plan called for utilizing DGA for any temporary edge drop-off safety wedges needed. | #2 stone is preferred for edge drop-off safety wedges especially if it is already being used as subgrade stabilization (i.e. tie-ins under traffic). #2 stone is much cleaner than DGA/CSB and can be cut away easier and subsequently utilized in shoulder co
2012-10-24 | Drainage | Omission | RECONSTRUCTION(O) | 4 | MARION | Due to the widening , the existing brick CBI could not be used to control drainage on the approach to I-75 northbound bridge over Donaldson Road at Sta. 27+535. | A new Curb Box Inlet Type B was added via Change Order.
2012-10-24 | Right-of-Way | CAP | RECONSTRUCTION(O) | 4 | MARION | Additional work was required to provide a drainage system for the Four Seasons Apartment complex located north of Donaldson Road at Sta. Lt. 0+860 to Lt. 0+620 as required by the memo of understanding for Parcel Number 15. Due to excessive water accumula | Numerous items needed to excavate and construct a proper drainage system for the apartment complex were added by Change Order.
2012-10-24 | Structures | Patching | RECONSTRUCTION(O) | 4 | MARION | Several areas on the existing abutments and pier for the northbound and southbound bridge over Donaldson Road were cracked with exposed rebar. | Concrete patching had to be set up to patch several areas on the substructure.
2012-10-23 | Design | Guardrail | MINOR WIDENING(O) | 4 | HART | The original plans provided for guardrail along the North side of KY 313 to wrap around the radius at Camelot Drive. The guardrail was shortened during construction because of field conditions encountered. The Type 2A end treatment that was indicated on | A Type 1 end treatment was added to better fit site conditions and was installed along the mainline at approximate station 246+75 Rt in accordance with Standard Drawing RBI-004-03.
2012-10-23 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 4 | MEADE | Several areas of soft subgrade were identified during the early part of construction. The plans directed these areas to be treated with shot rock from the job site; however , the contractor was concerned about the possible lack of suitable rock on the p | The Section Office decided to allow the contractor to treat the undercut areas with geotextile fabric Type 4 and 2' of crushed aggregate size 3 stone.
2012-10-23 | Design | Guardrail | MINOR WIDENING(O) | 4 | HART | The original plans provided for guardrail along the North side of KY 313 to wrap around the radius at Camelot Drive. The guardrail was shortened during construction because of field conditions encountered. The Type 2A end treatment that was indicated on | A Type 1 end treatment was added to better fit site conditions and was installed along the mainline at approximate station 246+75 Rt in accordance with Standard Drawing RBI-004-03.
2012-10-23 | Geotechnical | Unsuitable Material | MINOR WIDENING(O) | 4 | HART | The area by Camelot where the precast culvert was installed under KY 313 at Station 245 was very swampy. There are concerns about potential future issues with the culvert because during inspection water was seeping from the joint. There is a pond in thi | Some of the swampy material was undercut prior to installation of the culvert. It's uncertain if raising the bottom of the culvert or lowering the pond during construction would have helped. Using a three sided structure might have been a better option.
2012-10-23 | Geotechnical | Slides | MINOR WIDENING(O) | 4 | HART | The project had to sit through the winter. During the week of November 28th 2011 , Meade County received approximately 6 of rain. A slide occurred on a fill section with a 2:1 slope between Stations 282+00 and 283+00 Rt. | The contractor had to remove the saturated material , place geotextile fabric Type IV on the slope , and place crushed stone #2 on the slope at the original 2:1 slope. The saturated material was placed in an area where it could dry and then was wasted
2012-10-23 | Geotechnical | Soils | MINOR WIDENING(O) | 4 | HART | Extensive drilling was performed as per the geotechnical report. Eight hundred and seventy-nine bore holes were sampled but drilling was prevented in one area by a property owner. During construction , silty , sandy soils were encountered in this area | A change was made from lime stabilization to cement stabilization to prevent rutting and pumping due to the sandy , silty material. Seeding and protection was also added to stabilize the sandy slopes in this area.
2012-10-23 | Construction | Rumble Strips | NEW ROUTE(O) | 4 | MEADE | The project called for both warm and hot mix asphalt. The contract required a test strip of warm mix asphalt to be placed. However , the test strip was not allowed to be performed on the mainline so it was tested on the shoulder instead , and the cont | A change order was established to install milled rumble strips along the warm mix test strip on the shoulder.
2012-10-23 | Utilities | Relocation | RELOCATION(O) | 4 | MEADE | During construction , relocated utility issues became apparent near the KY 528 intersection. The temporary diversion was not accounted for when the utilities were relocated in this area. | Utilities were relocated in order to construct the necessary diversion. A final review needs to be performed on Utility Relocation Plans to coordinate with all the proposed design features including temporary diversions. Plans that are supplied to utili
2012-10-23 | Traffic | Markings | RELOCATION(O) | 4 | MEADE | The striping plans for this project indicated striping a left turn lane on the approach roads onto mainline. There were some accident issues on other projects with too many lanes on the approach roads. | The Section Office decided to stripe the left turn lanes as solid dead areas.
2012-10-23 | Design | Intersection | NEW ROUTE(O) | 4 | MEADE | Intersections with approach roads in cut sections tend to create sight distance issues if the cut slopes are not laid back far enough. | Moving stop bars closer to mainline can help improve sight distance after the fact. However , designers should proactively consider these situations and flatten the cut slopes at intersections to improve sight for stop conditions.
2012-10-23 | Geotechnical | Elevations | RELOCATION(O) | 4 | MEADE | The solid rock elevation encountered in the field was lower than the planned elevations. | The footing was lowered and the abutment wall was adjusted.
2012-10-23 | Design | Omission | RELOCATION(O) | 4 | MEADE | Delineators for temporary barrier walls were omitted from the contract. This issue was a result of interpretation of the specification manual concerning what is included in the Lump Sum item Maintenance of Traffic. | Bid item was established per change order.
2012-10-23 | Traffic | Markings | NEW ROUTE(O) | 4 | MEADE | Six-inch striping was included on the bid documents; however , the project only required 4-inch striping. | The bid items were corrected via change order.
2012-10-23 | Design | Shoulders | MINOR WIDENING(O) | 4 | HART | The Practical Solutions approach was applied to the ten foot paved shoulders on this project , changing them to six foot paved shoulders in combination with four foot earth shoulders. The shoulders on this section of the project differed from those on t | Eight foot paved shoulders would still have been insufficient to safely accommodate vehicles especially large trucks , and as such the shoulders should have either been constructed as two foot or ten foot. Keeping in the spirit of practical solutions ,
2012-10-23 | Utilities | Existing Utilities | NEW ROUTE(O) | 4 | MEADE | A gas line was in conflict with the proposed cut slope at the bottom of the hill near KY 933. The gas line was not shown on the plans. | The Section Office coordinated with District Project Development forces to locate the gas line and negotiated a relocation with the Utility Company.
2012-10-23 | Construction | Revisions | RELOCATION(O) | 4 | MEADE | The original design included a T-intersection of Old US 150 and the access road to St. Catherine College. | Construction Revision #1 involved redesigning the T-intersection into a roundabout design.
2012-10-23 | Structures | RCBC | MINOR WIDENING(O) | 4 | HART | Central Office Maintenance does not necessarily believe that contractors should be allowed to use precast box culverts when plans indicate using a box culvert because there is insufficient information regarding their lifespan. | Precast box culverts can serve a purpose , primarily reducing maintenance of traffic impacts on existing roadways. On the other hand , requiring construction of cast in place box culverts on new routes might better reflect the long term interests of th
2012-10-23 | Design | Adjacent Projects | MINOR WIDENING(O) | 4 | HART | Lime stabilization and asphalt curing seal were setup to be applied only to the mainline and not on the connector road. However , the connector road will eventually become part of the mainline after sections 2 and 3 are tied together. | These items were added for the KY 313 connector road at Sta. 384+00 to 395+20.4.
2012-10-23 | Traffic | Markings | RELOCATION(O) | 4 | MEADE | Striping paint does not adhere to concrete surfaces well unless a water blasting operation is performed first to remove the curing compound. | A special note should be included on projects involving concrete surfaces that require striping.
2012-10-23 | Design | Radius | MINOR WIDENING(O) | 4 | HART | There is a turning radius issue where KY 313 ties into KY 144. This intersection is near a school so buses and trailers might have some issues navigating this intersection. | Any issues with the turning radius would have been avoided with the wider shoulders as were originally designed.
2012-10-23 | Traffic | Raised Pavement Markers | RELOCATION(O) | 4 | MEADE | The plans included Type V Pavement Markers. | The Section Office eliminated this item of work because of the lack of an existing maintenance contract and the desire to not expose the concrete unnecessarily.
2012-10-23 | Pavement | Coordination | MINOR WIDENING(O) | 4 | HART | The typical section in the plans called for a Class 2 PG 64-22 0.38B mix for the final surface. However the quantity was incorrectly established in the contract as a Class 2 PG 64-22 0.38D mix , which was to be utilized on the shoulders. Further , aft | The District requested changing the Asphalt Surface to a Class 3 PG 64-22 0.38B mix. When possible , the different sections of a route should have the same pavement design because there can be issues with tying into different mixes on adjoining sections
2012-10-23 | Drainage | Culvert | NEW ROUTE(O) | 4 | MEADE | As a result of Practical Solutions , a RCBC was redesigned as an 84 culvert pipe during project development. Prior to completion of the project , a crack had developed in one end of the 84 pipe. | The supplier agreed that it was a defect and patched it to the satisfaction of the Section Engineer. The Division of Maintenance does not approve of this design practice. On major corridor projects , designers should consider the long term maintenance
2012-10-18 | Construction | Contracts | RELOCATION(O) | 8 | CLINTON | With Design/Build contracts if a UST is encountered , the cost falls solely on the contractor. Unless significant upfront investigation is performed , which still might not uncover everything , this places unfair risk upon the contractor. | Payment for dealing with UST's should be negotiated after the project or via change order.
2012-10-18 | Utilities | Omission | RELOCATION(O) | 8 | CLINTON | The plans only showed that waterlines needed to be a minimum depth of 30 inches. A necessary note on the plans specifying that extra depth cuts would be needed in certain areas to locate waterlines beneath ditch lines , structures , and creek crossings | A change order was approved to pay for the extra work associated with the extra depth cuts needed for the waterlines.
2012-10-18 | Geotechnical | Quantities | BRIDGE REPLACEMENT(P) | 8 | CLINTON | The granular embankment that was established on the contract was intended to be used for steep slope stabilization at a specific area , based on geotech recommendations due to grade/slope revisions late in the design phase. There was insufficient quanti | Additional quantity of granular embankment was established via change order. Using the term granular embankment to describe the material needed for slope stabilization and for sinkhole treatment interchangeably left the Department in a tough negotiating
2012-10-18 | Design | Evaluations | RELOCATION(O) | 8 | CLINTON | Originally the project was set up with #2's or #3's beneath the pavement. | The designer presented a value added proposal that was accepted. Due to the abundance of good rock on the project , a two foot rock roadbed was constructed below the pavement , which resulted in a savings for the Cabinet.
2012-10-18 | Geotechnical | Slides | RELOCATION(O) | 8 | CLINTON | During construction , there were two slides on KY 61 due to torrential rainfall occurring just after cuts had been made and before sufficient ground cover was established. Another contributing factor was the presence of laminated limestone rock , which | Any dirt placed on the rock quickly became saturated and would wash away almost immediately. The contractor had to remove some material and add rock to provide extra weight to prevent future slides.
2012-10-18 | Right-of-Way | Coordination | RELOCATION(O) | 8 | CLINTON | There were over one hundred parcels on this project which is a lot to handle through the design/build process. | The design consultant held a right of way conference call or meeting every single week. In order to help develop plans on a weekly basis , they displayed the entire plans on a large map so the project could be seen contiguously and they would color code
2012-10-18 | Utilities | Delays | BRIDGE REPLACEMENT(P) | 8 | CLINTON | During the initial construction phase of the project , several utilities remained in conflict with the planned improvements. Impact notes were included in the contract; however , the Utility Companies did not meet the dates established. | The project delivery team was forced to allow construction phasing and MOT changes which allowed reasonable progress for the contractor.
2012-10-18 | Geotechnical | Sinkhole | BRIDGE REPLACEMENT(P) | 8 | CLINTON | A large sinkhole was encountered in a rock cut at Station 428+50 right of centerline at subgrade elevation. | The sinkhole was cleaned out to a depth of roughly 18-20' below solid rock. It was additionally treated with fabric and #23 stone aggregate and capped with a 12 reinforced concrete cap per Condition 5B of the sepia drawing Treatment of Open Sinkholes.
2012-10-18 | Structures | Phasing | RELOCATION(O) | 8 | CLINTON | There were maintenance of traffic concerns regarding the construction of the box culverts on the project , which involved considerable part-width construction. | The subcontractor's request to use precast box culverts for four of the five culverts was accepted. However , it is still unclear whether this decision will result in future maintenance impacts due to the joints.
2012-10-18 | Erosion Control Plan | Omission | RELOCATION(O) | 8 | CLINTON | There werenÖt any items in the contract for the silt checks that were needed for utility work near creek crossings , which could have created issues with division of water. | Silt checks for the utility companies to install near creek crossings were added via change order.
2012-10-18 | Construction | Inspection | BRIDGE REPLACEMENT(P) | 8 | CLINTON | Project Delivery requests that typical sections include the designers intentions for approach roads to be tested as option A or option B. KY 1590 was inspected using option B; however , it could have been performed using option A. | This could be accomplished on the typical sections , but coordination efforts would be needed at the Final Joint Inspection during project development to get project delivery's input.
2012-10-18 | Drainage | Retention Basin | BRIDGE REPLACEMENT(P) | 8 | CLINTON | Drainage basins were designed to address increased runoff potential. These were located in sump areas with a natural sinkhole drain. After construction , several of these basins do not drain very well. One basin holds water all the time. | The basins are big enough to store the water that is draining to them without flooding adjacent properties. An entrance pipe was placed in one area to provide an overflow structure in case of high water. Dry wells have been discussed as an option , but
2012-10-18 | Construction | Contracts | RELOCATION(O) | 8 | CLINTON | The original contract included QC/QA on the culverts , which four of five wound up being precast. | The QC/QA for the precast culverts were eliminated and the Cabinet received a credit on the QC price from the contractor.
2012-10-18 | Design | Quantities | RELOCATION(O) | 8 | CLINTON | The original scope of the project called for applying the fuel and asphalt adjustments to the plan quantities. However , it was decided to apply the adjustments to the actual quantities produced by the contractor for constructing the job. There could b | Cabinet personnel had to go back and check with the plant to determine the actual amount of material used in the field , because even though District personnel collected tickets , they only pay plan quantities. This is an issue that needs to be discuss
2012-10-18 | Construction | Permits | RELOCATION(O) | 8 | CLINTON | Due to this being a Design/Build project , necessary permits had not been obtained when the project began. | The design consultant met with the U.S. Army Corps of Engineers upfront. Instead of just developing the permit and submitting it , they met with the USACE several times and partnered with them so that the Corps was involved with the generation of permit
2012-10-18 | Utilities | New Utilities | RELOCATION(O) | 8 | CLINTON | There were concerns about utilities delaying the project. | The design consultant requested and was granted permission to take on the design of several waterlines as part of their contract. Additionally , construction of the waterline was opened up for bid which allowed the contractor to dictate the pace of the
2012-10-18 | Design | Plans | RELOCATION(O) | 8 | CLINTON | The Design/Build process is not a good fit when the project is starting from scratch with no design at all. | When using Design/Build the Cabinet benefits from having phase 1 design complete because it decreases the need for in lieu fees which can drive up the cost. It also gives the Cabinet more control over the alignment , because the contractor has to follow
2012-10-18 | Utilities | New Utilities | BRIDGE REPLACEMENT(P) | 8 | CLINTON | Along the widening/reconstruction of Key 1590 , several relocated utility poles were in conflict with the planned construction , and a gas line was in conflict with the proposed temporary diversion. The diversion was necessary for the intended part wid | The road was closed during construction in order to eliminate the need for a diversion , and the utility poles were left in place with cut slopes being partially constructed around them (and completed later after poles were reset).
2012-10-18 | Utilities | Relocation | RELOCATION(O) | 8 | CLINTON | A waterline could not be installed per the plans due to a slope failure on one side of KY 61. | The contractor had to relay the waterline on the other side of the road.
2012-10-18 | Utilities | Quantities | RELOCATION(O) | 8 | CLINTON | There were some service line tie-in issues due to houses and structures being relocated and waterlines being rerouted. There were also new meters that needed to be added and some that needed to be moved , but this wasn't addressed in the plans. | Additional quantities were added via change order.
2012-10-18 | Utilities | Existing Utilities | RELOCATION(O) | 8 | CLINTON | After beginning construction of the roadway template on section 90a it was discovered that an existing waterline was located in the ditch line and lacked sufficient cover. Prior to construction the location and depth of the waterline was unknown. | The contractor had to relay 300 ft. at a lower depth in order to provide sufficient cover.
2012-10-18 | Right-of-Way | Coordination | RELOCATION(O) | 8 | CLINTON | Due to this being a Design/Build project , right of way had not been acquired when the project began and the plans had to be developed along the way. | The Design/Build team , headed by the contractor , had to prioritize right of way acquisition in order to obtain the right of way needed to begin the project. Additional right of way needed for subsequent phases was later acquired simultaneously during
2012-10-18 | Utilities | New Utilities | BRIDGE REPLACEMENT(P) | 8 | CLINTON | Several utilities were relocated in the detention basin adjacent to the KY 1590 intersection. The utility companies expressed concerns that water stands in the detention basins , leaving their utility lines inaccessible. | The city has requested that the Department pay for their lines to be moved out of the ponding area , but the Department has denied their request. Utility companies need to be aware of design features when performing relocations and potential ponding in
2012-10-18 | Construction | Revisions | RELOCATION(O) | 8 | CLINTON | The original contract and scope of services included only milling and asphalt overlay through the Marrowbone section of the KY 90 Project (~MP 4.0 - MP 4.961). However , the existing concrete curb , gutter , and sidewalk in this area were in poor cond | The contractor presented a Value Added proposal for removal and replacement of these items. The proposal was accepted and a change order revised the contract to include these enhancements , which should minimize future maintenance costs through this are
2012-10-18 | Drainage | Coordination | RELOCATION(O) | 8 | CLINTON | There were major potential maintenance of traffic issues involving construction of drainage structures at two locations. | Pipe liners were used to minimize the maintenance of traffic impacts at these locations.
2012-10-18 | Construction | Contracts | RELOCATION(O) | 8 | CLINTON | Since this was Design/Build the structure quantities could not be set up in the plans , bud had to come from the structures subcontractor. As a result , the structures were set up as lump sum which prevented partial progress payments and made it diffic | A change order was approved to change the original bridge bid from lump sum to a traditional quantity breakdown for the two bridges on KY 61. This breakdown allowed for more efficient partial pay , materials submittals , and contract accounting.
2012-10-18 | Construction | Revisions | RELOCATION(O) | 8 | CLINTON | There was an item in the original bid document encouraging the contractor to submit bids for value added enhancements. A Value Added proposal to reconstruct and realign KY 90 in order to eliminate a substandard existing horizontal curve near KY 691 was s | The Value Added proposal was accepted , then removed , and later reinstated.
2012-10-18 | Construction | Revisions | BRIDGE REPLACEMENT(P) | 8 | CLINTON | During the project , local school officials requested a design change to better accommodate traffic using their new entrance which will probably be the primary entrance to the school. | A construction revision was drafted to accommodate the request. Turning lanes were added at Station 495+00. Mainline pavement was widened to accommodate 2 northbound lanes (one left and one right) and one left southbound turn lane.
2012-10-18 | Right-of-Way | Communication | BRIDGE REPLACEMENT(P) | 8 | CLINTON | During construction , Parcel 335 owner requested that the entrance be adjusted to accommodate access to an easement that served a parcel on the back side of his property. | The entrance was modified to address this access issue with a frontage road. The County agreed to take ownership of this frontage road after construction.
2012-10-18 | Geotechnical | Embankment Stabilization | BRIDGE REPLACEMENT(P) | 8 | CLINTON | Rock Roadbed was designed for a portion of the project; however , it appeared likely an insufficient quantity of suitable rock existed in cuts for all purposes as noted in plans & geotechnical notes (i.e. embankment stabilization , undercut refill , ro | Granular Embankment was established on the contract for other uses; however , the Section Office and Contractor negotiated a lower price for durable shot rock from a local quarry and established a new bid item Special Embankment - Rock.
2012-10-18 | Construction | Contracts | RELOCATION(O) | 8 | CLINTON | Working on a project like this , there can be a very broad range for in lieu fees and working with the USACE it is impossible to know what the final costs are going to be , which creates high estimates that drive up the cost of the project. | The Cabinet should find a way to make the in lieu fees separate from the bid because the state would get a lower bid if they weren't included. On Design/Build projects , the Cabinet would benefit from having phase 1 complete , because it would eliminat
2012-10-15 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | A 6 sewer main was relocated prior to construction; however , the line remained in conflict with the planned storm sewer improvements from Sta. 1036+45 to Sta. 1038+91 Rt. | The Department requested appropriate line item prices from the prime contractor to perform the necessary relocation and added five days to the contract time.
2012-10-15 | Utilities | Relocation | RECONSTRUCTION(O) | 8 | CUMBERLAND | A 6 sewer main was relocated prior to construction; however , the line remained in conflict with the planned storm sewer improvements from Sta. 1036+45 to Sta. 1038+91 Rt. | The Department requested appropriate line item prices from the prime contractor to perform the necessary relocation and added five days to the contract time.
2012-10-15 | Design | Entrance | RECONSTRUCTION(O) | 8 | CUMBERLAND | The road approach access at Dairy Queen involved a thin overlay of asphalt over the existing concrete pavement. | The section office decided that a thin asphalt overlay would not be prudent , therefore , the section of concrete pavement was removed entirely and an approach asphalt typical was placed.
2012-10-15 | Traffic | Signals | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The signal controller cabinet was supplied by the Department and installed by a subcontractor on this project. Upon installation , it was determined that the controller cabinet was faulty. | The section office coordinated swapping out the faulty equipment and compensated the contractor for the additional work necessary to replace and reinstall.
2012-10-15 | Design | Omission | RECONSTRUCTION(O) | 8 | CUMBERLAND | Prior to letting the project , an empty parcel had been developed into a restaurant. The planned fill slope in this area impacted the existing parking lot. | The section office negotiated a price with the contractor to install a modified curb (retaining wall) to support the fill slope and leave the parking stalls unaffected. Handrail was added to the modified curb for safety reasons. Design worked closely wi
2012-10-15 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Several utility pole guy wires were determined to be in conflict with the construction of the cut slope at the intersection of US 31W and Alan Avenue. | The District coordinated with the Utility Company to brace the pole until the slope construction was completed. The guy wires were relocated on the new slope.
2012-10-15 | Utilities | Relocation | RECONSTRUCTION(O) | 8 | CUMBERLAND | Several utility pole guy wires were determined to be in conflict with the construction of the cut slope at the intersection of US 31W and Alan Avenue. | The District coordinated with the Utility Company to brace the pole until the slope construction was completed. The guy wires were relocated on the new slope.
2012-10-15 | Design | Omission | RELOCATION(O) | 8 | CUMBERLAND | Prior to letting the project , an empty parcel had been developed into a restaurant. The planned fill slope in this area impacted the existing parking lot. | The section office negotiated a price with the contractor to install a modified curb (retaining wall) to support the fill slope and leave the parking stalls unaffected. Handrail was added to the modified curb for safety reasons. Design worked closely wi
2012-10-15 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Several utility pole guy wires were determined to be in conflict with the construction of the cut slope at the intersection of US 31W and Alan Avenue. | The District coordinated with the Utility Company to brace the pole until the slope construction was completed. The guy wires were relocated on the new slope.
2012-10-15 | Design | Omission | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Prior to letting the project , an empty parcel had been developed into a restaurant. The planned fill slope in this area impacted the existing parking lot. | The section office negotiated a price with the contractor to install a modified curb (retaining wall) to support the fill slope and leave the parking stalls unaffected. Handrail was added to the modified curb for safety reasons. Design worked closely wi
2012-10-15 | Design | Omission | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Prior to letting the project , an empty parcel had been developed into a restaurant. The planned fill slope in this area impacted the existing parking lot. | The section office negotiated a price with the contractor to install a modified curb (retaining wall) to support the fill slope and leave the parking stalls unaffected. Handrail was added to the modified curb for safety reasons. Design worked closely wi
2012-10-15 | Design | Entrance | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The road approach access at Dairy Queen involved a thin overlay of asphalt over the existing concrete pavement. | The section office decided that a thin asphalt overlay would not be prudent , therefore , the section of concrete pavement was removed entirely and an approach asphalt typical was placed.
2012-10-15 | Design | Omission | RECONSTRUCTION(O) | 8 | CUMBERLAND | Prior to letting the project , an empty parcel had been developed into a restaurant. The planned fill slope in this area impacted the existing parking lot. | The section office negotiated a price with the contractor to install a modified curb (retaining wall) to support the fill slope and leave the parking stalls unaffected. Handrail was added to the modified curb for safety reasons. Design worked closely wi
2012-10-15 | Utilities | Relocation | RELOCATION(O) | 8 | CUMBERLAND | Several utility pole guy wires were determined to be in conflict with the construction of the cut slope at the intersection of US 31W and Alan Avenue. | The District coordinated with the Utility Company to brace the pole until the slope construction was completed. The guy wires were relocated on the new slope.
2012-10-15 | Utilities | Relocation | RECONSTRUCTION(O) | 8 | CUMBERLAND | Several utility pole guy wires were determined to be in conflict with the construction of the cut slope at the intersection of US 31W and Alan Avenue. | The District coordinated with the Utility Company to brace the pole until the slope construction was completed. The guy wires were relocated on the new slope.
2012-10-15 | Utilities | Relocation | RELOCATION(O) | 8 | CUMBERLAND | A 6 sewer main was relocated prior to construction; however , the line remained in conflict with the planned storm sewer improvements from Sta. 1036+45 to Sta. 1038+91 Rt. | The Department requested appropriate line item prices from the prime contractor to perform the necessary relocation and added five days to the contract time.
2012-10-15 | Design | Entrance | RECONSTRUCTION(O) | 8 | CUMBERLAND | The road approach access at Dairy Queen involved a thin overlay of asphalt over the existing concrete pavement. | The section office decided that a thin asphalt overlay would not be prudent , therefore , the section of concrete pavement was removed entirely and an approach asphalt typical was placed.
2012-10-15 | Utilities | Relocation | RECONSTRUCTION(O) | 8 | CUMBERLAND | A 6 sewer main was relocated prior to construction; however , the line remained in conflict with the planned storm sewer improvements from Sta. 1036+45 to Sta. 1038+91 Rt. | The Department requested appropriate line item prices from the prime contractor to perform the necessary relocation and added five days to the contract time.
2012-10-15 | Utilities | Relocation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | A 6 sewer main was relocated prior to construction; however , the line remained in conflict with the planned storm sewer improvements from Sta. 1036+45 to Sta. 1038+91 Rt. | The Department requested appropriate line item prices from the prime contractor to perform the necessary relocation and added five days to the contract time.
2012-10-15 | Design | Entrance | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The road approach access at Dairy Queen involved a thin overlay of asphalt over the existing concrete pavement. | The section office decided that a thin asphalt overlay would not be prudent , therefore , the section of concrete pavement was removed entirely and an approach asphalt typical was placed.
2012-10-15 | Design | Entrance | RELOCATION(O) | 8 | CUMBERLAND | The road approach access at Dairy Queen involved a thin overlay of asphalt over the existing concrete pavement. | The section office decided that a thin asphalt overlay would not be prudent , therefore , the section of concrete pavement was removed entirely and an approach asphalt typical was placed.
2012-10-15 | Drainage | Elevation | RECONSTRUCTION(O) | 8 | CUMBERLAND | The plans included installing a drainage box at the entrance into ACE Hardware from Gentry Street. The box was installed per plan elevation; however , the box was too high to adequately provide drainage of the surrounding pavement. | The contractor was paid to lower the box inlet and extend curb and gutter from mainline along Gentry Street to direct flow toward the box. The extended curb also served to encourage trucks to avoid cutting the radius and rutting the earthen island.
2012-10-15 | Drainage | Elevation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The plans included installing a drainage box at the entrance into ACE Hardware from Gentry Street. The box was installed per plan elevation; however , the box was too high to adequately provide drainage of the surrounding pavement. | The contractor was paid to lower the box inlet and extend curb and gutter from mainline along Gentry Street to direct flow toward the box. The extended curb also served to encourage trucks to avoid cutting the radius and rutting the earthen island.
2012-10-15 | Geotechnical | Sinkhole | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | A void under the existing pavement structure was located during this project near Sta. 1091+00. A small orifice had developed in the existing pavement along with a noticeable deflection of the surrounding pavement. | Traffic was diverted away from the site of the failure. The contractor excavated all loose material in the hole. The sinkhole was treated with fabric and granular backfill. The existing pavement was repaired to near original condition.
2012-10-15 | Geotechnical | Sinkhole | RECONSTRUCTION(O) | 8 | CUMBERLAND | A void under the existing pavement structure was located during this project near Sta. 1091+00. A small orifice had developed in the existing pavement along with a noticeable deflection of the surrounding pavement. | Traffic was diverted away from the site of the failure. The contractor excavated all loose material in the hole. The sinkhole was treated with fabric and granular backfill. The existing pavement was repaired to near original condition.
2012-10-15 | Geotechnical | Sinkhole | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | A void under the existing pavement structure was located during this project near Sta. 1091+00. A small orifice had developed in the existing pavement along with a noticeable deflection of the surrounding pavement. | Traffic was diverted away from the site of the failure. The contractor excavated all loose material in the hole. The sinkhole was treated with fabric and granular backfill. The existing pavement was repaired to near original condition.
2012-10-15 | Traffic | Signals | RECONSTRUCTION(O) | 8 | CUMBERLAND | The signal controller cabinet was supplied by the Department and installed by a subcontractor on this project. Upon installation , it was determined that the controller cabinet was faulty. | The section office coordinated swapping out the faulty equipment and compensated the contractor for the additional work necessary to replace and reinstall.
2012-10-15 | Drainage | Ponding | RECONSTRUCTION(O) | 8 | CUMBERLAND | Near the completion of the project , a ponding issue was noticed at the entrance to IGA during heavy rain events. The drainage box shown on the plans was up in the entrance higher than the roadway providing little drainage in this area. | The contractor agreed to install an additional inlet tying it into the newly installed storm sewer system. The work was performed as a Cost Plus agreement.
2012-10-15 | Geotechnical | Sinkhole | RELOCATION(O) | 8 | CUMBERLAND | A void under the existing pavement structure was located during this project near Sta. 1091+00. A small orifice had developed in the existing pavement along with a noticeable deflection of the surrounding pavement. | Traffic was diverted away from the site of the failure. The contractor excavated all loose material in the hole. The sinkhole was treated with fabric and granular backfill. The existing pavement was repaired to near original condition.
2012-10-15 | Traffic | Signals | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The signal controller cabinet was supplied by the Department and installed by a subcontractor on this project. Upon installation , it was determined that the controller cabinet was faulty. | The section office coordinated swapping out the faulty equipment and compensated the contractor for the additional work necessary to replace and reinstall.
2012-10-15 | Drainage | Elevation | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The plans included installing a drainage box at the entrance into ACE Hardware from Gentry Street. The box was installed per plan elevation; however , the box was too high to adequately provide drainage of the surrounding pavement. | The contractor was paid to lower the box inlet and extend curb and gutter from mainline along Gentry Street to direct flow toward the box. The extended curb also served to encourage trucks to avoid cutting the radius and rutting the earthen island.
2012-10-15 | Traffic | Signals | RELOCATION(O) | 8 | CUMBERLAND | The signal controller cabinet was supplied by the Department and installed by a subcontractor on this project. Upon installation , it was determined that the controller cabinet was faulty. | The section office coordinated swapping out the faulty equipment and compensated the contractor for the additional work necessary to replace and reinstall.
2012-10-15 | Drainage | Ponding | RELOCATION(O) | 8 | CUMBERLAND | Ponding issues were noticed in two separate locations along the project in adjacent yards. These issues were likely existing drainage problems and not a result of the scope of this project. The respective property owners complained about the water pondi | The section office coordinated with the contractor to install two yard boxes to alleviate the ponding issues which involved removing and replacing sidewalk and tying into the newly installed storm sewer system. During project development , one of the ya
2012-10-15 | Drainage | Ponding | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Ponding issues were noticed in two separate locations along the project in adjacent yards. These issues were likely existing drainage problems and not a result of the scope of this project. The respective property owners complained about the water pondi | The section office coordinated with the contractor to install two yard boxes to alleviate the ponding issues which involved removing and replacing sidewalk and tying into the newly installed storm sewer system. During project development , one of the ya
2012-10-15 | Drainage | Ponding | RECONSTRUCTION(O) | 8 | CUMBERLAND | Ponding issues were noticed in two separate locations along the project in adjacent yards. These issues were likely existing drainage problems and not a result of the scope of this project. The respective property owners complained about the water pondi | The section office coordinated with the contractor to install two yard boxes to alleviate the ponding issues which involved removing and replacing sidewalk and tying into the newly installed storm sewer system. During project development , one of the ya
2012-10-15 | Drainage | Ponding | RECONSTRUCTION(O) | 8 | CUMBERLAND | Ponding issues were noticed in two separate locations along the project in adjacent yards. These issues were likely existing drainage problems and not a result of the scope of this project. The respective property owners complained about the water pondi | The section office coordinated with the contractor to install two yard boxes to alleviate the ponding issues which involved removing and replacing sidewalk and tying into the newly installed storm sewer system. During project development , one of the ya
2012-10-15 | Drainage | Ponding | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Ponding issues were noticed in two separate locations along the project in adjacent yards. These issues were likely existing drainage problems and not a result of the scope of this project. The respective property owners complained about the water pondi | The section office coordinated with the contractor to install two yard boxes to alleviate the ponding issues which involved removing and replacing sidewalk and tying into the newly installed storm sewer system. During project development , one of the ya
2012-10-15 | Drainage | Elevation | RELOCATION(O) | 8 | CUMBERLAND | The plans included installing a drainage box at the entrance into ACE Hardware from Gentry Street. The box was installed per plan elevation; however , the box was too high to adequately provide drainage of the surrounding pavement. | The contractor was paid to lower the box inlet and extend curb and gutter from mainline along Gentry Street to direct flow toward the box. The extended curb also served to encourage trucks to avoid cutting the radius and rutting the earthen island.
2012-10-15 | Drainage | Ponding | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Near the completion of the project , a ponding issue was noticed at the entrance to IGA during heavy rain events. The drainage box shown on the plans was up in the entrance higher than the roadway providing little drainage in this area. | The contractor agreed to install an additional inlet tying it into the newly installed storm sewer system. The work was performed as a Cost Plus agreement.
2012-10-15 | Drainage | Ponding | RECONSTRUCTION(O) | 8 | CUMBERLAND | Near the completion of the project , a ponding issue was noticed at the entrance to IGA during heavy rain events. The drainage box shown on the plans was up in the entrance higher than the roadway providing little drainage in this area. | The contractor agreed to install an additional inlet tying it into the newly installed storm sewer system. The work was performed as a Cost Plus agreement.
2012-10-15 | Drainage | Ponding | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | Near the completion of the project , a ponding issue was noticed at the entrance to IGA during heavy rain events. The drainage box shown on the plans was up in the entrance higher than the roadway providing little drainage in this area. | The contractor agreed to install an additional inlet tying it into the newly installed storm sewer system. The work was performed as a Cost Plus agreement.
2012-10-15 | Geotechnical | Sinkhole | RECONSTRUCTION(O) | 8 | CUMBERLAND | A void under the existing pavement structure was located during this project near Sta. 1091+00. A small orifice had developed in the existing pavement along with a noticeable deflection of the surrounding pavement. | Traffic was diverted away from the site of the failure. The contractor excavated all loose material in the hole. The sinkhole was treated with fabric and granular backfill. The existing pavement was repaired to near original condition.
2012-10-15 | Drainage | Elevation | RECONSTRUCTION(O) | 8 | CUMBERLAND | The plans included installing a drainage box at the entrance into ACE Hardware from Gentry Street. The box was installed per plan elevation; however , the box was too high to adequately provide drainage of the surrounding pavement. | The contractor was paid to lower the box inlet and extend curb and gutter from mainline along Gentry Street to direct flow toward the box. The extended curb also served to encourage trucks to avoid cutting the radius and rutting the earthen island.
2012-10-15 | Drainage | Ponding | RELOCATION(O) | 8 | CUMBERLAND | Near the completion of the project , a ponding issue was noticed at the entrance to IGA during heavy rain events. The drainage box shown on the plans was up in the entrance higher than the roadway providing little drainage in this area. | The contractor agreed to install an additional inlet tying it into the newly installed storm sewer system. The work was performed as a Cost Plus agreement.
2012-10-15 | Design | Shelved Plans | RELOCATION(O) | 8 | CUMBERLAND | This project was fully designed with a rural typical. Later , it was redesigned with an urban typical (curb & gutter) with a TWLTL. Many of the issues encountered on this project were due to the plans being shelved. None of the original designers assi | District Design forces worked closely with Project Delivery to provide a corrected set of drawings during the construction phase.
2012-10-15 | Design | Shelved Plans | RECONSTRUCTION(O) | 8 | CUMBERLAND | This project was fully designed with a rural typical. Later , it was redesigned with an urban typical (curb & gutter) with a TWLTL. Many of the issues encountered on this project were due to the plans being shelved. None of the original designers assi | District Design forces worked closely with Project Delivery to provide a corrected set of drawings during the construction phase.
2012-10-15 | Design | Shelved Plans | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | This project was fully designed with a rural typical. Later , it was redesigned with an urban typical (curb & gutter) with a TWLTL. Many of the issues encountered on this project were due to the plans being shelved. None of the original designers assi | District Design forces worked closely with Project Delivery to provide a corrected set of drawings during the construction phase.
2012-10-15 | Design | Shelved Plans | RECONSTRUCTION(O) | 8 | CUMBERLAND | This project was fully designed with a rural typical. Later , it was redesigned with an urban typical (curb & gutter) with a TWLTL. Many of the issues encountered on this project were due to the plans being shelved. None of the original designers assi | District Design forces worked closely with Project Delivery to provide a corrected set of drawings during the construction phase.
2012-10-15 | Design | Shelved Plans | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | This project was fully designed with a rural typical. Later , it was redesigned with an urban typical (curb & gutter) with a TWLTL. Many of the issues encountered on this project were due to the plans being shelved. None of the original designers assi | District Design forces worked closely with Project Delivery to provide a corrected set of drawings during the construction phase.
2012-10-15 | Utilities | Existing Utilities | RELOCATION(O) | 8 | CUMBERLAND | An existing fire hydrant at Sta. 1050+00 Lt. ended up being approximately 1' below grade once the fill slope was constructed per plan. | The fire hydrant was raised by the prime contractor as part of this contract.
2012-10-15 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 8 | CUMBERLAND | An existing fire hydrant at Sta. 1050+00 Lt. ended up being approximately 1' below grade once the fill slope was constructed per plan. | The fire hydrant was raised by the prime contractor as part of this contract.
2012-10-15 | Pavement | Design | RELOCATION(O) | 8 | CUMBERLAND | The contractor proposed using a thicker application of #2 stone and reducing the thickness of the Crushed Stone Base layer as designed. | After confirming with Central Office Pavement , the proposal was accepted. This solution provided an easier method of maintaining temporary access to the adjoining properties during construction.
2012-10-15 | Pavement | Design | RECONSTRUCTION(O) | 8 | CUMBERLAND | The contractor proposed using a thicker application of #2 stone and reducing the thickness of the Crushed Stone Base layer as designed. | After confirming with Central Office Pavement , the proposal was accepted. This solution provided an easier method of maintaining temporary access to the adjoining properties during construction.
2012-10-15 | Pavement | Design | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The contractor proposed using a thicker application of #2 stone and reducing the thickness of the Crushed Stone Base layer as designed. | After confirming with Central Office Pavement , the proposal was accepted. This solution provided an easier method of maintaining temporary access to the adjoining properties during construction.
2012-10-15 | Pavement | Design | RECONSTRUCTION(O) | 8 | CUMBERLAND | The contractor proposed using a thicker application of #2 stone and reducing the thickness of the Crushed Stone Base layer as designed. | After confirming with Central Office Pavement , the proposal was accepted. This solution provided an easier method of maintaining temporary access to the adjoining properties during construction.
2012-10-15 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 8 | CUMBERLAND | An existing fire hydrant at Sta. 1050+00 Lt. ended up being approximately 1' below grade once the fill slope was constructed per plan. | The fire hydrant was raised by the prime contractor as part of this contract.
2012-10-15 | Utilities | Existing Utilities | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | An existing fire hydrant at Sta. 1050+00 Lt. ended up being approximately 1' below grade once the fill slope was constructed per plan. | The fire hydrant was raised by the prime contractor as part of this contract.
2012-10-15 | Traffic | Signals | RECONSTRUCTION(O) | 8 | CUMBERLAND | The signal controller cabinet was supplied by the Department and installed by a subcontractor on this project. Upon installation , it was determined that the controller cabinet was faulty. | The section office coordinated swapping out the faulty equipment and compensated the contractor for the additional work necessary to replace and reinstall.
2012-10-15 | Utilities | Existing Utilities | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | An existing fire hydrant at Sta. 1050+00 Lt. ended up being approximately 1' below grade once the fill slope was constructed per plan. | The fire hydrant was raised by the prime contractor as part of this contract.
2012-10-15 | Traffic | Markings | RECONSTRUCTION(O) | 8 | CUMBERLAND | The plans indicated striping an island in the transition at the end of the project; however , the left turn volume at the entrance Rt. Sta. 1093+92.23 was fairly high. | The section office along with District 4 Traffic decided to stripe a left turn lane in order to improve Southbound traffic flow.
2012-10-15 | Traffic | Markings | RELOCATION(O) | 8 | CUMBERLAND | The plans indicated striping an island in the transition at the end of the project; however , the left turn volume at the entrance Rt. Sta. 1093+92.23 was fairly high. | The section office along with District 4 Traffic decided to stripe a left turn lane in order to improve Southbound traffic flow.
2012-10-15 | Traffic | Markings | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The plans indicated striping an island in the transition at the end of the project; however , the left turn volume at the entrance Rt. Sta. 1093+92.23 was fairly high. | The section office along with District 4 Traffic decided to stripe a left turn lane in order to improve Southbound traffic flow.
2012-10-15 | Traffic | Markings | RECONSTRUCTION(O) | 8 | CUMBERLAND | The plans indicated striping an island in the transition at the end of the project; however , the left turn volume at the entrance Rt. Sta. 1093+92.23 was fairly high. | The section office along with District 4 Traffic decided to stripe a left turn lane in order to improve Southbound traffic flow.
2012-10-15 | Traffic | Markings | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The plans indicated striping an island in the transition at the end of the project; however , the left turn volume at the entrance Rt. Sta. 1093+92.23 was fairly high. | The section office along with District 4 Traffic decided to stripe a left turn lane in order to improve Southbound traffic flow.
2012-10-15 | Pavement | Design | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | The contractor proposed using a thicker application of #2 stone and reducing the thickness of the Crushed Stone Base layer as designed. | After confirming with Central Office Pavement , the proposal was accepted. This solution provided an easier method of maintaining temporary access to the adjoining properties during construction.
2012-10-15 | Design | Omission | RELOCATION(O) | 8 | CUMBERLAND | This project qualified for the standard rideability notes; however , the appropriate note and bid item was omitted from the contract documents. | The project was checked using a 10' straight edge to ensure compliance with the specifications concerning surface variability.
2012-10-15 | Design | Omission | RECONSTRUCTION(O) | 8 | CUMBERLAND | This project qualified for the standard rideability notes; however , the appropriate note and bid item was omitted from the contract documents. | The project was checked using a 10' straight edge to ensure compliance with the specifications concerning surface variability.
2012-10-15 | Design | Omission | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | This project qualified for the standard rideability notes; however , the appropriate note and bid item was omitted from the contract documents. | The project was checked using a 10' straight edge to ensure compliance with the specifications concerning surface variability.
2012-10-15 | Design | Omission | RECONSTRUCTION(O) | 8 | CUMBERLAND | This project qualified for the standard rideability notes; however , the appropriate note and bid item was omitted from the contract documents. | The project was checked using a 10' straight edge to ensure compliance with the specifications concerning surface variability.
2012-10-15 | Design | Omission | SPOT IMPROVEMENTS(O) | 8 | CUMBERLAND | This project qualified for the standard rideability notes; however , the appropriate note and bid item was omitted from the contract documents. | The project was checked using a 10' straight edge to ensure compliance with the specifications concerning surface variability.
2012-09-27 | Geotechnical | Soils | RECONSTRUCTION(O) | 1 | BALLARD | The design plans called for 1' Rock Roadbed to stabilize the subgrade prior to the placement of the pavement typical. The contractor proposed using Cement Stabilized Roadbed in lieu of Rock Roadbed as a cost savings measure. | The department agreed with the proposal and allowed the change.
2012-09-27 | Drainage | Coordination | NEW ROUTE(O) | 1 | GRAVES | The roadway plans showed a cross drain and drop box inlets within 25' of the bridge end. The structure plans showed a 25' buried approach slab. | Drop boxes and cross drain were moved outside the limits of the approach slab for maintenance reasons. Island integral curb was extended to the boxes to accommodate drainage.
2012-09-27 | Construction | Specifications | RECONSTRUCTION(O) | 1 | BALLARD | Due to the high variability in material available from local sources in regards to granular embankment , the review team discussed the possibility of improving our presentation of those items in the contract documents. | Designers should consider using separate bid items for erodible vs. non-erodible granular embankment and reflect the quantities as indicated in the geotechnical report.
2012-09-27 | Structures | Expansion Joints | NEW ROUTE(O) | 1 | GRAVES | As a result of current design practices , structural plans do not include expansion joints typically based on the request of bridge maintenance. The issue of expansion/contraction is currently pushed out to the end bents. Subsequently , a gap is formi | The solution is currently being studied , but will likely include building a short concrete wall on the buried approach slab and including an expansion material between the wall and the armored edge of the bridge.
2012-09-27 | Construction | Coordination | RECONSTRUCTION(O) | 1 | BALLARD | On one section of the project , the curb is designed to set on DGA Base and another section is designed to set on the first layer of asphalt base due to different pavement designs. | The contractor expressed some concern regarding the slip form method of placing curb. The subcontractor wants the paving contractor to leave the asphalt base layer low for constructability issues. This needs to be considered during development of typical
2012-09-27 | Structures | Elevation Difference | RECONSTRUCTION(O) | 1 | BALLARD | One bridge on this project was in a super transition , but the bridge plans indicated normal crown throughout. The roadway plans detailed the superelevation transition correctly. | Structures issued a plan revision detailing the correction. One end of the bridge had to be raised to accommodate the change. Contractor indicated that this issue and quick action by the department did not cause a delay on the project.
2012-09-27 | Erosion Control Plan | Slope Protection | RECONSTRUCTION(O) | 1 | BALLARD | Due to geotechnical concerns of slope erosion , a certain 2:1 slope was designed to be lined with rock. A neighbor noticed this and wanted the slope in front of his property lined with rock so he did not have to mow it. | During project development , more consideration should be given to slope protection of steep slopes to eliminate the need for mowing by the property owners in residential areas.
2012-09-27 | Design | Shelved Plans | RECONSTRUCTION(O) | 1 | BALLARD | Project plans were shelved on this project but were later submitted as a good project to build in 2011 to meet letting goals. During the time frame prior to letting , much development occurred on the Steve Smith Property at approximately Station 515+00 s | Designers should revisit plans just prior to letting to ensure areas of development have not impacted the design in particular the drainage features / patterns. The department and contractor worked together to adjust the drainage design to match field con
2012-09-27 | Structures | Approaches | NEW ROUTE(O) | 1 | GRAVES | The approach slab was designed to be 4 lower than the 8 JPC shoulder. This creates an issue with differential settlement and an associated bump or drop. | The Section Engineer decided to drop the 8 JPC shoulder 4 inches and place a coarse of base and surface on the next phase. Other possible solutions detailed in the comments section of this report.
2012-09-27 | Structures | Communication | RECONSTRUCTION(O) | 1 | BALLARD | During the project development phase , practical solutions was applied to the project and the design typical was reduced to 11' driving lanes , 13' turning lane , and 5' shoulders. The bridges were designed matching the original typical , so the bridg | There was not enough time before letting to change the bridge design; therefore , they were constructed as designed resulting in an obvious waste.
2012-09-27 | Structures | Piling/Drilled Shaft | NEW ROUTE(O) | 1 | GRAVES | The piles on this project were designed for drag down force (slippage) so the 30 day settlement restriction in the contract was not needed. | The settlement platform and associated steel piping were removed from the contract because of the 30 day settlement waiver.
2012-09-27 | Maintenance of Traffic | Changes | RECONSTRUCTION(O) | 1 | BALLARD | The designer presented a viable MOT plan based on using stone. Due to the feasibility of using Cement Stabilized Roadbed and the contractor having a borrow pit close to the project , several MOT changes were needed. | The department and contractor reached an agreement on the necessary MOT changes to reflect the change in subgrade stabilization and borrow soil.
2012-09-27 | Design | Borrow/Waste | RECONSTRUCTION(O) | 1 | BALLARD | As a result of the bridges being wider that the roadway , extra material was required in order to taper the roadway typical into the bridges. | The contractor and the designer have been working together to resolve the issues by providing some modifications to the plans regarding tapering the roadway design features into the bridges.
2012-09-27 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 1 | BALLARD | The contractor encountered some areas of unsuitable material in the subsurface soil. | These areas were undercut and removed and replaced with suitable borrow material soil. This method has added to the extra amount of borrow material needed to construct the project.
2012-09-27 | Design | Phasing | NEW ROUTE(O) | 1 | GRAVES | Due to the special nature of how this portion of the overall project was separated out , several items of work were not necessary for completion of partial fills and would likely be disturbed or damaged. | Perforated pipe , non-perforated pipe , and associated headwalls were removed from this contract and added to the next phase.
2012-09-26 | Erosion Control Plan | Slope Protection | RECONSTRUCTION(O) | 2 | CHRISTIAN | Originally , the project included some quantity of Class III Channel Lining in order to protect erosion on steep slopes with poor soil. The areas were detailed on the plans and the quantity was correct for those areas. During the project , the project d | The bid item used for this operation was changed to Crushed Aggregate Size 3. District 1 has found this method of slope protection to be more effective than traditional methods of seeding and/or erosion control blanket.
2012-09-26 | Pavement | Omission | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | An asphalt overlay was planned on this project; however , the existing pavement was significantly deteriorated due to rutting and cracking. These issues , combined with the high average daily traffic and the heavy truck traffic from Fort Campbell , wo | Level and Wedging was omitted from the original contract , but the Cabinet deemed it necessary to ensure the integrity of the new asphalt pavement. This issue might have been identified by a field visit.
2012-09-26 | Pavement | Omission | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | There were concerns about the lack of items in the contract to prevent weather and chemicals from prematurely deteriorating the asphalt roadway. | Asphalt Curing Seal , which was omitted from the original contract , was added by Change Order to ensure the integrity of the new pavement. The asphalt curing seal was applied directly to the DGA prior to placement of the asphalt base.
2012-09-26 | Maintenance of Traffic | Diversions | RECONSTRUCTION(O) | 2 | CHRISTIAN | A constructability issue came up during construction concerning the detour tie-in on the West end including safety concerns. The tie-in design appeared fine on the plans but did not match field conditions. | Upon request from the Section Engineer's Office , the contractor proposed a new tie-in location with a slight adjustment in grade. The department agreed with the solution and this resulted in a minimal cost increase.
2012-09-26 | Erosion Control Plan | Slope Protection | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | The embankment at the intersection of Cole Road and US 41 A was being eroded by water coming of the pavement. | During final inspection , channel lining for this area was added to the punch list. However , the channel lining also eroded and this area still needs maintenance. Erosion control blanket and established turf would not be sufficient to correct this is
2012-09-26 | Design | Omission | RECONSTRUCTION(O) | 2 | CHRISTIAN | An existing concrete box culvert on KY 286 was left in place but was not shown to be safeloaded on the plans. | The box culvert was safeloaded to alleviate future maintenance issues.
2012-09-26 | Pavement | Shoulders | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | Adding leveling and wedging beneath the overlay created a three inch shoulder drop-off. There was insufficient earth material to correct the drop-off situation. | Because vehicles frequently utilize the shoulders for passing purposes , additional DGA base was used to expedite correction of the unsafe shoulder drop-off condition.
2012-09-26 | Pavement | Repair | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | After the project was let it became necessary to correct a significant base failure located near the Fort Campbell gate. This area was not set up in the plans to be dug out , but upon inspection and meeting with Fort Campbell personnel it was marked for | The area of the failure was dug out two feet deep , then 15 inches of number two stone were placed , compacted , and wrapped with geotextile fabric , and then the area was capped with three 3 lifts of asphalt base placed on top of the rock. This addi
2012-09-26 | Erosion Control Plan | Slope Protection | RECONSTRUCTION(O) | 2 | CHRISTIAN | Related to issue #1 , no erosion control blanket was established on the contract documents. Some areas were identified by the Section Office to be lined using ECB. | Along the slopes lined with Crushed Aggregate Size 3 , ECB was used for the top 6-8' of the slope. From that point down the slope , #3's were placed.
2012-09-26 | Design | Plans | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | There was a typo on the plans at station number 72+00. The plans called for 60 cubic yards of embankment in place when it should have been 600 cubic yards. | Additional quantities were needed to complete the work shown on the plan sheets causing an overrun. There were insufficient material on the project to offset the typo. This error might have been identified with additional plan checks.
2012-09-26 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 2 | CALDWELL | Three Light Poles needed to be relocated to complete the widening of the roadway , installation of the gate entering Fort Campbell's base , and to build the turn lanes at the radii of 41 A as on plans. Two of the light poles were shown in the plans , | The original contract plans omitted the extra work necessary to complete this work , so an item for relocate light pole was added via Change Order.
2012-09-26 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 2 | CHRISTIAN | An inadequate quantity of temporary mulch was established on the contract to mulch the entire project considering a duration through winter months. The project actually occurred in three separate construction seasons. | Additional quantity of temporary mulch was established via change order.
2012-09-25 | Pavement | Approaches | SAFETY-HAZARD ELIM(P) | 2 | OHIO | The project was set up to only pave the approaches of the bridges , while leaving the gaps between the bridges in their existing condition which created rideability issues. | It would have been better if it were possible to completely pave between all three bridges , but mitigating the impacts on surrounding wetlands was a prohibitive factor. The project might have been improved if the Designer could have developed a templat
2012-09-25 | Design | Entrance | SAFETY-HAZARD ELIM(P) | 2 | OHIO | Originally the plans included an entrance onto the Knight property at Sta 119+20. However , on August 19 , 2010 the Design Consultant received a request from the District to eliminate it. This , along with other requested changes , was submitted wit | Guardrail had already been installed blocking the entrance before the issue was identified. The guardrail had to be removed , some changes had to be made to the remaining guardrail , and a 26 foot entrance was constructed. This issue might have been a
2012-09-25 | Construction | Damages | SAFETY-HAZARD ELIM(P) | 2 | OHIO | The original pavement design called for complete pavement removal and reconstruction with the new pavement receiving a 1 foot rock roadbed (no. 2Ös , 3Ös , or 23Ös wrapped in Geotextile Ty IV) for it's base , which would have also served as a working p | The original design may have worked better and prevented these issues , but the design was revised as a cost and time saving measure.
2012-09-25 | Geotechnical | Subsurface | SAFETY-HAZARD ELIM(P) | 2 | OHIO | There was a subgrade failure on one of the bridge approaches. | An agreement was made that the Contractor would pay for surveying and milling and the Cabinet would pay the tonnage for the corrective work.
2012-09-20 | Construction | Revisions | PAVEMENT REHAB-INT(P) | 1 | LYON | The entrance into the Fenton Campground Area became an issue on the project , because the Forest Service was slow to reach consensus on what design features they wanted installed at this location. | An extra lane was added during construction and the original design of two separate entrances into the campground was revised to a single entrance.
2012-09-20 | Environmental | Permitting | PAVEMENT REHAB-INT(P) | 1 | LYON | As a result of the ruling in the Supreme Court case of Rapanos v. United States , the USACE formalized their Jurisdictional Determination process resulting in a significant amount of more detailed documentation. The agreements made between the Design Bu | Significant delays were caused that were unforeseen and the Project Delivery Team decided to add 380 calendar days to the completion date.
2012-09-20 | Drainage | Culvert | PAVEMENT REHAB-INT(P) | 1 | LYON | In the original project proposal , the culverts at Station 3062+22 & Station 3084+35 were set up to be totally replaced. The Cabinet decided in the Design / Build phase of the project that the condition and size of the culverts were appropriate for exte | These culverts were extended in lieu of total replacement and a significant cost reduction was written into change order no. 1.
2012-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 1 | TRIGG | The guardrail was depicted with a 2' offset behind the face of curb on the plan sheets. The typical sections showed the guardrail detail correctly with the face of rail directly over the face of curb. The contractor installed the guardrail according to | The contractor was compensated for moving the guardrail to its correct location with the face of rail over the face of curb.
2012-09-20 | Erosion Control Plan | Seeding | PAVEMENT REHAB-INT(P) | 1 | LYON | The seed mix that was required by the US Forest Service was not effective for temporary or permanent erosion control or vegetative cover. The main reason for this was the lack of soil available for top dressing the backslopes. | The vegetation on the project slopes remains sparse in spots and the Cabinet is continuing negotiations with the Forest Service and the Contractor the resolve the issue.
2012-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 1 | TRIGG | The guardrail was depicted with a 2' offset behind the face of curb on the plan sheets. The typical sections showed the guardrail detail correctly with the face of rail directly over the face of curb. The contractor installed the guardrail according to | The contractor was compensated for moving the guardrail to its correct location with the face of rail over the face of curb.
2012-09-20 | Construction | Revisions | PAVEMENT REHAB-INT(P) | 1 | LYON | During the design / build portion of the project , the project development team decided to install an underpass for the hike and bike trail located near Bacon Creek Road for safety reasons. The trail was part of a bigger LBL facility and the volume of b | Con Span structures were utilized for both East and West bound lanes at the intersection to accomplish the underpass.
2012-09-20 | Pavement | Striping | MAJOR WIDENING(O) | 1 | TRIGG | The project documents directed the contractor to install permanent striping - paint on concrete pavements. Typical permanent paint does not adhere to concrete pavements very well and fades quickly. | The department decided to install permanent striping - tape to replace the paint. In areas with concrete pavement , designers should consider specifying either a durable tape type 2 or HD21 paint.
2012-09-20 | Utilities | Relocation | PAVEMENT REHAB-INT(P) | 1 | LYON | As outlined in the FONSI document , several utilities had to be relocated and buried as a mitigation item with the US Forest Service. | Several conduits were installed as part of the contract for use by various utility companies.
2012-09-20 | Pavement | Type | PAVEMENT REHAB-INT(P) | 1 | LYON | Class 2 Asphalt was set up in the contract documents; however , the traffic characteristics required Class 3 Asphalt. | Class 3 Asphalt was used and established on project via change order.
2012-09-20 | Construction | Delays | MAJOR WIDENING(O) | 1 | TRIGG | Just prior to letting , high mast lighting was added to the project. The schedule from award to the completion date was too tight considering the submittal process through Central Office and the lead time in acquiring the materials needed for this type | The department agreed to extend the completion date for the lighting item only. In the future , the Cabinet needs to consider setting an intermediate completion date for all project items except those requiring special submittals and/or delivery could b
2012-09-20 | Design | Entrance | MAJOR WIDENING(O) | 1 | TRIGG | The entrance radii at and just North of Applehouse Road were being damaged shortly after construction due to large trucks entering and exiting the truck stop. | The Department directed the contractor to repair curb sections and reinforce with a mountable curb apron behind the curb. This method should be considered in areas where entrance delineation is being proposed in and around businesses with a large volume
2012-09-20 | Design | Communication | PAVEMENT REHAB-INT(P) | 1 | LYON | A major issue on this project resulted from dealing with the US Forest Service as the property owner for the majority of this project. During the life of the project , Land Between the Lakes switched management from TVA to the Forest Service. The initi | The Design / Build Team held monthly team meetings that included KYTC and the Forest Service. Several memorandums of agreements were drafted in order to document consensus.
2012-08-09 | Design | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | The bid item 6 inch shield edge drain cap included approximately 1 sq yd per location. Once installed , traffic was pushed over top of the cap and it was severely damaged and had to be replaced. | The cap was dug out wider and replaced using about 3 sq yds per location.
2012-08-09 | Design | Median | MAJOR WIDENING(O) | 7 | FAYETTE | In order to appropriately construct the design template , the inside median needed to be adjusted which would require a thin lift of embankment resulting in more extensive erosion control measures. | The Project Delivery Team decided to use a DGA wedge to accomplish this work due to constructability reasons , also resulting in using fewer erosion control measures.
2012-08-09 | Design | Omission | MAJOR WIDENING(O) | 7 | FAYETTE | In the areas where the pavement was raised , the flumes had to be partially replaced/modified to accommodate the grade change. The plans did not include this modification. | The flumes were modified according to field condition and the appropriate bid items were adjusted.
2012-08-09 | Structures | Masonry Coating | MAJOR WIDENING(O) | 7 | FAYETTE | Project scope included bridge barrier wall retrofit; however , the bid item for masonry coating was left out of the contract documents. | The appropriate bid item was added via change order.
2012-08-09 | Construction | Method/Innovation | MAJOR WIDENING(O) | 7 | FAYETTE | The proposal included a special note concerning disposal of waste related to the diamond grinding operation which directed the contractor to dispose of material appropriately off site. During construction , the contractor proposed wasting of said materi | Upon approval by the FHWA Environmental Coordinator , the project delivery team decided to allow this practice which resulted in a reduction of the diamond grinding unit price. The disposal operation further complied with KAR 30:301 Environmental Perfor
2012-08-09 | Pavement | Shoulders | MAJOR WIDENING(O) | 7 | FAYETTE | The shoulders in this section of I-24 were severely damaged and deteriorated. | The Project Engineer decided to resurface the shoulders and bid items were adjusted.
2012-08-09 | Drainage | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | The plan quantity for perforated pipe headwalls did not include those needed for blow up relief joints and the longitudinal pavement repairs. | Appropriate quantities were adjusted via change order.
2012-08-09 | Construction | Rumble Strips | MAJOR WIDENING(O) | 7 | FAYETTE | The plans showed diamond grinding from Edge of Pavement to Edge of Pavement. This was difficult to accomplish without disturbing existing rumble strips. | In order to bring the rumble strips up to current standards and provide an additional safety enhancement to the project , sawed rumble strips were added to the contract.
2012-08-09 | Design | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | Plans showed eight Curb Box Inlet Type B-T but only six were established in the contract documents. | This bid item was adjusted via change order.
2012-08-09 | Pavement | Repair | MAJOR WIDENING(O) | 7 | FAYETTE | For the project operation longitudinal pavement repair , the plans indicated using #57 stone as backfill. The contractor proposed using #2 stone instead because of material availability and ease of construction. | At the preconstruction meeting , FHWA , Central Office Personnel , and the Project Engineer agreed to allow this and bid items were adjusted accordingly. It was also suggested that #2 stone performs better in this application historically.
2012-08-09 | Maintenance of Traffic | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | During installation of the temporary barrier wall for temporary traffic control , it was determined that more quantity was established in the contract than was necessary. Appropriate tapers were installed according to standards. | The extra quantity was taken out of the contract via change order.
2012-08-09 | Design | Guardrail | MAJOR WIDENING(O) | 7 | FAYETTE | Field conditions led the Project Delivery Team to change existing End Treatment types in certain locations. | The guardrail bid items were overrun and adjusted accordingly with change order.
2012-08-09 | Drainage | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | The actual shoulder width was 2' wider than indicated in the plans. The associated asphalt quantities were insufficient in quantity. | Appropriate quantities were adjusted via change order.
2012-08-09 | Design | Guardrail | MAJOR WIDENING(O) | 7 | FAYETTE | Field conditions led the Project Delivery Team to change existing End Treatment types in certain locations. | The guardrail bid items were overrun and adjusted accordingly with change order.
2012-08-09 | Pavement | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | Partial depth patching was established in the contract for certain locations. The project engineer decided that partial depth patching was not appropriate and marked all areas for full depth repair. | The partial depth patching item was not used and was removed from the contract with a change order. It was noted in the review that partial depth patching is typically not very effective for concrete pavement sections especially in a deteriorated conditi
2012-08-09 | Pavement | Repair | MAJOR WIDENING(O) | 7 | FAYETTE | During construction , several areas were located and marked for pavement repair due to the deteriorated nature of the pavement. Although quantities were established in the contract for pavement removal and JPC Pavement - 10 inch , they were insufficien | Appropriate quantities were adjusted via change order(s). The exact quantity for these items are difficult to estimate in the project development stage , because many of the failures do not show up until construction commences.
2012-08-09 | Drainage | Quantities | MAJOR WIDENING(O) | 7 | FAYETTE | Extra quantities were needed for 18 inch culvert pipe and metal end sections in order to properly install Type 3 Guardrail End Treatments to allow for proper drainage into existing ditches. | Associated quantities were adjusted via change order. An extra Type 3 end treatment was used in one location due to field conditions.
2012-03-22 | Environmental | Wells | NEW ROUTE(O) | 3 | LOGAN | A gas well located Rt. of Mainline Sta. 5+700 was not accounted for in the plans. | It was necessary to plug the gas well by Change Order.
2012-03-22 | Pavement | Repair | MINOR WIDENING(O) | 3 | EDMONSON | There were concerns about potential rutting on the mainline in the areas of subgrade repair. | Additional Class II Asphalt Base 25.0D PG64-22 was used on the mainline to resist rutting in these areas.
2012-03-22 | Utilities | Conflicting Information | MINOR WIDENING(O) | 3 | EDMONSON | Relocation of the sewer line beneath the proposed sidewalk was required because the alignment shown in the plans conflicted with relocated utility poles. | A supplemental item for Granular Backfill was created to compensate the Contractor for material used for backfill associated with the sewer line relocation.
2012-03-22 | Pavement | Repair | MINOR WIDENING(O) | 3 | EDMONSON | Additional material was needed to make repairs on the eastbound ramps just beyond the project limits. | A supplemental item for PCC Pavement-225mm/24 was created to compensate the Contractor. The twenty four hour strengths were necessary to facilitate the maintenance of traffic through the area.
2012-03-22 | Drainage | Error | NEW ROUTE(O) | 3 | LOGAN | The inlet of an existing 600mm culvert pipe at Lt. Sta. 3+687 was located past the ROW line and the outlet did not align with the Drop Box Inlet Type 2 as shown on the plans. | It was necessary to modify the Drop Box Inlet so it would connect with the existing culvert pipe.
2012-03-22 | Geotechnical | Top of Rock | NEW ROUTE(O) | 3 | LOGAN | While excavating to rock as shown on the plans for the culvert construction at ML Sta. 3+980 , a coal seam approximately 30 inches thick was encountered slightly above the bottom of the footing elevation. | Additional quantities of Structure Excavation ô Common and Structure Excavation ô Solid Rock had to be set up. This material had to be removed and the area refilled with granular embankment material.
2012-03-22 | Maintenance of Traffic | Entrances | NEW ROUTE(O) | 3 | LOGAN | The existing driveway at RT. Sta. 4+670 was in a cut section and the Right-of-Way agreement included maintaining daily access to the residence , but there were no items set up in the plans for this purpose. | Traffic Bound Base was added for maintaining access to the property until the cut was finished and the entrance was permanently constructed.
2012-03-22 | Maintenance of Traffic | Changes | MINOR WIDENING(O) | 3 | EDMONSON | Traffic separation on the diversion from Station 11+600 to Station 11+761 was needed due to a minor traffic control revision necessitated by constructability issues encountered under the Mountain Parkway Overpass. | A supplemental item for Water-Filled Barriers was needed to compensate the Contractor for installation of barriers.
2012-03-22 | Environmental | Wells | NEW ROUTE(O) | 3 | LOGAN | Two additional water wells were discovered within the project limits. | A Change Order was established to plug the two additional water wells discovered within the project limits.
2012-03-22 | Utilities | Omission | NEW ROUTE(O) | 3 | LOGAN | An existing 50mm natural gas line running under the proposed mainline at Sta. 3+350 was not addressed in the plans. | The natural gas line had to be encased before the new mainline was constructed over it.
2012-03-22 | Utilities | Omission | NEW ROUTE(O) | 3 | LOGAN | Numerous water line items were omitted from the plans due to plan errors. | Water line items were added through Change Order and installed based upon the specifications of the Morgan County Water District.
2012-03-22 | Geotechnical | Slides | NEW ROUTE(O) | 3 | LOGAN | Three slides occurred on the project at Sta. Rt 6+450 , Lt Sta 6+260 , and Rt Sta. 5+160. | An additional 25 , 000 cubic meters of roadway excavation was needed to clean up the slide material. The material was removed and measured per specification 204.03.05.
2012-03-22 | Design | Radius | MINOR WIDENING(O) | 3 | EDMONSON | Additional material was needed for minor widening at a radii. | A supplemental item for PCC Pavement-225mm/24 was created to compensate the Contractor. The twenty four hour strengths were necessary to facilitate the maintenance of traffic through the area.
2012-03-22 | Design | Entrance | MINOR WIDENING(O) | 3 | EDMONSON | Before the final quantities of asphalt surface were installed , the entrances required wedging at the ingress/egress in the curb and gutter sections. | Additional quantities of Leveling and Wedging Asphalt Surface PG64-22 were added to wedge the entrances.
2012-03-22 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 3 | LOGAN | Insufficient quantities were set up to maintain access of local traffic to their homes. | Additional quantities of Traffic Bound Base were established.
2012-03-22 | Erosion Control Plan | Quantities | MINOR WIDENING(O) | 3 | EDMONSON | Insufficient quantities of Seeding and Protection were established in the plans. | Additional quantities of Seeding and Protection were added through Change Order.
2012-03-22 | Pavement | Approaches | MINOR WIDENING(O) | 3 | EDMONSON | The Pendleton Street Approach was not designed to conform with the mainline pavement design. However , there were concerns that the proposed pavement design would be insufficient due to anticipated heavy loading from vehicles accessing the new State Mai | It was recommended that traffic counts be investigated to insure the proper pavement design for heavy traffic. In this case , additional quantities of Class II Asphalt Base 25.0D PG64-22 were added to conform Pendleton Street to the mainline pavement des
2012-03-22 | Maintenance of Traffic | Quantities | MINOR WIDENING(O) | 3 | EDMONSON | Additional material was needed for the diversion construction from Sta. 11+600 to Sta. 11+761. | Additional quantities of Class I Asphalt Base 25.0D PG64-22 were added by Change Order.
2012-03-22 | Geotechnical | Unsuitable Material | MINOR WIDENING(O) | 3 | EDMONSON | Unsuitable material was encountered at various locations throughout the project. The construction area was predominately swamp land and it was in the opinion of the construction team that the soil parameters specified for the job site were miscalculated. | It was felt that more Geotechnical investigation at the job site would have minimized a significant amount of undercutting. As it turned out , bid items for Fabric-Geotextile Type IV and Crushed Aggregate No. 2 were created and additional quantities of
2012-03-22 | Pavement | Quantities | MINOR WIDENING(O) | 3 | EDMONSON | Insufficient asphalt quantities were established in the plans to adequately construct the park and ride lot. | Additional quantities of Class I Asphalt Base 25.0D PG64-22 were added by Change Order.
2012-03-22 | Utilities | Delays | MINOR WIDENING(O) | 3 | EDMONSON | Delays in utility construction caused the project to be under traffic for an unanticipated extended period of time during which the Pavement Striping-Temporary Paint wore off. | Additional quantities of Pavement Striping-Temporary Paint-100mm were needed to compensate the Contractor for re-striping during the project.
2012-03-22 | Erosion Control Plan | Quantities | NEW ROUTE(O) | 3 | LOGAN | Different access points of the project needed additional erosion control to prevent mud and unsuitable debris from reaching the roadway. | Granular embankment material (crushed aggregate #2Ös) was used at different access points of the project.
2012-03-22 | Maintenance of Traffic | Changes | NEW ROUTE(O) | 3 | LOGAN | After construction began , a change in traffic control resulted in detouring traffic around the work zone by using KY 705. | In order to use KY 705 , 1.5 feet of trenching per side had to be performed in order to widen the road for safe vehicular use. The cost to upgrade KY 705 was offset by not using the paving items setup for the temporary diversions within the work zone.
2012-03-22 | Design | Entrance | MINOR WIDENING(O) | 3 | EDMONSON | Entrances at Left Sta. 11+415 and Right Sta. 11+430 were added and the entrance at Left Sta. 11+344 was widened. | Additional quantities of Cement Concrete Entrance pavementô200mm were established via Change Order.
2012-03-22 | Design | Omission | NEW ROUTE(O) | 3 | LOGAN | An additional structure not accounted for on the plans was discovered within the culvert excavation limits at Sta. 3+220. | The structure was removed via Change Order.
2012-03-22 | Erosion Control Plan | Quantities | NEW ROUTE(O) | 3 | LOGAN | The quantity of coir fiber Erosion Control Blanket set up in the plans was not needed for stream relocation , but additional erosion control mechanisms were needed on various cut slopes. | The coir fiber Erosion Control Blanket was replaced with Erosion Control Blanket (ECB) for the cut slopes and a percentage of the Seeding and Protection quantity was deleted as a result.
2012-03-22 | Pavement | Quantities | MINOR WIDENING(O) | 3 | EDMONSON | There were insufficient quantities in the original plans to properly reconstruct the eastbound off ramp and the westbound on ramp or construct their temporary diversions. | Additional quantities of PCC Pavement 225mm , Leveling and Wedging Asphalt Surface PG64-22 , and Class 2 Asphalt Base 25.0D PG64-22 were established through Change Order.
2012-03-22 | Utilities | Omission | MINOR WIDENING(O) | 3 | EDMONSON | The location of a water and sewer line was unknown because they were not shown on the plans , and they were damaged during construction. | Additional quantities of water and sewer line items were needed to reconstruct the lines.
2012-03-22 | Pavement | Repair | MINOR WIDENING(O) | 3 | EDMONSON | The mainline roadway crown was rendered incorrect due to settlement induced grade irregularities. | Additional quantities of Class 2 Asphalt Base 25.0D PG 70-22 were used to restore the proper mainline roadway crown.
2012-03-22 | Erosion Control Plan | Quantities | NEW ROUTE(O) | 3 | LOGAN | The quantity of Class IV Channel lining set up on the project for rock lined ditch construction and silt control was simply not available within the project limits. | Channel Lining Class IV had to be replaced with Channel Lining Class III.
2012-03-22 | Structures | Omission | MINOR WIDENING(O) | 3 | EDMONSON | A retaining wall was setup in front of one of the buildings at the industrial park , but no details for the retaining wall were included in the plans. | A more thorough review of the plans may have identified this oversight.
2012-03-22 | Utilities | New Utilities | MINOR WIDENING(O) | 3 | EDMONSON | The Stanton City Engineer requested that testing of the new lines be performed at stations 11+125 and 11+160 as well as at various stations between 11+362 , 11+440 , 11+498 , and east and west Pendleton Sta. 0+010 Rt. and Lt. | A supplemental item for Sewer Cleanout was needed to compensate the Contractor for the installation of sewer cleanouts that were not included in the plans , but were needed in order to facilitate testing of the new lines.
2012-03-22 | Utilities | Omission | MINOR WIDENING(O) | 3 | EDMONSON | There were no items shown in the plans for connecting the sewer system to the existing sewer lines at stations 11+160 , 11+125 , 11+369 , 11+440 and 11+550. | Supplemental items for sewer pipe and steel encasement pipe were established to compensate the Contractor for the pipe used to connect the sewer system to the existing lines.
2012-03-22 | Geotechnical | Slides | NEW ROUTE(O) | 3 | LOGAN | As many as six slides occurred during the project life due to the wet fall season. | Most of these were corrected by removing the unstable material and refilling as needed with Channel Lining Class III. An additional 200 meters of perforated pipe was established for drainage purposes during the slide correction at Rt. Sta. 3+150.
2012-03-22 | Design | Elevations | MINOR WIDENING(O) | 3 | EDMONSON | The manholes at stations 11+360 , 11+520 , 11+550 , 11+567 and 11+590 were ordered and installed per plans. However , the plans contained an error with respect to the sewer invert elevations. | A supplemental item for Adjusting Manhole was needed to compensate the Contractor for work performed involving the removal and replacement of the barrel sections of these manholes. The stock barrel sections were replaced with custom items in order to ach
2012-03-22 | Design | Granular Embankment | MINOR WIDENING(O) | 3 | EDMONSON | There were concerns regarding the proposed sidewalk construction because the trench geometry would have limited the compaction of the soil. | A supplemental item for Granular Backfill was created to provide support for the sidewalk construction.
2012-03-22 | Drainage | Quantities | NEW ROUTE(O) | 3 | LOGAN | There was insufficient channel lining for lining drainage ditches because the excavated rock on the job site was not a durable Class IV stone. | An additional quantity of Channel Lining Class III was added for ditch lining.
2012-03-22 | Geotechnical | Slides | NEW ROUTE(O) | 3 | LOGAN | A slide occurred from Sta. 6+400 to Sta. 6+510. | The slide material was removed and the excavated. The area was then backfilled with a channel lining buttress of 6.1m x 6.1m x 6.1m , which required 6 , 000 metric tons of channel lining. Channel Lining Class III was used because durable Class IV rock
2012-03-22 | Right-of-Way | Insufficient ROW | NEW ROUTE(O) | 3 | LOGAN | It was the opinion of the Post Construction Review Team that the Right-of-Way limits on this project were too restrictive. It was very difficult to construct the roadway within the Right-of-Way limits. | It was felt that additional Right-of-Way could have been purchased to accommodate construction within the project limits.
2012-03-22 | Drainage | Omission | MINOR WIDENING(O) | 3 | EDMONSON | The plans did not provide positive drainage at the reconstructed intersection at station 11+767. | Storm Sewer Pipe-450mm and Curb Box Inlet Type B were installed.
2012-03-22 | Maintenance of Traffic | Quantities | MINOR WIDENING(O) | 3 | EDMONSON | There were insufficient items in the plans for proper traffic control related to the eastbound off ramp and westbound on ramp diversions during ramp reconstructions. | Additional quantities of Signs and Pavement Striping-Temporary Paint-100mm were added to compensate the Contractor for signing and striping of the ramp diversions.
2012-03-22 | Design | Entrance | NEW ROUTE(O) | 3 | LOGAN | There were concerns about the slopes of reconstructed driveways. Some reinstalled entrances on the project including very long driveways were 20% grade or worse , which is too steep for driveways as mentioned in other post construction reviews. | It was recommended that slopes for entrances be 15% or less.
2012-03-22 | Erosion Control Plan | Slope Protection | MINOR WIDENING(O) | 3 | EDMONSON | There were several locations where additional slope protection was required. | Additional quantities of Channel Lining Class II were established via Change Order.
2012-03-22 | Drainage | Quantities | NEW ROUTE(O) | 3 | LOGAN | Insufficient quantities of perforated and non-perforated pipe were setup on the plans. | Additional perforated and non-perforated pipe was added via Change Order.
2012-03-22 | Design | Excavation | NEW ROUTE(O) | 3 | LOGAN | The original roadway excavation quantity did not include the material that had to be excavated for the approach Rt. of Mainline Sta. 5+200. | Additional roadway excavation quantities had to be setup through Change Order.
2012-01-31 | Maintenance of Traffic | Entrances | RELOCATION(O) | 11 | WHITLEY | There were insufficient materials established to maintain approach roads , field entrances , and residential drives during the construction of the project. | A Change Order provided additional quantities of Traffic Bound Base needed to maintain these areas during the construction of the project.
2012-01-31 | Erosion Control Plan | Slope Protection | NEW ROUTE(O) | 11 | KNOX | There were insufficient erosion control mechanisms set up on this project. | It was decided to use erosion control blanket on all 2:1 slopes encountered throughout the project. It was recommended that erosion control plans in areas such as this include an over estimate of quantities. The erosion control plans need to include ite
2012-01-31 | Drainage | Quantities | NEW ROUTE(O) | 11 | KNOX | No quantities for temporary pipe were setup on the original contract. Temporary entrance pipe was needed at two locations at Sta. 14+595 and Sta. 15+370. Temporary pipes were also needed for construction on both sides of the Arthur Road intersection. | Quantities for temporary pipe were established through a Change Order.
2012-01-31 | Drainage | Diversion Drainage | RELOCATION(O) | 11 | WHITLEY | A drainage problem arose at the end of the project where excessive runoff was affecting some adjacent property owners. | A decision was made to divert water back to the left side of the road to eliminate the excessive runoff problem for adjacent property owners. A string of culvert pipe was added , Channel Lining Class II was used in the ditch since the Channel Lining Cla
2012-01-31 | Design | Intersection | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | The current cross slope on existing KY 3041 (Corbin Bypass) was 3% instead of 2% as indicated on a previous project. The incorrect 3% slope caused the existing bypass to be approximately 3 inches too low at the proposed KY 3606 intersection. The design | This issue may have been indentified by more thorough field inspections checking the existing bypass cross slope. Additional Class III Asphalt Base was added to correct the cross slope on the bypass to provide a smooth transition for the proposed connect
2012-01-31 | Design | Special Note | RELOCATION(O) | 11 | JACKSON | There were $1 , 000 , 000 in funds left on this job , but there were additional potential safety improvements that were not addressed. | Allow plans to included a special note suggesting that any unused money be applied towards additional safety improvements on the project.
2012-01-31 | Design | Omission | RELOCATION(O) | 11 | JACKSON | The bid item needed to pay Mobilization of Milling and Texturing was inadvertently omitted from contract. | This item was added via Change Order. In general , this type of omission might have been noticed during a detailed review of the plans , but this project was under a tight timeline that did not allow adequate opportunity for review.
2012-01-31 | Maintenance of Traffic | Safety | NEW ROUTE(O) | 11 | KNOX | There were safety concerns regarding the need to protect the traveling public from a cut area created during construction of the new alignment at the beginning of the project along KY 101. | Temporary Guardrail was installed to protect the traveling public.
2012-01-31 | Drainage | Omission | RELOCATION(O) | 11 | WHITLEY | Entrance pipes for two locations were omitted from the bid items even though they were shown on the plans. One location was a field entrance and the other was a residential drive. | Entrance pipes for these locations were established through Change Order.
2012-01-31 | Design | Specifications | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | A change in lane taper length specifications occurred after the project was let. | This issue was unavoidable. Class III Asphalt Base quantities were added to construct the additional lane taper lengths required by the new specifications.
2012-01-31 | Design | Evaluations | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Additional investigation into the soil conditions at the proposed KY 6 connector site during the preconstruction phase would have been beneficial. Increased preparation would likely have helped identify the soft ground conditions in this area , but beca | This project would have benefitted from special surveying , or field pickups , conducted around the flat areas. Better mapping probably would have resolved many of the drainage issues. The Cabinet should have investigated the need for a bridge more th
2012-01-31 | Geotechnical | Sinkhole | RELOCATION(O) | 11 | WHITLEY | The contract plans called for a rock embankment to be constructed from Station 2+400 to 2+600. However , the existing ground was swampy because a large sinkhole at Station 2+565 received most of the water in this area. | Geotextile fabric was needed to provide the Contractor a good working platform at this location. Additionally , a decision was made to use the fabric as a barrier between the existing ground and the rock fill.
2012-01-31 | Right-of-Way | Coordination | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Based upon the plans , construction staff assumed that thirty feet of Right-of-Way was acquired but when work began it was discovered that none of the Right-of-Way had been purchased. | The plans should have included clarification that Right-of-Way was not already purchased. It was also suggested that instead of always assuming that all thirty feet of Right-of-Way have been acquired , the Cabinet should assume that only fifteen feet ha
2012-01-31 | Erosion Control Plan | Quantities | RELOCATION(O) | 11 | WHITLEY | There were insufficient erosion control quantities set up to help maintain the erosion control on both sides of the project. | Additional quantities of Crown Vetch and Temporary Silt Fence were added to help maintain erosion control.
2012-01-31 | Environmental | Stream Mitigation | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | The pier footers for the bridge were designed to be constructed within the creek despite environmental stipulations about not disturbing creeks. | The span arrangement should have been designed to avoid entering the creek or a permit should have been requested to divert the creek so it could be spanned.
2012-01-31 | Geotechnical | Elevations | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Unstable footing materials were encountered at Piers 3 , 4 , 5 , 6 , & 7. Despite core samples taken from the proper locations , the Geotechnical information showed durable rock at these locations , but in reality soft shale was uncovered. | All unstable material encountered was undercut and backfilled with Class B Concrete to achieve the proposed footing elevations. Some of the proposed footings needed to be undercut by as much as 4 feet.
2012-01-31 | Design | Communication | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | A septic tank that was not identified on the plans was located directly in the path of a proposed ditch. | The location of the unmarked septic tank was identified through conversation with a local property owner and the ditch was modified to avoid it.
2012-01-31 | Design | Omission | NEW ROUTE(O) | 11 | KNOX | The filter fabric for treating sinkholes was originally omitted from the bid quantities. | A Change Order added quantities of filter fabric.
2012-01-31 | Drainage | Pipe Sizing | RELOCATION(O) | 11 | WHITLEY | A drainage problem occurred at the end of the project. | Two existing entrance pipes were upsized and replaced. In order to fix this problem during the design stage , the project limits would have needed to be extended.
2012-01-31 | Erosion Control Plan | Communication | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | There were concerns regarding the Contractor's willingness to comply with the Cabinet's request for increased erosion control measures within the specified time frame. | A Change Order was approved to allow the Cabinet to enforce liquidated damages as a means to encourage the Contractor to comply with the Cabinet's erosion control requests.
2012-01-31 | Design | Safety | RELOCATION(O) | 11 | JACKSON | Four strings of guardrail from MP 17.34 to MP 18.97 had been hit repeatedly. During one winter , three end treatments were replaced while an additional two needed replacement. Accident records indicate that over the past five years , approximately for | Guardrail throughout this section was eliminated and the bifurcated median was excavated. Fill slopes were then widened creating a minimum of 4:1 traversable slopes in order to drastically reduce the amount of accidents in this area. These safety improv
2012-01-31 | Design | Shoulders | RELOCATION(O) | 11 | WHITLEY | There were maintenance concerns regarding the area from Station 1+700 to Station 3+015 , which consisted of a large fill constructed out of limestone shot rock with a 2:1 slope. | A decision was made to add chip sealed shoulders in this area because it was felt they would facilitate easier maintenance.
2012-01-31 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Swampy conditions were encountered on KY 6 at approximate Station 52+00. The water table in this area was very near the surface and needed to be lowered before the subgrade could be stabilized. However , the plans for this area did not address any drai | A 24 inch concrete culvert pipe was installed at this location to drain the fairly large watershed left of this area. District and construction personnel anticipate that adding this pipe will eliminate the surface water plus help drain the watershed.
2012-01-31 | Drainage | Omission | RELOCATION(O) | 11 | JACKSON | The plans did not address how to tie the new concrete pipe into the existing concrete pipe alignment within the median. | A concrete collar elbow was added to tie the new pipe into existing pipe. This oversight might have been discovered by increased scrutiny of the plans , but the short design timeline did not provide the opportunity.
2012-01-31 | Pavement | Quantities | RELOCATION(O) | 11 | WHITLEY | The project was designed for rock refill on the top 2 feet of subgrade with the subgrade tolerances for rock roadbed set at plus or minus 2 tenths. The subgrade on this project was placed on the lower end of the 2 tenths tolerance. | Additional DGA quantities were needed to achieve the proper grade.
2012-01-31 | Design | Special Note | RELOCATION(O) | 11 | JACKSON | The plans contained a note that required the Contractor to manage existing signage. However , there was some confusion regarding this note because notes involving signage typically apply only to sheeting not panel signs. | An item for removing and resetting panel signs on the Exit 15 ramps was added via Change Order. This issue might have been avoid by including increased clarification and detailed verbiage in the special note.
2012-01-31 | Utilities | Omission | NEW ROUTE(O) | 11 | KNOX | The Contractor was responsible for performing the water line relocation. However , when the utility plans were completed , four water service lines were omitted from the plans. | An agreement was made between the Division of Utilities , Division of Construction , and the utility company allowing the relocation of the four water service lines during the fourth phase of the project.
2012-01-31 | Structures | Specifications | RELOCATION(O) | 11 | JACKSON | This pavement rehab project included bridge overlays , but the bid item needed to remove the existing overlay material from the Cumberland River Bridge was incorrectly set up in the contract as Machine Prep of Slab. | The bid item for Machine Prep of Slab was changed to Remove Existing Concrete Overlay via Change Order. This oversight could have been caught by increased scrutiny of the plans , which time constraints did not allow.
2012-01-31 | Drainage | Ponding | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | This project was designed during a 3 year drought , but during construction standing water was encountered on the KY 6 Connector Road at approach ML Station 50+50. No drainage pipe was set up for this location on the plans but a large amount of water wa | An 18 inch culvert pipe , a sloped and flared inlet outlet box , and geotextile fabric type IV were added at this location to eliminate the water in this area.
2012-01-31 | Geotechnical | Slides | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | A slide occurred Rt. of mainline Station 47+00. | The slide material was removed from this area and Class III Channel Lining was used to backstow the slide area.
2012-01-31 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | Some of the proposed guardrail end treatments were not in compliance with the latest safety standards or did not accommodate actual field conditions. | Guardrail end treatments type 4A were changed to radius rails and terminal sections at the following locations: Station 1+070 Lt. , Station 2+070 Lt. , Station 2+055 Rt. , and Station 2+700 Rt.
2012-01-31 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | Some of the proposed guardrail end treatments were not in compliance with the latest safety standards or did not accommodate actual field conditions. | Guardrail end treatments type 4A were changed to radius rails and terminal sections at the following locations: Station 1+070 Lt. , Station 2+070 Lt. , Station 2+055 Rt. , and Station 2+700 Rt.
2012-01-31 | Geotechnical | Top of Rock | NEW ROUTE(O) | 11 | KNOX | Voids were encountered between the solid rock elevation and the bottom of the footing grade for the single barrel culvert at Sta. 15+820. This is a common problem in this area and is difficult to foresee. | Mass concrete was added to fill the voids.
2012-01-31 | Erosion Control Plan | Channel Lining | NEW ROUTE(O) | 11 | KNOX | The Contractor encountered some limestone on the project and requested to use it in the channel lined ditches , but the only types of Channel Lining that were set up were Classes II and III. | The decision was made to allow the Contractor to use the material for Channel Lining , Class IV.
2012-01-31 | Geotechnical | Sinkhole | RELOCATION(O) | 11 | WHITLEY | More sinkholes than were originally anticipated were encountered on the project. Although the plans did a good job of identifying the locations of most of these voids , the setup quantities were overran. | Additional quantities for cleaning sinkholes were established in order to compensate the Contractor for this necessary work. Also , additional quantities of roadway fill granular embankment and geotextile fabric type IV were needed to treat the sinkhole
2012-01-31 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Very unstable roadway foundation material was encountered throughout the entire length of the KY 6 Connector from Station 35+00 to 60+00. The existing material was very water saturated and too soft to support Crushed Stone Base. Given the location of th | Geotextile fabric type III and durable rock excavated from the project site were used to help provide a stable base on which to place the Crushed Stone Base. This issue should have been better assessed during the Design Phase.
2012-01-31 | Maintenance of Traffic | Omission | RELOCATION(O) | 11 | JACKSON | Initially , there was debate about whether barrier walls should be used for lane closures to complete the deck restoration on the Cumberland River Bridge because it was such a narrow bridge. At the last minute , a decision was made to use barrier wall | Crash Cushions Type VI T were added by Change Order in order to safely protect traffic from the temporary concrete median barrier used during the bridge overlay process. This oversight could have been caught by a thorough final review of the plans just b
2012-01-31 | Drainage | Omission | RELOCATION(O) | 11 | WHITLEY | A low flow diversion curb shown on the plans to be constructed on the inlet end of the triple barrel culvert at Station 2+531 was inadvertently omitted from the original contract bid items. | A bid item for constructing the low flow diversion curb was added via Change Order.
2012-01-31 | Environmental | Wells | RELOCATION(O) | 11 | WHITLEY | Contaminated material from an abandoned oil well at Station 2+531 was discovered during excavation operations for a triple barrel culvert. Three other abandoned oil wells were also encountered from Station 2+550 to Station 2+900. | The Contractor excavated , removed , and disposed the contaminated material left from an abandoned oil well at Station 2+531. The three other wells were capped with concrete.
2012-01-31 | Geotechnical | Sinkhole | NEW ROUTE(O) | 11 | KNOX | Multiple sinkholes were encountered at Sta. 11+400 , 16+400 and 17+180. This is always a problem in this area and is very difficult to discover until construction. | The sinkholes had to be cleaned out via Change Order. In areas such as this , it was recommended that extensive geotechnical work be performed. This may have helped in the early detection of caves and sinkholes.
2012-01-31 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Swampy conditions were encountered on KY 6 at approximate Station 52+00. The water table in this area was very near the surface and needed to be lowered so the subgrade could be stabilized. A 24 inch concrete culvert pipe was installed at this location | A lump sum payment was made to reimburse the Contractor for performing earth work to remove the unstable material.
2012-01-31 | Construction | Subsurface | NEW ROUTE(O) | 11 | KNOX | Soft areas were encountered during construction. | Additional quantities of Roadway Fill Granular Embankment and Geotextile Fabric Type III were used to create working platforms. One area was reinforced with fabric and a two foot lift of rock. When the Contractor drilled the area from Sta. 16+850 to St
2012-01-31 | Drainage | Error | RELOCATION(O) | 11 | WHITLEY | There was an issue at approximate Station 3+050 with getting runoff from a ditch to a cross drain added at this location. The metal end section would not properly accept runoff since the cross drain was perpendicular to the roadway. | A Drop Box Inlet Type 3 was added to take runoff from the ditch to the cross drain.
2012-01-31 | Right-of-Way | Private Utilities | PAVEMENT REHAB-INT(P) | 11 | WHITLEY | Private gas lines that crossed the mainline of the proposed project at several locations were not identified on the utility plans during the planning stage. While the utility companies had relocated their lines , these privately owned gas lines were not | Relocation of the gas distribution lines , encasement pipe , and tie ins was performed in accordance with KY 2008 Standard Specifications for Road and Bridge Construction , standard gas industry specifications , and applicable KRS and KRA statutes per
2012-01-31 | Erosion Control Plan | Seeding | NEW ROUTE(O) | 11 | KNOX | Crown Vetch was initially set up for erosion control. During construction , concerns arose that Crown Vetch would not offer a strong enough root system in the sandy soils located on the project. | It was decided to change the Crown Vetch to Sericea Lespediza. This ground cover offers a stronger root system in sandy soils. This item needs to be looked at closer on future projects within this area. The Sericea Lespediza should be used on future pr
2012-01-31 | Design | Omission | RELOCATION(O) | 11 | JACKSON | The need to adjust the crash wall heights at both shoulder piers of the KY 296 underpass was overlooked. The other bridges on this project lacked existing crash walls so the bid item was set up for pouring new walls. Walls on the KY 296 underpass , on | This oversight might have been caught by more thorough review of the plans , which time constraints did not allow. The height was adjusted by attaching additional concrete using dowel bars embedded into the existing walls.
2012-01-19 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 8 | LINCOLN | There were safety concerns regarding the detours required by this project. | The Contractor was reimbursed for placement and removal of temporary guardrail needed for safety purposes on the detours.
2012-01-19 | Drainage | Error | RECONSTRUCTION(O) | 8 | LINCOLN | There was a drainage problem caused by a 48 pipe at Station 1031+00 emptying into the barrel of a culvert. | A 48 junction box was added at the outlet end of the 48 pipe in order to have the pipe empty into the wing of culvert instead of the barrel.
2012-01-19 | Drainage | Drop Box Inlets | NEW ROUTE(O) | 8 | PULASKI | There were concerns regarding the amount of maintenance needed to keep proposed Drop Box Inlets clear. | The Drop Box Inlets were changed to Slope and Flare Inlet-Outlets due to reduce the amount of debris accumulation and to allow for easier maintenance clean outs.
2012-01-19 | Drainage | Drop Box Inlets | NEW ROUTE(O) | 8 | PULASKI | There were concerns regarding the amount of maintenance needed to keep proposed Drop Box Inlets clear. | The Drop Box Inlets were changed to Slope and Flare Inlet-Outlets due to reduce the amount of debris accumulation and to allow for easier maintenance clean outs.
2012-01-19 | Drainage | Pipes | RECONSTRUCTION(O) | 8 | LINCOLN | The plans showed bituminous coated pipe , but an incorrect bid item was set up in the plans resulting in the wrong type of pipe. | A Change Order was approved to install bituminous-coated pipes in lieu of non-coated types.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | Inadequate traffic control was set up for the bridges on the project. | Temporary removable tape was applied to the bridges for traffic control.
2012-01-19 | Geotechnical | Slides | RECONSTRUCTION(O) | 8 | LINCOLN | Two slides occurred during construction of the project. | A Change Order was approved for 50 , 000 cubic yards of roadway excavation.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | Items necessary to maintain traffic at the US 23 southbound intersection were not included in the plans. | Roadway resurfacing and striping were established. Arrows and stop bars were added to properly direct traffic.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | Items necessary to maintain traffic at the US 23 southbound intersection were not included in the plans. | Roadway resurfacing and striping were established. Arrows and stop bars were added to properly direct traffic.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | Inadequate traffic control was set up for the bridges on the project. | Temporary removable tape was applied to the bridges for traffic control.
2012-01-19 | Environmental | Wells | RECONSTRUCTION(O) | 8 | LINCOLN | Gas and water wells encountered within the project area were not discovered until construction. | A Change Order was approved to provide for the plugging of these wells.
2012-01-19 | Design | Shelved Plans | RECONSTRUCTION(O) | 8 | LINCOLN | Some guardrail on the project did not conform to the current Standard Drawings and Safety Regulations. | Type I End Treatment was added to conform to the current standards and regulations.
2012-01-19 | Pavement | Coordination | RECONSTRUCTION(O) | 8 | LINCOLN | The pavement design of the project did not match adjoining projects. Other nearby projects were designed as Superpave due to extreme heavy truck traffic in the area. | A Change Order was issued to change the pavement design of the project to Superpave.
2012-01-19 | Design | Quantities | RECONSTRUCTION(O) | 8 | LINCOLN | Crushed Stone Base (CSB) for the shoulders was left out of the plan quantities and there was a mistake in the calculations for the area of mainline. CSB shoulders were also added to the KY 199 and Coburn Branch approaches. | Quantities of CSB were added by Change Order.
2012-01-19 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 8 | PULASKI | There were insufficient quantities set up in the plans to maintain the detour and various entrances throughout the project. | An additional quantity of Traffic Bound Base was added.
2012-01-19 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 8 | PULASKI | There were insufficient quantities set up in the plans to maintain the detour and various entrances throughout the project. | An additional quantity of Traffic Bound Base was added.
2012-01-19 | Design | Coordination | NEW ROUTE(O) | 8 | PULASKI | The Division of Planning requested that a data collection system be added. | Pay items associated with this work were added to the contract.
2012-01-19 | Design | Coordination | NEW ROUTE(O) | 8 | PULASKI | The Division of Planning requested that a data collection system be added. | Pay items associated with this work were added to the contract.
2012-01-19 | Design | Safety | RECONSTRUCTION(O) | 8 | LINCOLN | An existing box on a KY 199 approach posed a safety concern because it did not have any crates. | The Contractor was reimbursed for building a 24 Double Safety Box on the KY 199 approach.
2012-01-19 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 8 | PULASKI | An exposed mud seam was encountered on the high wall adjacent to the cut area along the ramp. | An electric pole had to be relocated and additional quantities of roadway excavation were needed. This hazardous condition was corrected by removing unstable material.
2012-01-19 | Geotechnical | Mine | RECONSTRUCTION(O) | 8 | LINCOLN | A vent was encountered in an existing Raul Coal mine located on US 119 Connector No. 2. The depth of the mine vent was 240 feet. | The vent was required to be plugged as per the M.S.H.A regulations.
2012-01-19 | Right-of-Way | Easements | RECONSTRUCTION(O) | 8 | LINCOLN | Some existing concrete steps and septic system were overlooked by Right-of-Way when the easement was obtained. | A Change Order was approved to add the existing concrete steps and septic system.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | The plans did not address striping removal on the transition area for detours. | Blackout paint was added to blackout the striping.
2012-01-19 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 8 | LINCOLN | Central Office instructed the Contractor to provide effective Erosion Control measures. | Channel Lining Class II was added for slope ditches of the 4 Edge Drains and for permanent silt checks in the ditches.
2012-01-19 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 8 | PULASKI | An exposed mud seam was encountered on the high wall adjacent to the cut area along the ramp. | An electric pole had to be relocated and additional quantities of roadway excavation were needed. This hazardous condition was corrected by removing unstable material.
2012-01-19 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 8 | PULASKI | The plans did not address striping removal on the transition area for detours. | Blackout paint was added to blackout the striping.
2012-01-19 | Drainage | Diversion Drainage | RECONSTRUCTION(O) | 8 | LINCOLN | There were concerns regarding possible discharge from two mine openings that were encountered during Phase I of the project. | Two parallel lines of non-perforated and perforated 8 pipes were added to carry the possible discharge away.
2012-01-19 | Drainage | Omission | NEW ROUTE(O) | 8 | PULASKI | There was insufficient drainage set up on this project. | The project phasing was revised , allowing Drainage Blanket to be added. Quantities for perforated and non-perforated pipe , concrete for pipe headwalls , and Asphalt Drainage Blanket Type II were established via Change Order.
2012-01-19 | Drainage | Omission | NEW ROUTE(O) | 8 | PULASKI | There was insufficient drainage set up on this project. | The project phasing was revised , allowing Drainage Blanket to be added. Quantities for perforated and non-perforated pipe , concrete for pipe headwalls , and Asphalt Drainage Blanket Type II were established via Change Order.
2012-01-19 | Drainage | Temporary Drainage | RECONSTRUCTION(O) | 8 | LINCOLN | There was insufficient temporary drainage established in the median at Station 1137+50 to allow drainage of the cut until Detour No. 1 could be removed. | A junction box was added in the median at Station 1137+50 via Change Order.
2012-01-19 | Design | Adjacent Projects | RECONSTRUCTION(O) | 8 | LINCOLN | Construction of US 119 Connector No. 2 was not originally included in this project. Since mainline excavation was included in this project the cut would have to be broken down twice. | The decision was made by Central Office to add Connector No. 2 to this project. The Department felt that adding this Connector now would save money because the cut would not have to be broken down twice.
2012-01-19 | Maintenance of Traffic | Changes | NEW ROUTE(O) | 8 | PULASKI | There was a change in the detour construction on this project. | As a result of this change , quantities of Temporary Concrete Median Barrier and Crash Cushions were deleted from the contract.
2012-01-19 | Maintenance of Traffic | Changes | NEW ROUTE(O) | 8 | PULASKI | There was a change in the detour construction on this project. | As a result of this change , quantities of Temporary Concrete Median Barrier and Crash Cushions were deleted from the contract.
2012-01-19 | Design | Entrance | NEW ROUTE(O) | 8 | PULASKI | There were insufficient items set up needed to maintain temporary entrances throughout the project. | Guardrail was needed to maintain the temporary entrances.
2012-01-19 | Design | Entrance | NEW ROUTE(O) | 8 | PULASKI | There were insufficient items set up needed to maintain temporary entrances throughout the project. | Guardrail was needed to maintain the temporary entrances.
2012-01-19 | Geotechnical | Slides | RECONSTRUCTION(O) | 8 | LINCOLN | There was uncontrolled runoff coming from a slide area at Station 1114+00. | The pipe at Station 1116+75 was moved to Station 1114+00 and changed to 24 in order to handle the runoff.
2012-01-19 | Geotechnical | Slides | RECONSTRUCTION(O) | 8 | LINCOLN | An existing slide on US 119 presented a safety hazard to the traffic. | The damage to the roadway was repaired using railroad rails , which required drilling to place the rails , cribbing , excavation , and backfill.
2012-01-19 | Design | Shelved Plans | RECONSTRUCTION(O) | 8 | LINCOLN | The Guardrail End Treatments were designed before Design Memo 10-98 was written. | A Change Order was issued to upgrade Guardrail End Treatment Type 4A to Revised Guardrail End Treatment Type 4A as per Design Memo 10-98.
2012-01-19 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 8 | LINCOLN | Items dealing with Erosion Control had to be changed in order to reflect the BMP plan that was put into effect at the time of construction. | A Change Order was approved to provide means of Erosion Control.
2012-01-19 | Design | CAP | NEW ROUTE(O) | 8 | PULASKI | A property owner requested rustic guardrail. Also , the quantity of trees planted was increased as per a request from SHPO and a Memorandum of Agreement between the property owner and the Department. | These items were added via Change Order.
2012-01-19 | Environmental | Underground Tank | NEW ROUTE(O) | 8 | PULASKI | A septic tank was discovered during excavation on the project. | A pay item was established to compensate the Contractor for the removal of this tank.
2012-01-19 | Environmental | Underground Tank | NEW ROUTE(O) | 8 | PULASKI | A septic tank was discovered during excavation on the project. | A pay item was established to compensate the Contractor for the removal of this tank.
2012-01-19 | Design | CAP | NEW ROUTE(O) | 8 | PULASKI | A property owner requested rustic guardrail. Also , the quantity of trees planted was increased as per a request from SHPO and a Memorandum of Agreement between the property owner and the Department. | These items were added via Change Order.
2012-01-19 | Drainage | Temporary Drainage | RECONSTRUCTION(O) | 8 | LINCOLN | There was inadequate temporary drainage control set up across the northbound lanes at Station 1137+00. | A temporary pipe was added across the northbound lanes at Station 1137+00 until the final pipe could be laid.
2012-01-19 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 8 | LINCOLN | There were concerns about the need to warn southbound traffic of an upcoming curve on the project. | A variable message board was added to warn traffic of the curve. The message board became the property of the Department after project completion.
2012-01-19 | Drainage | Omission | RECONSTRUCTION(O) | 8 | LINCOLN | There was insufficient drainage set up in the plans. | Edge drains and drainage blankets on both shoulders were added throughout the project limits.
2012-01-19 | Design | Adjacent Projects | RECONSTRUCTION(O) | 8 | LINCOLN | There were concerns that the design of five concrete median barriers would conflict with the next project. | A Change Order was approved for the addition of the bottom phase of boxes to five concrete median barriers to eliminate any conflict.
2012-01-19 | Design | Omission | NEW ROUTE(O) | 8 | PULASKI | Items needed to connect guardrail along the roadway to the Bridge Ends were not established in the plans. | Guardrail Connectors to Bridge Ends were added.
2012-01-19 | Design | Omission | NEW ROUTE(O) | 8 | PULASKI | Items needed to connect guardrail along the roadway to the Bridge Ends were not established in the plans. | Guardrail Connectors to Bridge Ends were added.
2012-01-19 | Utilities | New Utilities | RECONSTRUCTION(O) | 8 | LINCOLN | Several homes had been obtaining their water supply from an abandoned mine that became dry when the contractor excavated material from the cut Right of Station 1115+00 to 1120+00. | An agreement was made with the Contractor to install water line to connect the water supply of these homes to Mountain Water District.
2012-01-19 | Design | Omission | RECONSTRUCTION(O) | 8 | LINCOLN | An item for crash cushion pads as per Standard Drawing No. RBE-060-09 was not set up on the project. | A Change Order was established to add Class AA Concrete to construct the crash cushion pads.
2012-01-19 | Drainage | Elevation | RECONSTRUCTION(O) | 8 | LINCOLN | The top of an existing 48 cross drain pipe at Station 1143+25 was too high after the vertical alignment at that location was changed from super-elevation to tangent section. | Fifty linear feet of the pipe was removed in order to tie the remaining length of the pipe in with a junction box connected by 12' pipe to a modified Sloped and Flared Box Inlet-Outlet that was installed.
2012-01-19 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 8 | LINCOLN | Construction of the KY 199 approach rendered the existing 8 ductile iron pipe too deep. | The existing 8 ductile iron pipe was replaced with a steel encasement pipe.
2012-01-19 | Drainage | Drop Box Inlets | RECONSTRUCTION(O) | 8 | LINCOLN | An approach where slotted drains were used needed to be changed. | The existing Drop Box Inlet Type 12 were replaced with Type 12A.
2012-01-19 | Drainage | Omission | NEW ROUTE(O) | 8 | PULASKI | Water was seeping into the roadway at the base of a cut. | Perforated pipe was added to assist in the drainage of this area.
2012-01-19 | Utilities | Communication | RECONSTRUCTION(O) | 8 | LINCOLN | The original relocation of a waterline was determined to be unacceptable by the Water Company. | The subsequent relocation of the water line , as required by the Water Company , necessitated use of a booster pump for which the Contractor was compensated.
2012-01-19 | Drainage | Omission | NEW ROUTE(O) | 8 | PULASKI | Water was seeping into the roadway at the base of a cut. | Perforated pipe was added to assist in the drainage of this area.
2012-01-19 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 8 | LINCOLN | The earth material in the project area suffered from poor geologic characteristics. | Additional quantities of roadway excavation were added to correct a number of slides , make slope revisions , and undercut various areas.
2012-01-19 | Erosion Control Plan | Omission | NEW ROUTE(O) | 8 | PULASKI | Items needed for Slope Protection and Erosion Control were not included in the original plans. | Number 2 Aggregate Slope Protection and Erosion Control Items were added by Change Order.
2012-01-19 | Traffic | Safety | RECONSTRUCTION(O) | 8 | LINCOLN | There were concerns regarding traffic speeds in the southbound lane near Station 1033+00. | Rumble strips were added at Station 1033+00 to slow traffic in the southbound lane.
2012-01-19 | Erosion Control Plan | Omission | NEW ROUTE(O) | 8 | PULASKI | Items needed for Slope Protection and Erosion Control were not included in the original plans. | Number 2 Aggregate Slope Protection and Erosion Control Items were added by Change Order.
2012-01-05 | Construction | Revisions | MAJOR WIDENING(O) | 10 | PERRY | The original project was not in accordance with the Empower Rest Area program. | A Change Order was issued to add all items and materials necessary to construct truck parking areas and restrooms as per a Construction Revision.
2012-01-05 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | There were safety concerns regarding a drop off at a cemetery located from station 765+26 to 767+20. Failure to address this situation was caused by an omission during the plan development process and was exacerbated by inaccuracies in the digital terrai | Quantities for a chain link fence to be installed at the cemetery were added via Change Order.
2012-01-05 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 10 | PERRY | Erosion Control items were not included in the original contract as the project was let prior to the effective date of the Erosion Control guidelines of Design Memo No. 8-98. | Erosion Control items such as Silt Fence and Straw Bales , which were necessary to provide adequate erosion control were added.
2012-01-05 | Construction | Safety | BRIDGE REPLACEMENT(P) | 10 | PERRY | In fall 2007 , fractures in the rock ledges along existing KY 7 were worsening at various locations between STA 696+00 and STA 700+00 within the work zone. Months of blasting and excavation were thought to be contributing factors and safety concerns bec | The existing route was closed for three days so the Contractor could remove as much overhanging rock as possible using a hoe ram. The existing route was bedded and used as a platform to perform the work in a manner that was amenable to CSX railroad , wh
2012-01-05 | Drainage | Pipes | BRIDGE REPLACEMENT(P) | 10 | PERRY | As per the plans , approximately 163 feet of 42 inch pipe was to be installed at Station 719+00 on the slope leading from the new KY 7 and tying into an existing culvert under old KY 7. Upon field review , it was determined this excessive length of pip | The Contractor was compensated for the unneeded culvert pipe at invoice price and the culvert pipe was delivered to the Perry County State Maintenance Facility where it became property of KYTC.
2012-01-05 | Utilities | Communication | MAJOR WIDENING(O) | 10 | PERRY | There was a potential conflict between the proposed location of the conduit providing power and communication to the Advantage 75 equipment and a future three lane I-75 widening project. | The planned location of the conduit was changed via Change Order.
2012-01-05 | Design | Median | MAJOR WIDENING(O) | 10 | PERRY | The island design for separating the scale and bypass lanes at both the Northbound and Southbound weight stations wouldn't provide adequate traffic flow or positive lanes separation according to Motor Vehicle Enforcement. | The islands were modified to installation of 4-inch raised island in lieu of a flush median between the lanes.
2012-01-05 | Pavement | Repair | BRIDGE REPLACEMENT(P) | 10 | PERRY | Blast debris from a side hill cut throughout the project damaged existing pavement. Difficulties arising from trying to build a new road while maintaining an existing one is a common problem and presents a grey area for inspectors. When work is being pe | A bid item specifically for patching and repairs during construction would be beneficial. For this situation , Asphalt surface was used to patch various locations along existing KY 7 as necessary.
2012-01-05 | Geotechnical | Slides | BRIDGE REPLACEMENT(P) | 10 | PERRY | Multiple slides occurred on the project due to heavy rains and existing problems exacerbated by construction. | The material from the slides caused by rain could not be hauled to the waste area because water was above the haul road. This slide material had to be stockpiled and then removed later. In the case of the larger slide , excavation was performed until s
2012-01-05 | Right-of-Way | Easements | MAJOR WIDENING(O) | 10 | PERRY | The Cabinet lacked an easement that was needed to tie the force main into the existing sanitary sewer manhole. | The Contractor was reimbursed for acquiring the easement.
2012-01-05 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | A bid item for Guardrail Removal was not included in the contract plans. | A Constructability Review may have caught this omission.
2012-01-05 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 10 | PERRY | A 24-inch pipe and a 15-inch pipe that were not shown on the plans were discovered. | A Change Order was approved to extend these pipes.
2012-01-05 | Drainage | Temporary Drainage | BRIDGE REPLACEMENT(P) | 10 | PERRY | A roadway failure occurred at approximate station 664+00 due to excessive rain running across KY 7. This location was at the transition point of the roadway template , meaning this area was to be disturbed little , if any , due to the new roadway cons | A Constructability Review may have identified a need for temporary drainage. In this case , the Contractor immediately began to divert water from running across KY 7. Additionally , shot material lying adjacent to the roadway was moved to create the c
2012-01-05 | Pavement | Coordination | MAJOR WIDENING(O) | 10 | PERRY | The asphalt pavement of both the northbound and southbound Loadometer ramps did not match the adjacent six-lane mainline construction. | A Change Order was approved to modify the asphalt pavement to coordinate and match ramp construction to the adjacent six-lane mainline construction.
2012-01-05 | Utilities | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | A gas line located at Sam Combs Road supplying Parcel 166 was omitted from the plans and was not spotted on any set causing an overrun of this item. | Additional quantities were established via Change Order.
2012-01-05 | Design | Alignments | MAJOR WIDENING(O) | 10 | PERRY | The horizontal and vertical alignment of both the northbound and southbound Loadometer ramps did not match the adjacent six-lane mainline construction. | A Change Order was approved to modify the horizontal and vertical alignments of both ramps.
2012-01-05 | Design | Omission | MAJOR WIDENING(O) | 10 | PERRY | Several items were depicted on the plans but not included in the bid items. | Pavement Striping , Tubular Markers , Handicap Logo , and Concrete Class AA needed for the installation of Type 7 Crash Cushions were added.
2012-01-05 | Erosion Control Plan | Quantities | BRIDGE REPLACEMENT(P) | 10 | PERRY | There were insufficient plan quantities for items such as erosion control blanket , silt fence , and seeding. | Additional quantities of these items were added through Change Order.
2012-01-05 | Utilities | Pipe Sizes | MAJOR WIDENING(O) | 10 | PERRY | The original elevation of the inverts at the northbound and southbound pump stations were too high for the collector pipes to allow gravity flow above the high water elevation. Also , the original diameter of the wet wells were too small to house the pu | The pump stations were modified by increasing the diameter of the wet wells from 4 ft to 6 ft and lowering the invert approximately 4 ft. The larger diameter also provided additional storage , which was required by restroom addition.
2012-01-05 | Utilities | Inaccurate Location | BRIDGE REPLACEMENT(P) | 10 | PERRY | Due to major waterline location issues , like waterlines not being spotted correctly on the plans , delays were encountered. | The number of Working Days on this project was extended and the waterline contractor had to perform exploratory digging in order to locate the lines.
2012-01-05 | Erosion Control Plan | Quantities | BRIDGE REPLACEMENT(P) | 10 | PERRY | There was an insufficient quantity of Erosion Control Blanket , which was needed to cover the back slopes of large cut sections throughout the 2.5 mile project where slopes were steeper than the 4:1 threshold. | An additional quantity of erosion control blanket was added and the original seeding and protection bid item was decreased by the same quantity.
2012-01-05 | Utilities | Omission | MAJOR WIDENING(O) | 10 | PERRY | Six-inch PVC sewer and cleanout lines were depicted on the plans but these bid items were not included in the contract. | Unit prices for these items were established and they were added via Change Order. Also , a Manhole Type A was added to collect these services and consolidate them into one pipe on the Northbound site in order to provide more efficient maintenance.
2012-01-05 | Utilities | Relocation | MAJOR WIDENING(O) | 10 | PERRY | There were concerns regarding an undesirable utility pole located in the median. | A raceway for underground electrical primary was constructed to eliminate the need for overhead lines.
2012-01-05 | Design | Plans | MAJOR WIDENING(O) | 10 | PERRY | Due to a plan error , the Northbound Loadometer Building was constructed in an unusable location. | The Northbound Loadometer Building was reconstructed to the correct orientation and location. A Change Order covered the labor and equipment cost to demolish the structure. All salvageable items , such as roof trusses , enforcement room beams , and w
2012-01-05 | Design | Sight Distance | BRIDGE REPLACEMENT(P) | 10 | PERRY | There were safety concerns regarding a dangerous sight distance hazard at the intersection of KY 1165 and KY 1166. | Excavation limits along KY 1165 were extended in order to eliminate the sight hazard at this intersection. The change was initiated by District Design Personnel as it became apparent this was a contract omission. Additional work included removal of exca
2012-01-05 | Design | Omission | MAJOR WIDENING(O) | 10 | PERRY | Several necessary items had not been specified in the original contract. | High-water alarms for scale equipment protection , high power (100-Watt) jar lights , ground fault receptacles , and all required items such as switches , conduit , circuit breakers , and the necessary wiring to provide lighting and electrical acces
2012-01-05 | Design | Railroads | BRIDGE REPLACEMENT(P) | 10 | PERRY | There was a lack of communication with the adjacent railroad. KYTC had recently revised their coordination policy with communication being handled via a Consultant instead of directly with the trackmasters. Additionally , CSX did not attend the Pre-Con | If a job requires railroad involvement , a thorough discussion should occur before the Pre-Construction meeting. Even if a project does not encroach upon the railroad's Right-of-Way it may potentially impact them. Railroads need to be made aware of pot
2012-01-05 | Design | Drainage | BRIDGE REPLACEMENT(P) | 10 | PERRY | According to the plans , the roadway water was to sheet flow to the railroad Right-of-Way. In order to avoid jeopardizing the KY 7 embankment and causing damage to CSX property , it was decided to devise a way to contain the water. | A roadway ditch from station 660+00 to 665+00 RT was constructed to keep water off the railroad Right-of-Way. Additional quantities of Channel Lining Class II and grout were required to stabilize the ditch.
2012-01-05 | Construction | Revisions | BRIDGE REPLACEMENT(P) | 10 | PERRY | The waterline plan set , developed before Right-of-Way negotiations , included an 8 inch line that ran the entire length of the job. However , most of the homes on this line had been acquired and removed during Right-of-Way negotiations. | District 10 Project Development and Construction Branches determined that significant savings could be achieved by revising the contract waterline plan set. It was determined that only a 3 inch line was needed at the Viper end of the job and an 8 inch li
2012-01-05 | Design | Quantities | BRIDGE REPLACEMENT(P) | 10 | PERRY | Many locations had no channel lining noted on the plans or had inadequate quantities listed. Additional quantities were also needed in order to stabilize some ditch line/embankment areas. | Additional quantities of Channel Lining Class IV were added via Change Order. A more thorough review of the plans and quantities or possibly a Constructability Review would have likely identified this issue.
2012-01-05 | Design | Grade | BRIDGE REPLACEMENT(P) | 10 | PERRY | Design plans did not address how to tie a very steep approach into the mainline. | Extra attention needs to be paid to approaches with 15-20% slopes because without room for realignments or grade changes they can become 25-30% slopes. In this case , an S curve was added to the approach in order to add length and decrease the slope. I
2012-01-05 | Pavement | Repair | BRIDGE REPLACEMENT(P) | 10 | PERRY | The pavement was padded with dirt prior to the hoe ram utilization for rock overhang removal , but large equipment and heavy loads still caused damage to the old pavement. | Additional quantities of asphalt base were utilized for repair and minor widening of existing KY 7 between STA 696+00 and 700+00.
2012-01-05 | Design | Access | BRIDGE REPLACEMENT(P) | 10 | PERRY | The approaches and drainage at the Ponderosa Drive Subdivision and Rest Haven Cemetery were constructed per plan. However , once constructed , it was obvious that corrections needed to be made in order to access the cemetery. | The approaches to Rest Haven Cemetery and Ponderosa Drive were both reconstructed and widened , in addition to corrective drainage revisions. This work was approved by District and Central Office personnel.
2012-01-05 | Materials | Backfill | BRIDGE REPLACEMENT(P) | 10 | PERRY | The plans specified the use of a proprietary lightweight foaming fill. Due to a disconnect between Design , Construction , and Materials , plans occasionally include materials that are extremely special in nature. In this instance , the lightweight | The plans should have been less restrictive in order to avoid dictating the use of such a rare and unique material. In this particular case involving a roadway fill , experimentation would not have been desirable. Instead , the Contractor requested an
2012-01-05 | Construction | ROW | BRIDGE REPLACEMENT(P) | 10 | PERRY | A major safety issue arose from leaving a little island of houses after the Right-of-Way acquisitions. These houses were located at the lowest point under a slope near where cuts and blasting were being performed and there was insufficient room for a fal | These properties should have been purchased during Right-of-Way negotiations or the road should have been realigned slightly so the they could have been legally taken.
2012-01-05 | Design | Lighting | MAJOR WIDENING(O) | 10 | PERRY | The planned lighting for the rest area did not provide adequate illumination. | The height of the high mast lighting systems (luminaries) was increased from 100 ft to 120 ft and four luminaries were moved to the perimeter of the parking area in order to maximize the projected area of illumination.
2011-12-19 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 9 | CARTER | There was no traffic bound base included in the bid items for maintenance of local traffic and entrances while mainline embankments were constructed. The original Contract was only set up with an item for DGA. It was also mentioned that there are common | This omission could have been noticed with additional review of the MOT plans/notes. While drafting MOT notes , designers need to be aware of the difference between maintenance stone and DGA. Some district personnel stated a preference that the size of
2011-12-19 | Right-of-Way | Omission | RECONSTRUCTION(O) | 9 | CARTER | The Contractor uncovered two septic tanks during grade construction at station 281+00 and 283+00. These should have been identified during the Right-of-Way phase. | More thorough field inspections or increased communication with local property owners during the Right-of-Way phase might have discovered this oversight. The Contractor had the tanks pumped before removing them.
2011-12-19 | Structures | Omission | RECONSTRUCTION(O) | 9 | CARTER | The total epoxy coated steel reinforcement quantity shown on Northbound Bypass Bridge Plans for the superstructure was incorrect. The rebar quantity shown on layout sheet was not copied over to be included in bill of reinforcement sheet for this structur | This oversight could have been prevented with a more thorough QA/QC check. Instead the plan quantity needed to be increased via Change Order to correct the plan omission.
2011-12-19 | Structures | Omission | RECONSTRUCTION(O) | 9 | CARTER | The total epoxy coated steel reinforcement quantity shown on Ringgold Road Bridge Plans for the superstructure was incorrect. The rebar quantity shown on layout sheet was not copied over to be included in bill of reinforcement sheet for this structure. | This oversight could have been prevented with a more thorough QA/QC check. Instead the plan quantity needed to be increased via Change Order to correct the plan omission.
2011-12-19 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 9 | CARTER | The existing water main along Hacker Rd. was 8 inch pipe instead of 6 inch pipe as shown on utility plans. | Therefore 8 inch tie-in items were added to connect the newly relocated water main to existing water main and the 6 inch quantities were deleted. More accurate utility information is needed.
2011-12-19 | Structures | Omission | RECONSTRUCTION(O) | 9 | CARTER | The total steel reinforcement quantity shown on for Abutment #2 on Ringgold Rd. Bridge was incorrect. The rebar quantity shown on layout sheet was not copied over to be included on the bill of reinforcement sheet for this structure. | This oversight could have been prevented with a more thorough QA/QC check. Instead the plan quantity needed to be increased via Change Order to correct the plan omission.
2011-12-19 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 9 | CARTER | Addendum #1 issued on October 10 , 2007 revised sheet R2m which included the quantities for rock embankment. This sheet showed a need for 251 , 148 cubic yards of rock embankment to be provided by rock excavation of 609 , 532 available cubic yards. How | Approximately 110 , 000 additional cubic yards of rock roadbed material were needed and had to be hauled from beyond the project limits. This was unavoidable barring more accurate geotechnical information.
2011-12-19 | Drainage | Elevation | RECONSTRUCTION(O) | 9 | CARTER | A proposed ditch profile would have conflicted with the location of a planned concrete box culvert. As shown in the plans , the ditch would be too low to align with the box culvert outlet. | This issue may have been identified with by more thorough QA/QC or perhaps a Constructability Review. Instead , the box was raised , which required a waterline to be rerouted below it contrary to the original design.
2011-12-19 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 9 | CARTER | The temporary concrete median barrier on Louie B. Nunn Parkway needed to be relocated to a different location for the median crossover diversion , but no bid item was established. | These omissions could have been caught with additional plan review , perhaps a Constructability Review.
2011-12-19 | Design | Intersection | RECONSTRUCTION(O) | 9 | CARTER | An opportunity was identified to apply a practical solutions approach to the proposed interchange configuration connecting the Louie B. Nunn Parkway to the new Southwest Bypass (KY 914) , which included a bridge over KY 914. | A construction revision was made to change the proposed connection from an interchange to an at-grade signalized intersection , which resulted in approximately $2 , 500 , 000 in savings for the Cabinet.
2011-12-19 | Design | Adjacent Projects | RECONSTRUCTION(O) | 9 | CARTER | High mast roadway lighting was supposed to be installed at the interchange of newly constructed Somerset Northern Bypass (I-66) and US 27 during a separate project. However , US 27 traffic will use a portion of this interchange until the next portion of | The high mast lighting was added via Change Order and installed for safety purposes. This apparent disconnect might have been identified by a Constructability Review.
2011-12-19 | Drainage | Omission | RECONSTRUCTION(O) | 9 | CARTER | The KY 914 Bridge crossing the project was constructed with a normal crown while the approach roads were constructed as super elevated sections , but there was no drainage set up to catch the water coming off the bridge. | Improved coordination between roadway and structure designers is needed , otherwise increased plan scrutiny or a Constructability Review may have identified this omission.
2011-12-19 | Design | Communication | RECONSTRUCTION(O) | 9 | CARTER | During excavation , a cavity was discovered in the vertical rock face of Abutment #2. The geotechnical report did not address this situation due to differences between the roadway and bridge designs. The geotechnical investigation was based on a propos | Improved coordination between roadway and structure designers is needed , otherwise a Constructability Review may have identified the discrepancy. Class B Concrete was added to construct a gravity type retaining wall at Abutment #2 to prevent the footin
2011-12-19 | Design | Sight Distance | RECONSTRUCTION(O) | 9 | CARTER | There was a sight distance problem at the new intersection of Cedar Hill Lane and KY 3261 (S. Hacker Rd). | This intersection was adjacent to mainline construction and may not have been evaluated for sight distance issues. Sight distances should be scrutinized at all proposed intersections.
2011-12-19 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 9 | CARTER | While excavating the footings for Abutment #1 and #2 of the Ringgold Rd. Bridge , solution channels were encountered. | This may or may not have been identified with additional geotechnical coring , but these conditions are common to this part of the state. The voids were cleaned and filled with mass concrete.
2011-12-19 | Design | Adjacent Projects | RECONSTRUCTION(O) | 9 | CARTER | There were three different designers for adjacent projects that were sections of the same road. Consequently , the ends of this project did not properly tie into the adjacent projects; the vertical alignment on one end was off by a foot. Pavement desig | The Cabinet no longer uses project datum factors which may help reduce some alignment issues. Additionally , there needs to be increased coordination between designers of adjacent projects. Lastly , this issue might have been determined in advance by
2011-12-19 | Structures | Plans | RECONSTRUCTION(O) | 9 | CARTER | There was a lack of information regarding the fascia offset and radial information on the Ringgold Bridge plans. | A more thorough QA/QC review of the structure plans may have identified these oversights.
2011-12-19 | Design | Median | RECONSTRUCTION(O) | 9 | CARTER | There were discrepancies with the plan median widths. The cross sections showed the current width and the typical sections showed an incorrect median width (40 ft instead of 60 ft). There were also problems with the underdrain plans caused by incorrect | This issue may have been identified with by more thorough QA/QC or perhaps a Constructability Review.
2011-12-19 | Design | Omission | RECONSTRUCTION(O) | 9 | CARTER | The flow line of culvert at Sta. 282+71 required solid rock be excavated to get culvert to plan grade. There was a solid rock excavation item set up for a bridge but not for this particular culvert. | The item for rock excavation on this culvert was simply omitted from the plans , there was no geotechnical note for this location but the rock was clearly visible so this item should have been addressed in the plans.
2011-12-19 | Right-of-Way | Omission | RECONSTRUCTION(O) | 9 | CARTER | Two water wells located near mainline station 238+10 @ 112' Rt. and mainline station 291+55 @ 120' Rt. were discovered during clearing and grubbing. These wells were overlooked during the Right-of-Way phase. | More thorough field inspections or increased communication with local property owners during the Right-of-Way phase might have discovered this oversight. The wells were plugged and sealed in accordance with State regulations.
2011-12-19 | Maintenance of Traffic | Lane Closures | RECONSTRUCTION(O) | 9 | CARTER | Excessive maintenance efforts were required to repair and replace damaged tubular markers that were being used to separate opposing traffic while it was shifted onto one side of parkway. | Unless visual delineation is imperative for safety , rumble strips offer a viable alternative. Using rumble strips in conjunction with tubular markers may also reduce the frequency of damage and thus the effort needed to maintain them.
2011-12-19 | Right-of-Way | CAP | RECONSTRUCTION(O) | 9 | CARTER | Entrance locations that were agreed to during Right-of-Way were not included in the CAP notes , which caused additional work for the grading Contractor. | Right-of-Way negotiators need to be more thorough about documenting the concessions they make.
2011-12-19 | Design | Omission | RECONSTRUCTION(O) | 9 | CARTER | Concrete needed to construct entrances located on Ringgold Road was shown in the plans but there were no bid items established for this purpose. | This oversight could have been prevented with a more thorough QA/QC check.
2011-12-19 | Construction | Contracts | RECONSTRUCTION(O) | 9 | CARTER | The original plans called for the use of Flowable Fill to backfill the end bents at Northbound and Southbound Southwest Bypass bridges. A Change Order was approved to change the backfill to Structure Granular Backfill. However , the accepted bid price | The low bid price for flowable fill should have been identified during the construction procurement process as an unbalanced bid. In addition , the section office should have also recognized the unbalanced bid and questioned such a drastic price change.
2011-12-19 | Materials | Backfill | RECONSTRUCTION(O) | 9 | CARTER | In general , granular backfill allows better drainage while flowable fill lessens the £settlement bump¥ at the ends of bridges. | This corresponds to the bigger issue of how bridges should be designed and whether approach slabs should be used. These issues need to be considered on a case by case basis and site specific solutions should be adopted.
2011-12-19 | Geotechnical | Slides | RECONSTRUCTION(O) | 9 | CARTER | The embankment slope on Ramp 4 (US 27) was constructed on a previous project with clay fill , which had developed a major slide. | The clay fill was replaced with granular embankment. A flume inlet and concrete wedge curb were added to divert storm water runoff away from the repaired slide area to prevent a slide reoccurrence.
2011-12-19 | Traffic | Signs | RECONSTRUCTION(O) | 9 | CARTER | The only signing plans that were included in the original plans were along the newly constructed mainline Louie Nunn Parkway. There were no signing plans for the intersecting roadways , which likely added to confusion among the traveling public since th | The need for additional signage on intersecting roadways should have been foreseen. Central Office Traffic developed the signing plans , which were inserted at the end of the design process. It would be beneficial if Signing Plans could be completed ea
2011-12-19 | Drainage | Quantities | RECONSTRUCTION(O) | 9 | CARTER | There was an insufficient quantity of class II channel lining set up for this project. This was likely the result of a miscalculation that may have been exacerbated by differing preferences between design and construction. When designing a ditch , desi | A more thorough QA/QC review of the plans may have caught this quantity miscalculation.
2011-12-01 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | Temporary Guardrail was needed , but not included in the plans for phase 3 during construction. | A Constructability Review likely would have identified this oversight.
2011-12-01 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 4 | GRAYSON | It was felt that there was not enough Channel Lining set up on the project. Rock ditches in lieu of silt fences are being used in this area especially on smaller projects where there is not adequate room to work and constructability is a problem. | Additional quantities of Channel Lining should be set up when it is anticipated that rock ditches will be used in lieu of silt fences because there is inadequate work space.
2011-12-01 | Geotechnical | Slides | MAJOR WIDENING(O) | 4 | NELSON | There was a good 2:1 slope , but it was intermixed with odd rock ledges that would be difficult to detect with normal drilling. Once it rained , a slide occurred. | A rock buttress (big toe at the bottom) was constructed to prevent slide reoccurrence.
2011-12-01 | Design | Evaluations | RECONSTRUCTION(O) | 4 | GRAYSON | Some Right-of-Way markers were located in an existing driveway and near an existing county road adjacent to the project. | After examination in the field , it was decided to change the Right-of-Way markers from Rural Markers Type 1 to municipal markers.
2011-12-01 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 4 | NELSON | A fiber optic line located over top of the bridge created clearance issues , which caused construction delays. | In this case , the City is responsible for deciding when the fiber optic line above the bridge was moved. Scheduling fiber optic line relocations need to done during the design phase so the schedule can be included in the construction contract.
2011-12-01 | Design | Radius | RECONSTRUCTION(O) | 4 | GRAYSON | It is very difficult to install double posts with double rail at a sharp radius. | A suggestion was made to use either double post or double rail at these locations , but not both.
2011-12-01 | Design | Intersection | NEW ROUTE(O) | 4 | HARDIN | It is often difficult to tie curb and gutter from the mainline into an approach road unless detail sheets are available. | Designers should include detail sheets depicting how to tie curb and gutter from the mainline into an approach road in the plans. It is also worth considering including abbreviated intersection development sheets for spot elevations (beginning , middle
2011-12-01 | Design | Quantities | RECONSTRUCTION(O) | 4 | GRAYSON | Additional quantities of several items were needed due to overruns based on actual field calculated quantities. | Additional quantities of Bituminous Base , Asphalt Seal Aggregate , Emulsified Asphalt RS-2 , and Seeding and Protection were added via Change Order.
2011-12-01 | Design | Omission | MAJOR WIDENING(O) | 4 | NELSON | There was existing guardrail located from Sta. 94+00 to 98+00 that needed to be removed , but no removal bid item was set up. | Design plans , especially shelved plans , should receive a thorough QA/QC check to catch oversights such as this.
2011-12-01 | Maintenance of Traffic | Detours | RECONSTRUCTION(O) | 4 | GRAYSON | An adjacent county road located on the project had heavier than normal traffic due to the construction of a detour crossing established by the county. | Traffic Bound Base was added to the contract in order to maintain traffic entering and leaving the adjacent county road.
2011-12-01 | Utilities | Relocation | MAJOR WIDENING(O) | 4 | NELSON | This was a major grade and drain project , but none of the utilities had been relocated prior to construction because the contract for Grade and Drain was let before the Utilities contract. | Ideally , utility plans should be designed by the roadway designer and constructed by the roadway contractor. At the very least , utility plans need to be overlaid with the roadway plans to identify potential conflicts. Making utility plans available
2011-12-01 | Structures | Quantities | MAJOR WIDENING(O) | 4 | NELSON | There was an error calculating box culvert concrete quantities. | Calculations should be more closely checked.
2011-12-01 | Design | Omission | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | In accordance with Section 601.03.18 of the 2004 Standard Specifications for Road and Bridge Construction , Retaining Walls are to be finished with Masonry Coating. However , Masonry Coating was not included as a bid item for the Retaining Walls. | Designers should pay increased attention to certain requirements contained in the Specifications book.
2011-12-01 | Design | Shelved Plans | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | After the utilities were designed , the project was not let for approximately five years. During that time , the City of Leitchfield's water standards changed. According to the city and the Division of Water , water pressure in the existing line woul | A hydro-stop insertion valve was installed to allow water pressure to remain above 20 psi. Utility relocations should have been included in the cityÖs utility plans.
2011-12-01 | Design | Coordination | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | Utility poles were installed per the plans prior to a design change that altered the embankment slopes. | The utility poles had to be removed and reinstalled closer to the proposed sewer lines than anticipated. Steel encasement pipes were added to the sewer lines to minimize any potential damage caused by the utility poles.
2011-12-01 | Structures | Dimensions | MAJOR WIDENING(O) | 4 | NELSON | Double barrel culverts can cause reoccurring maintenance issues due to the tendency for debris to become affixed on the concrete divider between the two barrels. Additionally , box culverts less than four foot tall typically require increased maintenanc | When considering the use of a double barrel culvert , Designers should be mindful of their potential for blockage. The increased maintenance required by double barrel culverts may make a single barrel culvert or a bridge a better option. Also when desi
2011-12-01 | Right-of-Way | Insufficient ROW | MAJOR WIDENING(O) | 4 | NELSON | Sufficient work space , especially on or around structures , should be provided in the design. | Increased consideration should be given to providing sufficient room for construction equipment. Right-of-Way processes should include seeking solutions that enhance constructability without requiring excessive right-of-way taking. Savings during the co
2011-12-01 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | A 10 waterline that was not shown on the utility relocation plans was discovered. The waterline entered the project at Sta. 53+13 Lt. and continued to the end of the project. A proposed 6 waterline was originally included in the utility relocation plans | A Change Order added items for upgrading the proposed 6 waterline to a 10 waterline in order to maintain the same water pressure and water flow to the facilities in this area as they had before the project began.
2011-12-01 | Design | Radius | NEW ROUTE(O) | 4 | HARDIN | After construction was complete , there were turning radius issues for school buses , garbage trucks , and other large vehicles at the Lutheran Church Road approach. The original approach was wider than the newly constructed road. | A decision was made to widen the approach. The recently completed curb and gutter had to be removed and the area was restored to grade on a cost plus basis. This problem may have been identified earlier if the proper turning radius software had been use
2011-12-01 | Utilities | Plans | MAJOR WIDENING(O) | 4 | NELSON | There were concerns that not enough resources are being devoted to checking utility plans. | It would be beneficial to create additional positions within the Cabinet that are solely devoted to reviewing utility plans. At the very least , this task should be clearly assigned to specific staff members prior to construction.
2011-12-01 | Design | Specifications | RECONSTRUCTION(O) | 4 | GRAYSON | The Crushed Stone Base used on this project had too many fines and did not drain properly. | It was mentioned that gradation requirements for Crushed Stone Base and DGA need to be reviewed. It was felt that there should be a distinct difference between the gradation of these two items.
2011-12-01 | Utilities | Existing Utilities | NEW ROUTE(O) | 4 | HARDIN | The City of Bardstown hired a utility consultant to perform the Utility Relocation Plan and the Consultant mistakenly identified incorrect pipe sizes. For example , the existing force main from the hospital was actually a 4 inch line as opposed to the 1 | Designers usually have to rely on utility companies for sizes and locations of existing utilities. More accurate utility records are needed.
2011-12-01 | Structures | RCBC | MAJOR WIDENING(O) | 4 | NELSON | The plans proposed removing and replacing approximately 40 feet from each end of the existing culvert. While this is a common design , it is not necessarily appropriate especially when the culvert remains in good condition. Implementing this design wou | Rather than replacing all or part of a culvert , sometimes the best option is to leave the existing structure in place while using lightweight fill to accommodate it's extension and prevent overloading. If roadway Designers were given access to Structur
2011-12-01 | Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | Thermo Arrows required for the center turn lane at the beginning of this project were omitted from the contract. | Designers should be responsible for performing an adequate QA/QC check of their plans.
2011-12-01 | Pavement | Quantities | MAJOR WIDENING(O) | 4 | NELSON | Sufficient quantities of mainline and shoulder Asphalt Base and Surface were not included in planned quantities. The general summaries included the correct quantities , but during the transfer from plans to bid sheets the shoulder and middle turning lan | Pavement materials constitute a major portion of a projectÖs total cost. Calculations for these items need to be closely checked.
2011-12-01 | Drainage | Temporary Drainage | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | During several significant rainfalls , the newly installed 53 x 41 pipe arch was at full capacity causing water to pond on the road. The proposed drainage might have worked after the project was completed , but it was insufficient during construction b | This issue should have been identified during development of drainage calculations. Whenever the headwater is above the intermediate elevation , the drainage design should receive additional review including consideration of temporary drainage devices.
2011-12-01 | Utilities | Omission | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | Two sewer service lines were overlooked when designing the utilities. | Check valves were installed to prevent sewage back up at these locations.
2011-12-01 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | Removable Tape was omitted from the contract. This item was necessary due to temporary lanes being used on the bridge. | Increased attention should be devoted to reviewing MOT plans and this omission may have been discovered by a Constructability Review.
2011-12-01 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 4 | NELSON | The designed erosion control for the stream bank near the bridge did not work. When water levels rose they overflowed the silt fence , which prevented it from filtering properly. Additionally , since the piers were on the bank and not actually in the | Silt fence is inadequate for erosion control around stream banks and bridge abutments. There should be a standard bid item for the use of channel lining to construct a rock berm around stream bank to prevent erosion. The Channel Lining could be used tem
2011-12-01 | Design | Grade | MAJOR WIDENING(O) | 4 | NELSON | The plans showed very steep grades on three entrances. | Two of these entrances were combined into one in order to create more distance to flatten their slope.
2011-12-01 | Design | Quantities | MAJOR WIDENING(O) | 4 | NELSON | The plans required two applications of chip seal , but adequate quantities for only one application were calculated. | Quantities should be checked more closely. NOTE: There may be an issue with the way this item is calculated.
2011-12-01 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | A proposed 6 waterline was supposed to tie into an existing 6 line at Roadway Sta. 1+90 , however the 6 line was actually a 2 line. The City of Leitchfield still wanted a 6 line in that location. | The Contractor had to tie into an existing 6 waterline located on Mulberry Street. It was agreed that since the city was upgrading their line , they would pay for the material cost of an upgrade from a 2 line to a 6 line and the State would pay the rema
2011-12-01 | Maintenance of Traffic | Incentive | RECONSTRUCTION(O) | 4 | GRAYSON | The contract plans called for closing the road and building the new bridge in the same location as the old structure. However , there was a court order to stop work on the project. No detour was set up on the project and the closest detour route was ap | A Change Order was established to pay the Contractor an incentive to accelerate work on this project.
2011-12-01 | Design | Shelved Plans | MAJOR WIDENING(O) | 4 | NELSON | A bid item for Construction Signs was not included on this project because the plans were designed before signage sheets were standard procedure. | These were shelved plans and as such , they need to be reviewed closely and thoroughly checked before being let. Developing a checklist for shelved plans and making sure they receive Constructability Reviews would also help.
2011-12-01 | Design | Shelved Plans | MAJOR WIDENING(O) | 4 | NELSON | An additional quantity of temporary pavement striping was needed to meet current traffic control specification requirements for multiple phases of the construction. | These were shelved plans and as such , they need to be reviewed closely and thoroughly checked before being let. Developing a checklist for shelved plans and making sure they receive Constructability Reviews would also help.
2011-12-01 | Utilities | Stacked Utilities | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | Field conditions were different than anticipated. An existing sanitary sewer encasement pipe was in the way of a proposed storm sewer pipe. | In order for the storm sewer to be installed , the grade of the storm sewer line had to be changed by removing sixty-five feet of 15 inch pipe and resetting it on a flatter grade. Consequently , the corresponding Type B Curb Box had to be raised and a
2011-12-01 | Design | Shelved Plans | MAJOR WIDENING(O) | 4 | NELSON | A bid item for Temporary Ditching was not established in the plans. Temporary Ditching is now a standard erosion control bid item included on all major grade and drain jobs especially those involving culverts. | These were shelved plans and as such , they need to be reviewed closely and thoroughly checked before being let. Developing a checklist for shelved plans and making sure they receive Constructability Reviews would also help.
2011-12-01 | Right-of-Way | Coordination | MAJOR WIDENING(O) | 4 | NELSON | Existing overhead lights along a bridge approach at the west end of the project were not addressed. These lights had to be removed and reinstalled. | Electrical issues should be handled during the Right-of-Way phase. A Constructability Review may identified this situation.
2011-12-01 | Design | Shoulders | MAJOR WIDENING(O) | 4 | NELSON | Depending upon driving lane widths , paved shoulders can be difficult , even impossible , to construct in accordance with design plans and Cabinet specifications. | It is important that the project team consider the combination of shoulder width , lane width , and the location where the shoulder break occurs. If paved shoulder widths are less than 10 feet , their design should be carefully reviewed with input fro
2011-12-01 | Structures | Omission | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | A bid item for Structural Excavation needed to construct standard gravity retaining walls was not included in the plans. | This omission may have been identified with a more thorough QA/QC check of the plans.
2011-12-01 | Design | Radius | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | There was a tight turning radius at the KY 259 intersection. | This issue could have been identified earlier if AutoTURN software was used to check this intersection. It should be standard procedure to test the turning radii at all intersections using turn modeling software during the design phase.
2011-12-01 | Geotechnical | Slides | NEW ROUTE(O) | 4 | HARDIN | During construction of a fill section at the North end of the project , multiple slides occurred. Significant water seepage was encountered coming from the slopes , which was unexpected because there was no apparent reason for the presence of water. | The slope was stabilized by installing a drain system that collected the excess water before tying into perforated pipe.
2011-12-01 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | End treatment quantities for temporary guardrail shown in the plans on the multiple detours and diversions were not established. The end treatments were shown on the plans , but not in the notes or the summary sheets. | A checklist may have prompted someone reviewing the plans to take note of this omission.
2011-12-01 | Geotechnical | Top of Rock | MAJOR WIDENING(O) | 4 | NELSON | Solid rock was not encountered as stated on the Geotechnical Plans for Abutment 1. The rock elevation was lower than expected. | This was unavoidable based upon actual field conditions. Mass Concrete was used to achieve the desired elevation.
2011-12-01 | Utilities | Omission | SAFETY-HAZARD ELIM(P) | 4 | HARDIN | Three sanitary sewer line services were missed during the utility relocation design phase. This may have been due to the city not knowing which direction the line ran; the sewer actually ran the opposite direction than expected. | An 8 inch sanitary sewer line was extended to provide service to these 3 parcels. The existing line that was extended will no longer be in use after the switch to the new line is made. If it were not for the initial oversight , a temporary line could h
2011-05-18 | Structures | Retaining Walls/MSE | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | The Contractor proposed constructing four gravity walls in lieu of the block retaining walls specified in the plans. | This proposal was approved by the Department , City , County , and property owners. There was no additional cost to the Department.
2011-05-18 | Structures | Bearing Pad | BRIDGE REPLACEMENT(P) | 2 | OHIO | The bearing pad did not adequately transfer loads from the bridge to the end bent. A shim on one side had been working its way loose. | A supplemental item for Shim Bearings was needed to shim and anchor the existing bearing pad for Existing Beam Line 3 at End Bent 2.
2011-05-18 | Pavement | Type | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | Reflective Crack Relief Interlayer was eliminated and replaced with additional thickness of CL3 Asph Base 1.00D PG 64-22. | The Reflective Crack Relief Interlayer may have been applied incorrectly. Relief joints should be placed every 950Ö-1000Ö.
2011-05-18 | Design | Quantities | BRIDGE REPLACEMENT(P) | 2 | OHIO | The amount of full depth patching on the bridge was minimal. | This created a significant decrease in the quantity needed for Concrete Class M Full Depth Patch.
2011-05-18 | Maintenance of Traffic | Omission | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | The need for Standard Barrier Median Type 4 , which provides a barrier between traffic and the newly installed railroad signals , was not addressed in the original contract. A bid item for Temporary Tape was also excluded. | A Constructability Review may have identified these omissions.
2011-05-18 | Maintenance of Traffic | Entrances | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | The plans specified that an entrance would be closed during phase 2 construction. This closure would leave the property owner with inadequate access. | The contractor incurred additional labor cost from the additional forming and pouring of two sections of pavement which had to be blocked out to maintain the entrance during construction. A Change Order for Labor Pavement Blockout was approved to compensa
2011-05-18 | Design | Omission | BRIDGE REPLACEMENT(P) | 2 | OHIO | Since the existing bridge had been previously overlain , a bid item for Machine Prep of Slab was not needed. | An item for Blast Cleaning was added to the contract.
2011-05-18 | Materials | Asphalt Mixtures | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | There was a widespread shortage of PG76-22 asphalt. | Statewide production of all mixes specified as requiring PG76-22 asphalt was changed to PG64-22 asphalt in lieu of PG76-22.
2011-05-18 | Maintenance of Traffic | Lane Closures | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | The Contractor proposed to eliminate the JPC concrete at an intersection and replace it with a modified asphalt mix with special compaction requirements to provide a rut resistant pavement. This design eliminates the need for a full 10-day closure and two | The ContractorÖs proposal was approved. Note: This was not a VECP.
2011-05-18 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 2 | OHIO | During excavation for the footer at Pier 1 , the encountered rock was erodible soft shale. | Soft shale was excavated until suitable rock material was apparent. Concrete Class A Mass Concrete was used to refill the excess excavation.
2011-05-18 | Maintenance of Traffic | Phasing | BRIDGE REPLACEMENT(P) | 2 | OHIO | In conjunction with replacement bridge expansion joints , it was deemed appropriate to modify the contract traffic control plans associated with the latex concrete bridge overlay and supplemental expansion joint replacement. | The modification consolidated the latex concrete and joint replacement operation from 3 phases to 2 phases.
2011-05-18 | Utilities | Plans | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | The Contractor proposed to bore the storm sewer crossings in lieu of open cutting and repairing the roadway as called for in the plans. | The Department approved the proposal. Designers need to look at existing storm water sewer pipes being bored as opposed to open cut and placement when certain cases like this arise.
2011-05-18 | Design | Omission | BRIDGE REPLACEMENT(P) | 2 | OHIO | The contract plans did not include a bid item for Blast Cleaning , which according to section 606.03.04 of the 2008 KY Standard Specifications , was needed. | An item for Blast Cleaning was added to the contract.
2011-05-18 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | Due to a conflict with an existing waterline , the design for a sanitary sewer force main system needed to be revised. | The upgraded system was significantly changed to tie-in to the Sanitation District's larger system. The revised scope included a force main , gravity main , and some very specialized items (e.g. , vortex manhole and a bore under the railroad). Paymen
2011-05-18 | Erosion Control Plan | Slope Protection | BRIDGE REPLACEMENT(P) | 2 | OHIO | Placement of sod was not considered an appropriate form of erosion control for large , disturbed , Right-of-Way areas near the bridge widening. | Seeding and Protection was to control erosion in these areas.
2011-05-18 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | There was an existing 16 Inch Water Main that must be replaced as it would not have adequate cover over the pipe once the new roadway was constructed. | Better coordination is needed between Utility Coordinators and Roadway Designers as plans are developed.
2011-05-18 | Traffic | Signals | BRIDGE REPLACEMENT(P) | 2 | OHIO | During attachment of the existing signal system to the new strain pole , the deteriorated cable failed. | An emergency replacement of the messenger cable was needed for the intersection.
2011-05-18 | Maintenance of Traffic | Moving Traffic | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | With a high volume of truck traffic , a larger turning radius is needed to accommodate trucks. The plans did not account for this turning radius during phase 3 construction. | A rapid cure JPC pavement was used to allow pavement to be placed and opened the same weekend.
2011-05-18 | Structures | Longitudinal Joint | BRIDGE REPLACEMENT(P) | 2 | OHIO | An additional joint in the bridge deck surface would result from the original design. The plans were designed to build the bridge deck widening 8 in depth to the final riding surface , then overlaying the existing deck; thus creating an additional longi | Designers need to be aware of cross-sections for this type of construction sequence.
2011-05-18 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | In order to build an embankment without breaking the existing clay tile sewer , field conditions revealed the necessity to reconstruct the existing sanitary sewer system. The existing clay sanitary sewer line had been broken numerous times at no fault o | The sanitary sewer system was upgraded , pavement thickness was increased , and additional sanitary sewer was installed as requested by Sanitation District 1. This was handled as a betterment situation , but better utility identification earlier would
2011-05-18 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 2 | OHIO | While the contract plans depicted the required 23 ft. of clearance over the railroad; the on-site conditions , after setting the new beams , demonstrated that such clearance was not obtained , even though the bridge substructure was built according to | To improve clearance over the railroad , it was necessary to raise the beam 5¥ and shim the bridge beams. This work included removing the new diaphragms , jacking and shimming the bridge beams , correcting the new diaphragm bolting patterns , adjustin
2011-05-18 | Design | Omission | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | A bid item for Sawcut Pavement was not included in the contract. Sawcut Pavement produces a neat edge along the existing pavement to provide a proper joint between the existing pavement and the proposed widening. The existing paved shoulder was not full | A Constructability Review may have identified this omission.
2011-05-18 | Drainage | Embankment Benches | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | An upgraded drainage plan was implemented for proposed embankment benches. | The original plans called for DGA to be placed on the benches. The improved drainage system replaced the DGA with Type IV Geotextile Fabric , Drainage Blanket , and Perforated Pipe.
2011-05-18 | Structures | Expansion Joints | BRIDGE REPLACEMENT(P) | 2 | OHIO | Expansion joints at both ends of a bridge were deteriorated. | The deteriorated expansion joints were replaced. For this replacement , contract items were added for Armored Edge for Concrete and Steel Reinforcement. Joint Sealing was eliminated as there would no longer be existing joints to re-seal. Contract items
2011-05-18 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 2 | HENDERSON | Due to utility conflicts caused by two water mains , a gas main , and two phone ducts that run under and parallel to Dixie Highway , it was necessary to construct an 18 inch storm sewer at a different location than originally planned. | Better site investigation.
2011-05-18 | Design | Quantities | BRIDGE REPLACEMENT(P) | 2 | OHIO | The upper portion of the existing deck was extremely deteriorated. | This resulted in a significant over-run of Concrete Overlay-Latex for partial depth patching.
2011-05-18 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 2 | OHIO | In accordance with Standard Drawing RBC-004-05 , since the bridge includes sidewalk , guardrail should be tied to the bridge end with Guardrail Connector to Bridge End TY D. Instead , the contract plans called for installation of Guardrail Connector t | Guardrail Connector to Bridge End TY D was added to the contract items; Guardrail Connector to Bridge End TY A was eliminated.
2011-05-18 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 2 | OHIO | In accordance with Standard Drawing RBC-004-05 , since the bridge includes sidewalk , guardrail should be tied to the bridge end with Guardrail Connector to Bridge End TY D. Instead , the contract plans called for installation of Guardrail Connector t | Guardrail Connector to Bridge End TY D was added to the contract items; Guardrail Connector to Bridge End TY A was eliminated.
2011-04-21 | Drainage | Ponding | BRIDGE REPLACEMENT(P) | 6 | BOONE | The existing topography of the new Artisan Center Access resulted in ponding of water. | A v ditch was constructed to provide adequate drainage.
2011-04-21 | Geotechnical | Subsurface | CONGESTION MITIGTN(O) | 6 | KENTON | Unsuitable material to construct a proposed embankment was encountered during construction. | Roadway Excavation was used to undercut the embankment and an existing pond. Excavated areas were re-filled with suitable material.
2011-04-21 | Design | Omission | BRIDGE REPLACEMENT(P) | 6 | BOONE | Removal of existing guardrail on ramps was left out of the contract. | A Constructability Review may have caught this oversight.
2011-04-21 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 6 | BOONE | Material located at several locations contained a high percentage of organic material that was unsuitable for construction of the roadway fill. Quantities established in the original contract were insufficient to perform the work as required by the Geote | This was a basic undercut situation: unsuitable material was removed and replaced as noted in the Geotechnical Notes of the project plans. A French drain was constructed to provide adequate drainage for multiple natural springs encountered at this locatio
2011-04-21 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | BOONE | An elevation conflict was discovered with existing water and sewer lines. | A manhole was installed to adjust the elevation of the storm sewer pipe to avoid conflict with the existing lines. The manhole allows future access for maintenance issues.
2011-04-21 | Structures | Elevation Difference | CONGESTION MITIGTN(O) | 6 | KENTON | Proposed bridge deck elevations did not match approach slab elevations as detailed in the project structure plans. Elevation differences varied between 1 and 10. | Armored Edge was installed at the leading edge of approach slabs at each end of the bridge. Major intersections should have elevation development plans. Elevation development sheets should be made for non-symmetrical alignments to help catch cut / fill
2011-04-21 | Materials | Asphalt Mixtures | BRIDGE REPLACEMENT(P) | 6 | BOONE | There was a widespread shortage of PG76-22 asphalt. | Statewide production of all mixes specified as requiring PG76-22 asphalt were changed to PG64-22.
2011-04-21 | Design | Slopes | RECONSTRUCTION(O) | 6 | BOONE | Designed and constructed slopes were too steep. | Culvert pipe was inserted to soften front and back slopes.
2011-04-21 | Maintenance of Traffic | Striping | MAJOR WIDENING(O) | 6 | BOONE | Lane Striping set up in the original contract was confusing. The striping plans appeared to be acceptable; however , field conditions and complaints from drivers revealed the necessity for change. | We need to broaden our view and look to see whatÖs coming into our project ô e.g. , other lanes might be affected. Tie-ins at intersections require additional survey of existing conditions.
2011-04-21 | Maintenance of Traffic | Safety | CONGESTION MITIGTN(O) | 6 | KENTON | Cameras were needed to safely control traffic through an intersection after the existing loops were damaged during construction. | The Cabinet supplied four cameras and hardware. Recommendation: Add cameras as a bid item for future projects.
2011-04-21 | Drainage | Ponding | RECONSTRUCTION(O) | 6 | BOONE | Additional hydraulic analysis indicated that the original design was insufficient to handle drainage received from the US 460 bypass. Existing culvert pipes under the bypass were larger than indicated on the roadway plans and larger than used in the origi | A storm sewer was installed in the median to address significant ponding.
2011-04-21 | Right-of-Way | Insufficient ROW | MAJOR WIDENING(O) | 6 | BOONE | A Right-of-Way parcel was missed ô the property owner was incorrectly identified. | This parcel had to be re-purchased from the real property owner.
2011-04-21 | Utilities | Delays | RECONSTRUCTION(O) | 6 | BOONE | Existing travel lanes had to be used to maintain traffic a year longer than expected due to utility delays. Work was necessary to maintain traffic on the roadway due to extreme rutting , shoulder failure , and potholes that developed in existing lanes. | Leveling and wedging existing of the existing driving lanes was approved as directed by the engineer.
2011-04-21 | Design | Railroads | MAJOR WIDENING(O) | 6 | BOONE | The bid plans had not been reviewed and approved by the Norfolk Southern Railroad prior to letting. Upon review by the railroad consultant , changes were required. | Construction should have been delayed until after plans were approved by Norfolk Southern Railroad. Coordination with Norfolk Southern should have been followed through as plans were changed (both bridge and roadway).
2011-04-21 | Right-of-Way | Communication | BRIDGE REPLACEMENT(P) | 6 | BOONE | Property owners felt they had not been reimbursed properly for their chain link fence. The removal of the existing chain link fence was necessary to complete waterline and sewer line relocations. | After construction , it was determined that the property owners had not been adequately compensated for their fence during the right-of-way acquisition. New chain link fence was placed on their property.
2011-04-21 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 6 | BOONE | The Cabinet determined that an OSS Galvanized Steel Cantilever panel sign shown in the plans did not meet MUTCD warrants and therefore should not be installed. This deletion would reduce a roadside hazard and future maintenance costs. | The OSS Galvanized Steel Cantilever was not installed. Since the OSS Galvanized Steel Cantilever had been manufactured prior to the decision to omit it from the project , the Cabinet agreed to take ownership and paid the invoice price for material , wh
2011-04-21 | Drainage | Diversion Drainage | MAJOR WIDENING(O) | 6 | BOONE | Water was entering the new railroad embankment and saturating it. | A 4 perforated pipe was installed to drain water between the existing railroad embankment and the new railroad embankment.
2011-04-21 | Erosion Control Plan | Silt Fence | RECONSTRUCTION(O) | 6 | BOONE | Since grading operations were suspended during the winter months , disturbed areas of phase 2 needed to be stabilized. | Plan quantities for Temporary Silt Fence and Silt Trap Type B were insufficient to adequately control erosion generated during construction of the project. Temporary Mulch was needed to minimize erosion of the disturbed areas. This erosion control was re
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | Once construction began , it became clear that there was not enough quality rock in the cut sections to provide the material necessary to construct the rock roadbed. | The Geotechnical Branch reviewed the geotechnical plans and determined that there was enough rock to construct 1/3 of the rock roadbed. The Division of Highway Design was consulted; they provided a revised pavement design that accounted for the lack of th
2011-04-21 | Structures | Reinforcement Steel | BRIDGE REPLACEMENT(P) | 6 | BOONE | Plan errors in the bill of reinforcement did not account for all the steel needed for culverts. Calculations had been performed assuming the steel was placed on 9 centers however , the plans showed the steel to be placed on 7 centers causing an overrun | Additional steel had to be ordered to complete the bridge.
2011-04-21 | Construction | Wells | RECONSTRUCTION(O) | 6 | BOONE | A water well , which was not shown on the design plans , was encountered during construction. | The water well was plugged.
2011-04-21 | Geotechnical | Subsurface | CONGESTION MITIGTN(O) | 6 | KENTON | Existing material was found to be saturated and unsuitable to construct a proposed fill. | The area was undercut and backfilled with suitable material.
2011-04-21 | Structures | Omission | BRIDGE REPLACEMENT(P) | 6 | BOONE | Armored edge quantities for the CSX Bridge were omitted. | An overrun of armored edge at the US 25 Silver Creek Bridge was needed to pay for the armored edge.
2011-04-21 | Traffic | Omission | BRIDGE REPLACEMENT(P) | 6 | BOONE | After construction , it was observed that the right turn lane at the Peggy Flatts Road Intersection required two ONLY Thermo Pavement Markers. The right turn lane converts from a through lane to a mandatory turn lane and therefore requires this marking. | Two ONLY Thermo Pavement Markers were ordered and installed.
2011-04-21 | Pavement | Thickness | RECONSTRUCTION(O) | 6 | BOONE | Depth cores indicated that the base thicknesses were lower than the allowable tolerance according to Kentucky Method 64-420-0304. Additional pavement thickness was needed. This was one of the first jobs in which GPS equipment was used; however the GPS | A leveling and wedging item was established at the unit bid price for CL2 Base for this corrective paving.
2011-04-21 | Traffic | Signals | RECONSTRUCTION(O) | 6 | BOONE | Signalization for the intersection of US 62 and Ironworks Pike was not called for according to the plans. | An executive decision was made to install the traffic signals.
2011-04-21 | Construction | Omission | RECONSTRUCTION(O) | 6 | BOONE | Special staking was necessary for the contractor to properly lay out a traffic signal , even though this item was omitted from the construction revision. | A more thorough review may have caught this.
2011-04-21 | Traffic | Lighting | RECONSTRUCTION(O) | 6 | BOONE | Roadway lighting devices needed to be installed at the intersection of two roads. | It should be noted that the total cost for these items was less than 110% of the total cost using 2008 average unit bid prices and that the total cost is less than the cost estimated by Central Office Traffic.
2011-04-21 | Traffic | Lighting | RECONSTRUCTION(O) | 6 | BOONE | Pole bases did not match plan details. Since the poles were too big for the bases , bolts were cracking , which caused a structural issue. | The contractor proposed replacing the existing bases with 60 (1524mm) diameter x 10' (3.05m) deep bases at no cost to the Cabinet. Since the pole bases had to be replaced , the Central Office Division of Traffic requested that an alternate size base be i
2011-04-21 | Design | CAP | RECONSTRUCTION(O) | 6 | BOONE | Prior to the completion of the project plans , a property owner was promised , by the design team , a seed mixture that did not include fescue to be placed on the slopes adjoining the farm. However , the plans lacked a special note. | In order to fulfill our verbal promise to the property owner , a special seed mixture was placed on our slopes adjacent to the property. All promises need to be communicated. We need to have better communication with our legal department since the owne
2011-04-21 | Pavement | Design | CONGESTION MITIGTN(O) | 6 | KENTON | There was a conflict between the shallow depth of storm sewer pipes and the significant depth of the overall pavement design thickness. Two feet of #2 stone plus additional depth of underdrains were lower than the storm sewer they were draining into. Le | The revised pavement design used one foot of #2 stone in lieu of the two feet of #2 stone proposed in the plans. The revision provided for an additional thickness of asphalt and replacing the crushed stone base with DGA base. Eliminating one foot of dept
2011-04-21 | Structures | Erosion Control | RECONSTRUCTION(O) | 6 | BOONE | There was significant sediment coming from the joints between the abutment and the abutment diaphragm causing staining and potential subgrade erosion diaphragm that could occur if the cork resting between the beam seats is damaged due to weathering. | Waterproof the joints between the substructure and the superstructure of the bridge in order to prevent long term subgrade failure at the bridge ends. In this case , a rubber seal was added.
2011-04-21 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 6 | BOONE | After constructing a triple barrel culvert that diverts water into a nearby stream , runoff water no longer drained through existing pipes into an adjacent pond. Because drainage had been changed , there was no need for the existing pipes. | The existing pipes were initially going to be abandoned; instead , they were removed and an open ditch line was created. This decision was made in order to avoid potential future maintenance problem , such as a collapsed pipe.
2011-04-21 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 6 | BOONE | Bid items were not set up for Removable Striping Tape and Perforated Pipe. | A Constructability Review may have identified these omissions.
2011-04-21 | Utilities | New Utilities | CONGESTION MITIGTN(O) | 6 | KENTON | A proposed water main was to be constructed after completion of an embankment. When the embankment was nearing completion , a water main broke. | The water district fixed the leak by installing valves on both sides of the break and back feeding water through an adjacent subdivision. Flowable Fill was used to backfill the excavated area.
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | Significant settlement occurred at bridge ends near the bridge , which was built with buried approach slab. There was a void beneath the approach slab causing a bump in road. It was deemed necessary to inspect the newly constructed 15 Storm Sewer Pipe | Due to insufficient daily inspection records , KYTC could not prove the Contractor was at fault. A compromise was made with the Contractor. All curb and gutter was removed by the Contractor; drop boxes were installed. KYTC paid for expandable foam to
2011-04-21 | Design | Survey | MAJOR WIDENING(O) | 6 | BOONE | Cross sections showing borrow and fill quantities were significantly changed after a parcel was purchased. The former property owner removed a large quantity of fill material from the project site. | Additional fill material had to be obtained off site. Update survey.
2011-04-21 | Design | Omission | RECONSTRUCTION(O) | 6 | BOONE | Temporary stop bars needed to be placed at an intersection to mark new stopping limits established during phase II of the maintenance of traffic plans. A pay item for this work was not included in the original bid items. | Temporary stop bars were placed at the intersection. A check list , or review , may have caught this oversight.
2011-04-21 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 6 | BOONE | Safe two-way traffic was needed on the diversions while shifting traffic to complete phase 1 construction. The original alignment did not allow vehicles to stay in one lane while making turns at design speed. | Additional pavement widths were provided to maintain safety. Designers need to check geometrics of diversions to see if it will work with speeds in preliminary design meetings; curve widening may have been overlooked since they are usually sufficient.
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | New Albany Shale (soapstone) , which is common in this area , becomes unstable during wet weather. | Establish notes to address the presence of New Albany Shale.
2011-04-21 | Construction | Contracts | BRIDGE REPLACEMENT(P) | 6 | BOONE | The project was set up to use natural sand as sand for blotter. Class I Sand performs equal to natural sand and the lower unit price would provide a savings to the project. | Class I Sand was substituted for the natural sand.
2011-04-21 | Drainage | Pipes | RECONSTRUCTION(O) | 6 | BOONE | A pipe length shown in the plans needed to be longer. | The pipe was extended. This situation may have been revealed with a Constructability Review.
2011-04-21 | Design | Communication | BRIDGE REPLACEMENT(P) | 6 | BOONE | At the time of construction , an existing entrance was a double entrance serving two lots. However , the project was designed for a single entrance. This created an issue for large trailers and equipment. | A double entrance was constructed; entrance pipe was extended; and the guardrail radius was increased. This work was done to accommodate the property owner; designers did not know what function the double entrance served.
2011-04-21 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 6 | BOONE | A bid item for Signs was not set up in the original contract. In accordance with section 112.04.02 of the 2004 Kentucky Standard Specifications for Road and Bridge Construction , bid quantities for construction signing are required. | A more thorough review may have caught this oversight.
2011-04-21 | Drainage | Ponding | BRIDGE REPLACEMENT(P) | 6 | BOONE | During construction , a drainage problem became apparent in the parking lot of a newly constructed building , the Middletown Baptist Church. The drainage design for the new roadway was causing water to pond in the church parking lot; gravel was being | In order to maintain the existing location of the church sign , which had already been relocated as part of this project , it was decided to construct a drainage box next to the sign. Type 7 DBI was placed at the intersection of KY 956 and KY 1983. St
2011-04-21 | Utilities | Relocation | RECONSTRUCTION(O) | 6 | BOONE | The original plans relocated a waterline under an access opening that was proposed for large development. After the relocation was completed , it was decided by the Cabinet and Georgetown Municipal Water and Sewer Service that the location under the acc | A new waterline and some new encasement pipe were installed and connected to the existing waterline as directed by the engineer.
2011-04-21 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 6 | BOONE | Soft embankment areas were encountered during construction. | These areas required undercutting and benching into the existing Railroad embankment.
2011-04-21 | Drainage | Bridge Ends | BRIDGE REPLACEMENT(P) | 6 | BOONE | Water flowing off of the newly constructed Silver Creek Bridge emptied onto the grade causing erosion problems. | Two Type 2 Flume Inlets were installed to capture and direct the runoff to a channel line ditch.
2011-04-21 | Pavement | Approaches | RECONSTRUCTION(O) | 6 | BOONE | It was necessary to provide a smooth pavement transition between the intersections of two roadways due to minor profile differences. | Leveling and wedging was installed at the transition between intersections of two roadways. Leveling and wedging was also installed at another location to eliminate driver confusion witnessed at the intersection.
2011-04-21 | Maintenance of Traffic | Omission | CONGESTION MITIGTN(O) | 6 | KENTON | The Maintenance of Traffic Plan did not specify Barrier Wall or Temporary Guardrail for phased construction; Variable Message Signs were not included with the original contract bid items. | Barrier Walls , Temporary Guardrail , and Crash Cushions were installed. Barrier Walls provide positive separation between vehicular traffic and excessive pavement edge drop-offs. Recommendation: Use Barrier Walls when there is a high concentration of
2011-04-21 | Design | Slopes | BRIDGE REPLACEMENT(P) | 6 | BOONE | During construction on US 25 , it became evident that the designed slopes on several entrances were too steep for future maintenance , such as mowing. Property owners were unhappy with the steep slopes; they were also unhappy with the mess created and | The entrances were re-graded , seeded , and fertilized. To maintain drainage , Type 7 DBI was added because of the confined space within the ditch line. Entrance pipe was extended 6 ft. in order to lessen the slope and make the area traversable.
2011-04-21 | Utilities | Delays | RECONSTRUCTION(O) | 6 | BOONE | The project was let prior to the use of cpm schedules. The contractor submitted a claim for delays associated with utility relocations. There were approximately 9 months of idle time causing the project to last 3 years compared to 1 as initially planned | This project should not have been let until utility relocations were at least 50-75% complete , especially since some level of delays were expected. Temporary relocations may have helped.
2011-04-21 | Design | Plans | RECONSTRUCTION(O) | 6 | BOONE | A Bore Pit was located right on the edge line of traffic on an existing roadway with 10 ft lane widths. | The Bore Pit was extended to provide a safe buffer zone from traffic.
2011-04-21 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | BOONE | An existing gas line was located at a higher elevation than shown on the plans. | The existing gas line had to be lowered. This may have been a survey issue.
2011-04-21 | Structures | Reinforcement Steel | BRIDGE REPLACEMENT(P) | 6 | BOONE | An error in the plans for the CSX Bridge caused the bill of reinforcement to be incorrect. | In order to construct the bridge as designed , 2320 lbs of additional steel reinforcement had to be ordered.
2011-04-21 | Pavement | Omission | RECONSTRUCTION(O) | 6 | BOONE | Quantities for DGA and Crushed Stone Base were mistakenly omitted from the Paving Summary. | A check list , or more thorough review , may have caught these oversights.
2011-04-21 | Traffic | Lighting | BRIDGE REPLACEMENT(P) | 6 | BOONE | Removal of 5 lights that were in the way of constructing a new entrance was not included as a bid item. The lights had to be removed , stored , and relocated to the newly constructed entrance. | A Constructability Review may have caught this oversight.
2011-04-21 | Design | Omission | RECONSTRUCTION(O) | 6 | BOONE | Temporary removable tape pavement striping was needed to maintain two-way traffic on a bridge during phase II of maintenance of traffic plan. Pay items for temporary removable tape were not included in the original bid items. | This oversight may have been noticed with a Constructability Review.
2011-04-21 | Drainage | Omission | BRIDGE REPLACEMENT(P) | 6 | BOONE | Not enough quantity was established for non-perforated pipe to make headwalls. Plan quantities might not ever be exactly correct for this bid item; but , typically it is close enough to not warrant a change order. | Additional non-perforated pipe was ordered.
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | Unstable areas were found in three areas , which weren't included within geotechnical notes on the plans. | These areas had to be excavated and backfilled with Granular Embankment.
2011-04-21 | Drainage | Drop Box Inlets | RECONSTRUCTION(O) | 6 | BOONE | Pipe sheets did not account for a left turn lane that was added later in the design process. | A drop box inlet was constructed according to the plans , but the pipe sheets did not account for a left turn lane that was added. A Constructability Review may have caught this oversight.
2011-04-21 | Design | Plans | BRIDGE REPLACEMENT(P) | 6 | BOONE | Design plans did not provide details and quantities to reestablish the termini of the multi-use path to the Artisan Center entrance road and repair areas disturbed due to the construction of the new Artisan Center Entrance. | The multi-use path from the Artisan Center was reconstructed to tie back in at a more appropriate location. This plan revision enables service vehicles to cross the multi-use path to the frontage road.
2011-04-21 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 6 | BOONE | There were several minor discrepancies with water line plans , which were inserted into the final plans. | Water line plans are from utility company; we do not get a chance to review.
2011-04-21 | Construction | Contracts | MAJOR WIDENING(O) | 6 | BOONE | Incorrect Project Wage Rates were included in the contract when let. | A more thorough review of wage rates may have prevented this oversight.
2011-04-21 | Drainage | Pipes | MAJOR WIDENING(O) | 6 | BOONE | There was no way to outlet water collected in a subbase. | Perforated pipe was installed to outlet water into curb boxes.
2011-04-21 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 6 | BOONE | Material from the old railroad embankment was unsuitable to be used in the new embankment areas. | Recommendation: Do not include existing Railroad embankment (fill) material for roadway.
2011-04-21 | Drainage | Pipes | RECONSTRUCTION(O) | 6 | BOONE | Entrance pipe quantities were mistakenly recorded as culvert pipe in the project summary and original bid items. | This mistake was discovered at the time of construction and entrance pipe was installed. A more thorough review may have caught this earlier.
2011-04-21 | Utilities | Delays | RECONSTRUCTION(O) | 6 | BOONE | Additional quantities of traffic bound base were needed to adequately maintain access to properties throughout the project. Utility delays resulted in additional construction seasons , thus greatly increasing the time necessary to maintain entrances on | New rock had to periodically be added to entrances for property owners. The longer you drag out a project ô the longer entrances have to be maintained.
2011-04-21 | Design | Omission | RECONSTRUCTION(O) | 6 | BOONE | Existing thermoplastic stop bars and thermoplastic cross-hatching needed to be removed at an intersection to accommodate the traffic shift at this location during phase II of the maintenance of traffic plan. Pay items for pavement marker removal were not | Temporary stop bars were placed at the intersection. A check list or review may have caught this oversight.
2011-04-21 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 6 | BOONE | A sanitary sewer line was discovered during construction. This line was not on the plans and had been overlooked during the design phase. The Utility company did not know it was there. | Steel encasement was needed in order to relocate the existing line.
2011-04-21 | Right-of-Way | Communication | RECONSTRUCTION(O) | 6 | BOONE | Property owners changed their intent; two additional entrances and turning lane were requested. | The additional entrances and turning lane were added; this cost was deducted from their settlement.
2011-04-21 | Construction | Railroads | MAJOR WIDENING(O) | 6 | BOONE | Vibrations from rail traffic can cause hex nuts to loosen from anchor bolts. | In an effort to prevent future maintenance problems , an additional hex nut was added to the anchor bolts.
2011-04-21 | Drainage | Pipes | MAJOR WIDENING(O) | 6 | BOONE | A 24 Storm Sewer Pipe was already on site when a Construction Revision deleting this pipe was issued. | After the Construction Revision and Change Order were issued , a restocking fee was paid.
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | An unstable area was found during construction. In this area , the subgrade was very close to the existing grade and little excavation was required. The existing ground held water , creating a soft area. Test holes were dug in hopes of finding more soli | In order to construct the roadway , it was determined that the area needed to be bridged over. To do this 5 , 817.2 cubic yards of material had to be removed; then , 8 , 623.7 square yards of Geotextile TY III Fabric was placed and backfilled with 5817
2011-04-21 | Design | Quantities | MAJOR WIDENING(O) | 6 | BOONE | The typical section shows that the Crushed Aggregate be wrapped with Type IV Fabric. A bid item was set up for one layer; however , two layers were needed. | This quantity was increased based on actual field measurements for both layers.
2011-04-21 | Construction | Delays | MAJOR WIDENING(O) | 6 | BOONE | Construction delays were caused by inspector bearing issues on the Norfolk Southern bridge. | The Contractor filed a claim and was compensated for the delays.
2011-04-21 | Pavement | Design | CONGESTION MITIGTN(O) | 6 | KENTON | Newly constructed asphalt pavement did not match the existing concrete pavement at the tie-in location. | 9 JPC Pavement was installed on the Ramp and Shoulder in order to match the existing concrete pavement.
2011-04-21 | Erosion Control Plan | Topdressing Fertilizing | BRIDGE REPLACEMENT(P) | 6 | BOONE | Top dressing fertilizer was requested by Central Office Construction to maintain and promote the establishment of vegetation on the project. | A bid item for topdressing should be set up on all projects.
2011-04-21 | Maintenance of Traffic | Omission | CONGESTION MITIGTN(O) | 6 | KENTON | Bid items were not set up for Pavement Striping , Signs , Temporary Striping , and Temporary Tape. | A Constructability Review may have identified these omissions.
2011-04-21 | Maintenance of Traffic | Phasing | CONGESTION MITIGTN(O) | 6 | KENTON | Maintenance of Traffic plans were incomplete; significant drop-off conditions occurred in the phasing. | MOT modeling efforts need to be increased. MOT plans should be included on cross sections.
2011-04-21 | Traffic | Lighting | RECONSTRUCTION(O) | 6 | BOONE | Roadway construction and utility relocations impacted existing electric service and conduits. Interchange lighting was one of the first things utilities removed for relocation. | New electric service and conduits were installed to reestablish interchange lighting at the intersection. Specific notes may need to be added for the Contractor to provide temporary lighting at intersections during construction. District staff indicate
2011-04-21 | Right-of-Way | Easements | BRIDGE REPLACEMENT(P) | 6 | BOONE | Access to Berea Municipal Water CompanyÖs existing waterlines and associated easements were cut-off by the new roadway construction. Relocation of KY 595 did not address reconnecting access to Berea Municipal Water pump station. | A Double Vehicular Woven Wire Gate was installed to provide access for Berea Municipal Water.
2011-04-21 | Drainage | Pipes | MAJOR WIDENING(O) | 6 | BOONE | Norfolk Southern Railroad requested a change to the designed drainage system. The Railroad required ductile iron pipe under the bridge; Railroad notes specified ductile iron. | The drainage system was changed from galvanized steel pipe to painted ductile iron pipe. Ductile iron pipe has better corrosion resistance properties than the steel pipe to deal with potential corrosive materials coming off of the trains.
2011-04-21 | Utilities | Delays | RECONSTRUCTION(O) | 6 | BOONE | The plan quantities for Temporary Silt Fence and Silt Trap Type B were insufficient to adequately control erosion generated during construction of the project. Major utility delays caused the contractor to suspend operations on the project. The length of | Disturbed areas were stabilized with Temporary Mulch or Temporary Seeding and Protection as directed by the engineer. This work was required to comply with environmental laws and specifications. Designers need to consider phasing of traffic when setting u
2011-04-21 | Maintenance of Traffic | Striping | BRIDGE REPLACEMENT(P) | 6 | BOONE | Temporary traffic markings were not set up on the project , but they were essential to limit confusion and provide a safer roadway. Due to construction phasing , the District felt it was necessary to provide temporary pavement markings. There were no av | Temporary pavement markings were provided. Temporary straight and curve arrows were used to designate lanes; temporary stop bars were used to better emphasize the intersections. Paint was used due to the temporary situation and cheaper cost.
2011-04-21 | Structures | Quantities | MAJOR WIDENING(O) | 6 | BOONE | There was an error in the structure plans stating the approximate quantity for Shear Connectors as 1670. The actual quantity for Shear Connectors was 5010. | An adjustment was made to increase the unit price for this item. The original bid item was per pound; this should have been £each¥ or £lump sum¥.
2011-04-21 | Geotechnical | Subsurface | BRIDGE REPLACEMENT(P) | 6 | BOONE | Solid rock was found to be two to four feet lower than shown in the plans at all columns at pier one and columns 3 , 4 , and 5 at pier two. Solid rock was well below the elevation shown in the plans at both piers and it was approximately one foot highe | One pier was shifted 15 feet to get out of clear zone. Mass concrete was needed to bring the footing up to the elevation shown in the plans. As per Standard Specifications 601.05 , mass concrete had to be paid at two times the delivered price of concr
2011-04-21 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 6 | BOONE | Pavement markings were shown on the plans , but bid items were missing. Pavement markings are necessary to allow proper traffic flow through the project. | A check list , or more thorough review of bid items , may have caught this omission.
2011-04-21 | Drainage | Headwalls | RECONSTRUCTION(O) | 6 | BOONE | There was a miscalculation for concrete for head wall; calculations were for a single but it was a triple. | A more thorough review may have caught this error.
2011-04-12 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 7 | MADISON | A bid item to remove and reset crash cushion was left off the plans. This item was necessary to protect blunt ends on temporary median barrier wall during MOT phases. | A more thorough check of plans may have caught this oversight.
2011-04-12 | Design | Adjacent Projects | NEW INTERCHANGE(O) | 7 | MADISON | Water was ponding on the pavement during heavy rain storms , which caused vehicles to hydroplane. This was a bad spot for a tie-in section with 2 different projects coming together; there was a transition from vertical curve into a superelevated sectio | Items were added to correct the drainage problem. Better communication during design regarding adjacent property may have prevented this problem. Better coordination between the two engineering firms was needed at the tie-in of the two sections and perh
2011-04-12 | Geotechnical | Top of Rock | MAJOR WIDENING(O) | 7 | SCOTT | A bridge was designed to excavate to solid rock on abutments one and two. Granular embankment was designed to be placed on the solid rock to plan elevation. The rock line varied dramatically in areas. Rock was as deep as 12 feet in some areas and other | Mass concrete was proposed to fill in the areas. However , when rock was found to be lower than anticipated , mass concrete was determined to be too costly and hard to pour. Flowable fill was used to fill all voids; this was recommended by the centr
2011-04-12 | Design | Adjacent Projects | RECONSTRUCTION(O) | 7 | MADISON | Water was ponding on the pavement during heavy rain storms , which caused vehicles to hydroplane. This was a bad spot for a tie-in section with 2 different projects coming together; there was a transition from vertical curve into a superelevated sectio | Items were added to correct the drainage problem. Better communication during design regarding adjacent property may have prevented this problem. Better coordination between the two engineering firms was needed at the tie-in of the two sections and perh
2011-04-12 | Maintenance of Traffic | Omission | NEW INTERCHANGE(O) | 7 | MADISON | A bid item to remove and reset crash cushion was left off the plans. This item was necessary to protect blunt ends on temporary median barrier wall during MOT phases. | A more thorough check of plans may have caught this oversight.
2011-04-12 | Construction | Bench Marks | NEW ROUTE(O) | 7 | MADISON | Construction personnel set a bench mark closer to the project for convenience during construction; however , the bench mark was located incorrectly ô there was a 3¥ vertical differential. Contractor had to hire a surveyor to adjust approaches. | Contractors should be required to set their own bench marks.
2011-04-12 | Structures | Striping | MAJOR WIDENING(O) | 7 | SCOTT | Durable striping was set up on the rest of the project so the bridge would probably not be restriped on an annual basis. | Permanent durable tape was needed on the bridges in lieu of thermoplastic striping due to the bonding problems associated with thermoplastic and concrete.
2011-04-12 | Pavement | Design | RECONSTRUCTION(O) | 7 | MADISON | The 0.38D skid resistant surface material needed to be 0.50A for mainline I-65. | By checking plans more closely , this could have been corrected during pavement design.
2011-04-12 | Pavement | Design | NEW INTERCHANGE(O) | 7 | MADISON | The 0.38D skid resistant surface material needed to be 0.50A for mainline I-65. | By checking plans more closely , this could have been corrected during pavement design.
2011-04-12 | Design | Underground Tank | NEW ROUTE(O) | 7 | MADISON | There were delays finishing the project due to septic tank issues (e.g. , could not get legal system from the county health agent , perk test failed). Any time you touch a septic system it can be major. | Whomever obtained the right-of-way should have better evaluated the situation. For example , if a project is within 30 feet of septic tank , leach lines (perforated pipe) need to be established.
2011-04-12 | Design | Omission | MAJOR WIDENING(O) | 7 | SCOTT | The concrete median barrier wall on I-75 had to be removed to allow the construction of the center pier for the new bridge; however , there was no bid item set up for this removal. Temporary median wall quantities were insufficient to allow for tapers o | Better plan review is needed and a constructability review might have caught the bid item omission. Designers need to consider the work area , not just the footprint , when work on interstate medians under traffic is needed. Typically , a larger work
2011-04-12 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 7 | SCOTT | No bid items were set up for Type IV Geotextile Fabric and Type I Geotextile Fabric. Type IV Geotextile Fabric was needed to properly construct the fill at the end-bent; Type I Geotextile Fabric must be placed under the crushed aggregate slope protect | A check list may have identified this oversight. This would not be in the plans but is shown in the standard drawings.
2011-04-12 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 7 | SCOTT | Temporary barrier wall and temporary crash cushions were relocated in order to reopen two-way traffic on Duncannon Road while protecting the drop-off between phases one and two of the roadway construction. | This provided savings to the Cabinet with less inconvenience to the traveling public , while maintaining a safe work zone.
2011-04-12 | Construction | Contracts | MAJOR WIDENING(O) | 7 | SCOTT | The grass was posing a sight distance issue and needed to be mowed. Three mowing cycles were estimated during the 2009 mowing season. | Since this road would not become a State Route until completion of the project , Statewide Maintenance funds could not be used for mowing during the 2009 season. The following year , Statewide Maintenance funds were used for mowing the mowing cycles.
2011-04-12 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 7 | SCOTT | Temporary guardrail was needed on the ends of the bridge over CSX railroad during Maintenance of Traffic phase III. When traffic was switched to this phase , guardrail was needed to protect traffic from the barrier wall ends and from the resulting drop- | Temporary guardrail used on phase three of CSX Bridge should have been in traffic plans. A more thorough review would have been beneficial.
2011-04-12 | Structures | Erosion Control | MAJOR WIDENING(O) | 7 | SCOTT | Water draining at the bridge ends of the Duncannon Road Bridge over I-75 ran down the slope causing erosion problems. | Standard curb and gutter were added at the bridge ends directing water to a flume inlet type 2 and a channel lined ditch. Erosion problems at bridge ends should have been addressed by bridge end drainage standard drawings.
2011-04-12 | Design | Guardrail | MAJOR WIDENING(O) | 7 | SCOTT | By eliminating one of the two entrances at the Day Care owned by the City of Richmond , school buses had to turn around in order to exit the facility's only entrance. But , the facilityÖs existing parking lot did not allow adequate maneuvering space for | Contractors essentially built a cul-de-sac so buses could turn around.
2011-04-12 | Design | Guardrail | MAJOR WIDENING(O) | 7 | SCOTT | By eliminating one of the two entrances at the Day Care owned by the City of Richmond , school buses had to turn around in order to exit the facility's only entrance. But , the facilityÖs existing parking lot did not allow adequate maneuvering space for | Contractors essentially built a cul-de-sac so buses could turn around.
2011-04-12 | Maintenance of Traffic | Omission | NEW INTERCHANGE(O) | 7 | MADISON | A bid item needed for barrier mounting bracket was not in the plans. | A more thorough check of plans may have caught this omission.
2011-04-12 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 7 | MADISON | A bid item needed for barrier mounting bracket was not in the plans. | A more thorough check of plans may have caught this omission.
2011-04-12 | Design | Shoulders | MAJOR WIDENING(O) | 7 | SCOTT | After the existing rest areas were eliminated , trucks continued to stop at this location , parking on the shoulders. Trucks sometimes became stuck on the earth shoulders , which were rapidly deteriorating. | DGA was placed along shoulders but rutting was still occurring so a request was made to preform chip sealing on the shoulders.
2011-04-12 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 7 | SCOTT | An existing 18 inch pipe , which was not shown on the plans , was discovered during construction. The pipe was approximately 14 feet below the new roadway. | Fill material was placed in the area so that the pipe is no longer usable. Approximately 6 cubic yards of fill was required to safe load the pipe.
2011-04-12 | Construction | Contracts | MAJOR WIDENING(O) | 7 | SCOTT | The contractor bid the project with CSX notes on it , but CSX came back and changed the requirements. The issues involved flagging costs. | An Administrative Settlement was made for full compensation for all issues associated with the construction of the bridge over the CSX railroad.
2011-04-12 | Right-of-Way | CAP | MAJOR WIDENING(O) | 7 | SCOTT | An agreement to provide a steel encasement pipe was made with a property owner during Right-of-Way negotiations. However , this was not included in the plans. The error was discovered after the embankment was placed. | The bore and jack method was used to install the pipe as this method was less costly than open cutting the roadway. This should have been entered as a CAP.
2011-04-12 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 7 | SCOTT | Unstable material was found in several areas. | These areas were undercut and backfilled to provide a stable subgrade.
2011-04-12 | Design | Safety | MAJOR WIDENING(O) | 7 | SCOTT | Guardrail and two Type I End Treatments were necessary to increase the safety of the public by protecting them from colliding with the concrete pedestals which hold up the overhead panel signs. However , two Type I End treatments and 700 LF of guardrai | The panel signs were overdesigned. Smaller panel signs with break-away posts should have been used on this project. Often , signs are the last thing added and there's not much consideration given to how we can shield the traveling public from these pot
2011-04-12 | Utilities | Conflicting Information | MAJOR WIDENING(O) | 7 | SCOTT | The Madison County Utility District had a contract specification for a 20 inch steel encasement pipe with a wall thickness of .25 inches. However , before the letting , the area was placed in the city limits of Richmond , making the utilities property | Could have possibly been avoided with better communication with local officials.
2011-04-12 | Design | Entrance | MAJOR WIDENING(O) | 7 | SCOTT | After construction , it was necessary to remove and reset the constructed guardrail at several intersections because it was too high and caused a sight distance issue at the stop bar. | This could have been prevented by adjusting grade of ramp or adjusting the stop bar location.
2011-04-12 | Structures | Omission | MAJOR WIDENING(O) | 7 | SCOTT | Although the bridge plans showed temporary guardrail attached to box beam #7 , this item was omitted from the bid items. | A check list may have identified this oversight.
2011-04-12 | Design | Plans | MAJOR WIDENING(O) | 7 | SCOTT | Removal of median barrier wall , Type C and C1 , under existing bridge wasnÖt addressed in plans. | A constructability review might have caught this oversight.
2011-04-12 | Maintenance of Traffic | Phasing | MAJOR WIDENING(O) | 7 | SCOTT | The phasing for the bridge over the CSX Railroad was supposed to maintain two lanes of traffic by using temporary guardrail bolted to a box beam. The placement would not allow the deck to be poured around the rail and it would create an unsafe area for bo | A temporary traffic signal was used to correct some of the problems with the proposed method. This reduced traffic to one lane , which allowed ample room for properly constructing the second phase of the bridge deck. Additional barrier wall was needed
2011-03-22 | Geotechnical | Slides |  |  |  | A slide occurred along the top of the slope on Connector Right. | A Change Order was set up for the removal and disposal of material from the slide.
2011-03-22 | Construction | Coordination |  |  |  | The contractor was asked to participate in a two day Partnering Workshop including follow up session , all course materials , and workshop amenities. | A Change Order was made to incorporate Special Provision No. 99(94) into the contract.
2011-03-22 | Construction | Railroads |  |  |  | Railroad flagging was necessary while working in closes proximity to the railroad. | An item was established for 37.31 hours at $550.00 per hour for a total of $20 , 520.50.
2011-03-22 | Pavement | Striping |  |  |  | Four inch pavement striping was needed. | The striping was added to the contract.
2011-03-22 | Drainage | Pipe Sizing |  |  |  | An 18 inch Bituminous-coated corrugated steel structural plate pipe (BCCSSPP) was specified to carry a 15 inch culvert pipe beneath the roadway and railroad at Sta. 118+20.3 (KY 8 - mainline). This size pipe was not commercially available and would not b | A larger diameter (24 inch) pipe was required.
2011-03-22 | Geotechnical | Quantities |  |  |  | There was an overrun of quantities for roadway excavation of the Lawrence Creek embankment benching and for the undercut of unsuitable material along KY 8 and connector left. | A Change Order was established to provide funds for these items.
2011-03-22 | Erosion Control Plan | Slope Protection |  |  |  | Areas of the cut slopes along KY 8 Connector Left and along KY 8 mainline were of an erodible , sandy material. After this area was seeded , the slopes became eroded by water runoff. | To stabilize these areas , geotextile fabric was placed on the slopes and covered with one foot of Channel Lining Class II.
2011-03-22 | Drainage | Ditches |  |  |  | Due to the volume and velocity of the runoff in the roadway ditches on the north end of the project and along the KY 8 connector roads , erosion problems occurred. | The ditches were lined with Channel Lining Class 1-A to prevent undercutting of the bottom and front slope of the ditches.
2011-03-22 | Geotechnical | Slides |  |  |  | A slide occurred on the slopes of the KY 3056 approach. | A Change Order provided funds for the removal and disposal of material from the slide.
2011-03-22 | Maintenance of Traffic | Safety |  |  |  | There were concerns regarding the safety of the traveling public during construction of the project specifically near the approach for KY 435. | It was necessary to construct temporary guardrail along the approach at KY 435.
2011-03-22 | Construction | Contracts |  |  |  | An existing residence was used as a field office for the contractor. | A Change Order was established to use an existing residence as a field office for the contractor.
2011-03-22 | Drainage | Pipe Sizing |  |  |  | The project plans specified a 78 inch diameter pipe to carry a 72 inch culvert pipe beneath the railroad at Sta. 118+50 and at Sta. 124+75 (KY 8 - mainline). This pipe was not large enough to provide for the corrugations on the culvert. | A larger diameter (84 inch) pipe was required.
2011-03-22 | Construction | Coordination |  |  |  | The railroad company decided to perform the installation of a bid item for Railroad Crossing themselves. | This bid item was removed from the contract and a decrease of $10 , 000 was allocated.
2011-03-22 | Geotechnical | Quantities |  |  |  | The project plans specified that the embankment benches be constructed into solid rock at the approach to the bridge over Lawrence Creek. A one foot thick drainage blanket wrapped in geotextile fabric was to be placed on the benches , but insufficient q | Quantities were added via Change Order.
2011-03-22 | Drainage | Ditches |  |  |  | Some ditches along the project were damaged by flooding. | A Change Order was set up to repair the flood damaged ditches.
2011-03-22 | Design | Safety |  |  |  | There were concerns regarding the safety of the traveling public. | Sloped boxes were installed on drainage pipe instead of concrete headwalls. Also , slopes were flattened and this required the height of previously constructed drop box inlets to be increased.
2011-03-22 | Geotechnical | Soils |  |  |  | Unsuitable material was encountered at the location of a 60 inch pipe. | Extensive work was required to create a stable foundation on which the pipe was placed.
2011-03-22 | Construction | Contracts |  |  |  | Prior to letting of the contract , it was noted that Railroad Protective Insurance would be required on this project. | A Change Order was set up to establish an item to reimburse the contractor for his costs.
2011-03-22 | Construction | Temporary Fencing |  |  |  | As a result of damage to an adjacent property owner's home the contractor chose to provide lodging for them in the residence that was being used as a field office by the contractor. This was done at no cost to the department. | The cost incurred by this Change Order was the installation of a 4' chain link fence around a small cliff region next to the house. This was to provide safety for the occupants of the house.
2011-03-22 | Construction | Contracts |  |  |  | A 5'x4' RCBC under KY 8 conflicted with the location of the piling for the foundation of the proposed pier. This was originally to be included on the bridge project but was moved to the earthwork contract because of the amount of excavation required. | The 5'x4' RCBC under KY 8 had to be removed in order to drive the piling for the foundation of the proposed pier.
2011-03-22 | Design | Safety |  |  |  | In the interest of safety for the traveling public and at the request of the Division of Traffic , the decision was made to widen the connector ramps from KY 8 to the mainline roadway. | This required flattening of the embankment slopes and constructing a concrete median barrier between opposing lanes of traffic.
2011-03-22 | Drainage | Ditches |  |  |  | Due to the volume and velocity of runoff through a 72 inch pipe under the railroad , the area at the end of the pipe was eroding along the sides and bottoms of the channel during periods of normal rainfall. | The ditch was reconstructed and lined to a depth of two feet using stone of a larger size. Class B concrete was placed in the flow line and side slopes of the ditch to fill excess voids and prevent erosion.
2011-03-22 | Erosion Control Plan | Slope Protection |  |  |  | Due to the type of material encountered in the finishing slopes along Connectors Left and Right , a large amount of erosion occurred leaving deep gullies in the slopes. | The slopes had to be redressed to fill in the gullies.
2011-03-22 | Construction | Earthwork |  |  |  | The plans for this project specified constructing a Gabion Retaining Wall along the toe of the embankment at Lawrence Creek. The typical section depicts burying approximately 4 feet of the lower portion of these gabions. | Since the material on the lower side of the gabions would be susceptible to erosion , this resulted in the need to dispose of the excess excavated material.
2011-03-22 | Construction | Railroads |  |  |  | The project plans specified cutting embankment benches along existing KY 8 prior to constructing the embankment in this area. After the work had started , it was discovered that the existing signal poles along the existing CSX Railroad would hinder the | As relocation of these poles would require several weeks work and this area was in a slide plane , these benches were temporarily refilled and the slopes graded to prevent further sliding.
2011-03-22 | Erosion Control Plan | Omission |  |  |  | The original project plans did not satisfy the requirements as set forth by the Clean Water Act. | Items such as Silt Fence and Sediment Traps had to be added and these items were to remain in place through the life of the project.
2011-03-22 | Drainage | Pipes |  |  |  | There were safety concerns regarding a 60 inch pipe. | The pipe was extended using a Type 3 A , 60 inch metal end section.
2011-03-22 | Design | Guardrail |  |  |  | Guardrail on the project did not meet current standards for construction. | A Change Order provided funds to add an end treatment.
2011-03-22 | Design | Guardrail |  |  |  | Guardrail on the project did not meet current standards for construction. | A Change Order provided funds to add an end treatment.
2011-03-22 | Design | Quantities | MAJOR WIDENING(O) | 3 | WARREN | The project plans specified constructing a double seal on the outside edge of the shoulders throughout the project. Field calculations showed the establish quantities were not sufficient for this construction. | Quantities were added.
2011-03-22 | Design | Quantities | MAJOR WIDENING(O) | 3 | WARREN | The project plans specified constructing a double seal on the outside edge of the shoulders throughout the project. Field calculations showed the establish quantities were not sufficient for this construction. | Quantities were added.
2011-03-22 | Utilities | CAP | MAJOR WIDENING(O) | 3 | WARREN | The project plans specified constructing steel encasement pipe at two locations for future utility construction. In order to comply with previous property owner agreements , additional pipe was required. | Additional pipe was added.
2011-03-22 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 3 | WARREN | The plans for this project specified the installation of metal encasement pipe at two locations on the project. However , the fill materials encountered in the excavation for these pipes were not suitable for re-compaction in the pipe trench. | Flowable Fill Concrete was added via Change Order and used around the pipe.
2011-03-22 | Geotechnical | Settlement | MAJOR WIDENING(O) | 3 | WARREN | After completion of the surfacing on this project , major settlement occurred at the approaches to the Lawrence Creek Bridge. | In order to correct the approaches and to provide safety of the public , additional work was required.
2011-03-22 | Geotechnical | Settlement | MAJOR WIDENING(O) | 3 | WARREN | After completion of the surfacing on this project , major settlement occurred at the approaches to the Lawrence Creek Bridge. | In order to correct the approaches and to provide safety of the public , additional work was required.
2011-03-22 | Utilities | CAP | MAJOR WIDENING(O) | 3 | WARREN | The project plans specified constructing steel encasement pipe at two locations for future utility construction. In order to comply with previous property owner agreements , additional pipe was required. | Additional pipe was added.
2011-03-22 | Traffic | Raised Pavement Markers | MAJOR WIDENING(O) | 3 | WARREN | Additional pavement markers were needed between the two sections. | Additional pavement markers were added.
2011-03-22 | Traffic | Raised Pavement Markers | MAJOR WIDENING(O) | 3 | WARREN | Additional pavement markers were needed between the two sections. | Additional pavement markers were added.
2011-03-22 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 3 | WARREN | The plans for this project specified the installation of metal encasement pipe at two locations on the project. However , the fill materials encountered in the excavation for these pipes were not suitable for re-compaction in the pipe trench. | Flowable Fill Concrete was added via Change Order and used around the pipe.
2011-03-22 | Design | Omission | MAJOR WIDENING(O) | 3 | WARREN | The plans for this project specified constructing a traffic signal at the intersection of KY 9 (AA Highway) and the River Bridge Approach. Several items necessary for this construction were omitted from the bid items. | Several bid items were added.
2011-03-22 | Design | Omission | MAJOR WIDENING(O) | 3 | WARREN | The plans for this project specified constructing a traffic signal at the intersection of KY 9 (AA Highway) and the River Bridge Approach. Several items necessary for this construction were omitted from the bid items. | Several bid items were added.
2011-03-22 | Geotechnical | Settlement | MAJOR WIDENING(O) | 3 | WARREN | After construction had begun , settlement of an embankment area was noted. A field inspection of the area indicated sub-surface water was accumulating in the embankment. | A Change Order was set up for the following changes: (1) Mobilization of all equipment , site preparation and dressing of disturbed areas. (2) Furnishing materials and installing horizontal drains in various areas of the embankment. (3) Drilling a ver
2011-03-22 | Geotechnical | Settlement | MAJOR WIDENING(O) | 3 | WARREN | After construction had begun , settlement of an embankment area was noted. A field inspection of the area indicated sub-surface water was accumulating in the embankment. | A Change Order was set up for the following changes: (1) Mobilization of all equipment , site preparation and dressing of disturbed areas. (2) Furnishing materials and installing horizontal drains in various areas of the embankment. (3) Drilling a ver
2011-03-22 | Design | Guardrail | MAJOR WIDENING(O) | 3 | WARREN | The end treatments did not meet current standards. | The end treatments were changed from Type 4 to Type 4A.
2011-03-22 | Design | Guardrail | MAJOR WIDENING(O) | 3 | WARREN | The end treatments did not meet current standards. | The end treatments were changed from Type 4 to Type 4A.
2011-03-22 | Design | Guardrail | MAJOR WIDENING(O) | 3 | WARREN | The end treatments did not meet current standards. | The end treatments were changed from Type 4 to Type 4A.
2011-03-22 | Design | Guardrail | MAJOR WIDENING(O) | 3 | WARREN | The end treatments did not meet current standards. | The end treatments were changed from Type 4 to Type 4A.
2011-03-08 | Structures | RCBC | RECONSTRUCTION(O) | 8 | CASEY | A culvert was grossly over designed since it just needed to handle backwater. | This culvert could have been significantly shortened.
2011-03-08 | Design | Guardrail | RECONSTRUCTION(O) | 8 | RUSSELL | To construct the guardrail end treatments to the most current standards , two Type 7 End Treatments at the intersection of Lincoln Trail Blvd and Hill Street were changed to Type 3 End Treatments to better fit site conditions and eliminate guardrail arou | The guardrail end treatment change was made. The drop box inlets Type 5f were needed on the inlet ends of the pipe used at the Guardrail End Treatments Type 3 at the intersection of Lincoln Trail Blvd and Hill Street.
2011-03-08 | Erosion Control Plan | Silt Fence | RECONSTRUCTION(O) | 8 | CASEY | The proposal lacked a pay item for a Temporary Silt Fence. | A pay item was established for a Temporary Silt Fence.
2011-03-08 | Design | Guardrail | RECONSTRUCTION(O) | 8 | RUSSELL | To construct the guardrail end treatments to the most current standards , two Type 7 End Treatments at the intersection of Lincoln Trail Blvd and Hill Street were changed to Type 3 End Treatments to better fit site conditions and eliminate guardrail arou | The guardrail end treatment change was made. The drop box inlets Type 5f were needed on the inlet ends of the pipe used at the Guardrail End Treatments Type 3 at the intersection of Lincoln Trail Blvd and Hill Street.
2011-03-08 | Design | Access | RECONSTRUCTION(O) | 8 | CASEY | Plans did not provide pedestrian access from KY 72 to the city of Harlan ball fields , the parking area along the Harlan Housing Authority high rise apartment building , or access between US 421 and KY 72. | Added Sidewalk-100mm concrete to complete sidewalks.
2011-03-08 | Erosion Control Plan | Slope Protection | RECONSTRUCTION(O) | 8 | RUSSELL | Bituminous Wedge Curb and Flume Inlet Type 1 were needed at Station 18+00 to Station 26+00 (Lincoln Trail Blvd) to control run-off and erosion of the embankment slopes. | Bituminous Wedge Curb and Flume Inlet Type 1 were used.
2011-03-08 | Erosion Control Plan | Channel Lining | RECONSTRUCTION(O) | 8 | RUSSELL | Channel lining quantities needed to be increased to stabilize ditches and control erosion at various locations throughout the project. | Channel lining quantities were increased.
2011-03-08 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 8 | CASEY | Motorist have a tendency to park on the shoulder around Huff Park during ball games. | Constructing curb and gutter along with the sidewalk should help deter motorists from parking on the shoulder.
2011-03-08 | Structures | RCBC | RECONSTRUCTION(O) | 8 | CASEY | The wing of a culvert could not be constructed per plans due to an existing paved ditch. | The paved ditch had to be removed and replaced to construct the wings.
2011-03-08 | Design | Intersection | RECONSTRUCTION(O) | 8 | RUSSELL | Milling and texturing needed to be added to this project to construct a smooth grade transition at the project limits of Hill Street and the intersection with Lincoln Trail Blvd. | Milling and texturing were added.
2011-03-08 | Design | Plans | RECONSTRUCTION(O) | 8 | CASEY | The pedestrian structure was not designed to meet ADA requirements. | The structure had to be redesigned for handicap ramps which required additional materials to be added to the project.
2011-03-08 | Design | Specifications | RECONSTRUCTION(O) | 8 | RUSSELL | Contract items needed to be modified to construct the 1.5 neoprene expansion dam on the bridge at Station 42+60 in accordance with the new Armor Plate Expansion Dam detail now being used. | Contract items were modified.
2011-03-08 | Geotechnical | Top of Rock | RECONSTRUCTION(O) | 8 | CASEY | Top of rock was lower than expected and sloping. | Mass concrete was used to level the surface and bring it to the planned bottom of the footer grade.
2011-03-08 | Design | Access | RECONSTRUCTION(O) | 8 | CASEY | No pedestrian access was provided from Walnut St. and the new pedestrian bridge to Huff Park , Main Street , and US 421. | As per request by the city of Harlan a 100-MM concrete sidewalk was constructed.
2011-03-08 | Design | Quantities | RECONSTRUCTION(O) | 8 | CASEY | There was not enough Channel Lining Class II in the proposal. | Increase the amount of Channel Lining Class II.
2011-03-08 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 8 | RUSSELL | A change order was necessary to modify contract items and establish new items as a part of a Value Engineering Proposal submitted by the contractor. | The Value Engineering Proposal eliminated the lime stabilized roadbed and utilized Tensar Geogrid which was placed on the subgrade and then DGA was place on top of the Geogrid. No additional working days were allowed for this change order.
2011-03-08 | Geotechnical | Top of Rock | RECONSTRUCTION(O) | 8 | CASEY | The rock line in two locations was higher than anticipated. | The two piers were changed from footers on piling to spread footers on rock.
2011-03-08 | Design | Omission | RECONSTRUCTION(O) | 8 | CASEY | Plans showed flowable fill and steel sheeting to contain flowable fill , however no pay quantities were set up on the project. | The price negotiated for this item was agreed on by doubling the invoice cost.
2011-03-08 | Design | Omission | RECONSTRUCTION(O) | 8 | CASEY | Additional curb and gutter was needed. | Curb and gutter was added in a change order.
2011-03-08 | Drainage | Pipes | RECONSTRUCTION(O) | 8 | CASEY | Water was seeping out of fill while benching operations were taking place. | Perforated pipe was added along the toe of the existing fill.
2011-03-08 | Structures | Omission | RECONSTRUCTION(O) | 8 | CASEY | Nothing was provided to retain the fill material at an abutment for the pedestrian bridge. | Wing walls were added to retain fill material as well as to allow the construction of the proposed sidewalk that ties Clover Street and the Harlan City School.
2011-03-08 | Structures | Fencing | RECONSTRUCTION(O) | 8 | CASEY | It was felt that a fence with barbed wire could pose a safety problem for the public. | Chain link fence was used instead of Type I ROW fencing.
2011-03-08 | Pavement | Design | RECONSTRUCTION(O) | 8 | CASEY | It was felt that Class I Base was not adequate to sustain the heavy truck traffic on the roadway. | Class K Base was used instead of Class I Base.
2011-02-15 | Drainage | Culvert | MAJOR WIDENING(O) | 5 | OLDHAM | Sheet piling was not needed in the construction of Box Culvert. The cost for this item was deducted. | Sheet piling could have been incidental to culvert construction for the original bid item.
2011-02-15 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 5 | OLDHAM | Road was currently constructed on a shale embankment; £crust over a mud hole¥. Had to remove and add embankment to stabilize. | Could have designed to remove old road in original design rather than using existing and widening outside. This may have realized some savings.
2011-02-15 | Design | Phasing | MAJOR WIDENING(O) | 5 | OLDHAM | The first Section was let with a lot of good rock waste material. Then this Section was let , which could have used the material from the previous letting for embankment. | Project size/break should not have been changed at the last minute. This issue needs to be considered when deciding on or funding construction sections. This was , most likely , an administrative decision.
2011-02-15 | Pavement | Omission | MAJOR WIDENING(O) | 5 | OLDHAM | Pavement markers were not included in the plans. | A more thorough review of the plans may have caught this omission.
2011-02-15 | Design | Omission | MAJOR WIDENING(O) | 5 | OLDHAM | Ride Quality Adjustment was not included as a bid item. | There is no longer a bid item for Ride Quality Adjustment.
2011-02-15 | Design | Special Note | MAJOR WIDENING(O) | 5 | OLDHAM | The Special Note for QC/QA Specifications for Aggregate Acceptance was removed at the request of both the District and Contractor. The reason for the removal of this note is twofold. The Federal Highway Administration only allowed this note to be used on | Removing the special note alleviated the difficulties this problem presents to the project. The Division of Materials agreed to the removal of this special note.
2011-02-15 | Design | Omission | MAJOR WIDENING(O) | 5 | OLDHAM | A material specification was not made in the plans. | A Change Order to specify the material was required because of SiteManager.
2011-02-15 | Maintenance of Traffic | Plan | MAJOR WIDENING(O) | 5 | OLDHAM | Traffic control plans were not detailed in this area. | This project may have benefitted from a Constructability Review.
2011-02-15 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 5 | OLDHAM | Silt traps were not included in the plans. | A more thorough review of the plans may have caught this omission.
2011-02-15 | Maintenance of Traffic | Shoulders | MAJOR WIDENING(O) | 5 | OLDHAM | Shoulder design was not of adequate depth to handle traffic during construction. | Two layers of base were added on shoulders (full depth) for traffic control to allow for driving on shoulders. Traffic diversion during construction needs to be considered in design of pavements. This may have been identified with a constructability re
2011-02-15 | Design | Omission | MAJOR WIDENING(O) | 5 | OLDHAM | Additional turning lanes could have been used at major approaches. | This may be addressed now under new turning lane policy. It is easier to include as part of the original project rather than retrofit later.
2011-01-27 | Right-of-Way | Coordination | RECONSTRUCTION(O) | 11 | WHITLEY | Right of way had not been obtained for Parcels No. 4 and No. 5 when the project was let. As a result , the embankments Right of Sta. 60+70 through 66+00 and the approaches Left and Right of Sta. 65+00 could not be constructed. The contractor was requir | A Change Order established a lump sum item to reimburse the contractor to place this stockpiled material at the above stations according to plans and specifications.
2011-01-27 | Right-of-Way | Coordination | RECONSTRUCTION(O) | 11 | WHITLEY | Right of way had not been obtained for Parcels No. 4 and No. 5 when the project was let. As a result , the embankments Right of Sta. 60+70 through 66+00 and the approaches Left and Right of Sta. 65+00 could not be constructed. The contractor was requir | A Change Order established a lump sum item to reimburse the contractor to place this stockpiled material at the above stations according to plans and specifications.
2011-01-27 | Construction | Earthwork | RELOCATION(O) | 11 | LAUREL | Slopes were flattened from the original design for ease of mowing during future maintenance cycles. | The need for this work was not discovered until well after completion of all other contract items for corrective work.
2011-01-27 | Drainage | Pipes | RECONSTRUCTION(O) | 11 | WHITLEY | Drainage from the original plans was changed due to clear zone criteria. | Sloped Box Inlet/Outlets were added to the ends of the entrance pipes at certain locations.
2011-01-27 | Construction | Revisions | RECONSTRUCTION(O) | 11 | WHITLEY | A 12' field entrance was constructed on the left side of the AA Highway at Sta. 197+30. The plans indicated an existing 24 inch entrance pipe at this location. The actual size of the existing pipe was 42 inches. Construction Revision No.2 required wide | Additional 42 inch pipe was necessary for this revision because the existing pipe was to be extended 20 feet on each end with metal end sections installed.
2011-01-27 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 11 | WHITLEY | The plans for the project specified an application of a moisture barrier on the subgrade of the AA Approach section. Part of this item was eliminated due to the nature of the material from which the subgrade was constructed. | A Change Order was established to adjust quantities to reflect what was actually used for this construction item.
2011-01-27 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 11 | WHITLEY | The plans for the project specified an application of a moisture barrier on the subgrade of the AA Approach section. Part of this item was eliminated due to the nature of the material from which the subgrade was constructed. | A Change Order was established to adjust quantities to reflect what was actually used for this construction item.
2011-01-27 | Construction | Revisions | RECONSTRUCTION(O) | 11 | WHITLEY | A 12' field entrance was constructed on the left side of the AA Highway at Sta. 197+30. The plans indicated an existing 24 inch entrance pipe at this location. The actual size of the existing pipe was 42 inches. Construction Revision No.2 required wide | Additional 42 inch pipe was necessary for this revision because the existing pipe was to be extended 20 feet on each end with metal end sections installed.
2011-01-27 | Erosion Control Plan | Silt Fence | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans were not in compliance with the Clean Water Act. | Items such as Rock Silt Fence and Silt Fence were added in accordance with the requirements of the Clean Water Act.
2011-01-27 | Erosion Control Plan | Silt Fence | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans were not in compliance with the Clean Water Act. | Items such as Rock Silt Fence and Silt Fence were added in accordance with the requirements of the Clean Water Act.
2011-01-27 | Design | Omission | RELOCATION(O) | 11 | WHITLEY | Bid items that were included on the summary sheets were excluded from the plans. | Someone on the project design team should have double checked quantities and bid items.
2011-01-27 | Design | Plans | RECONSTRUCTION(O) | 11 | WHITLEY | After the slopes on the north end of KY 9 (AA Highway) approach to this project were constructed and the roadway was prepared for paving , a plan error was discovered. | To correct this error , the slopes were reshaped , the roadway ditches were moved , and the subgrade was reshaped.
2011-01-27 | Design | Plans | RECONSTRUCTION(O) | 11 | WHITLEY | After the slopes on the north end of KY 9 (AA Highway) approach to this project were constructed and the roadway was prepared for paving , a plan error was discovered. | To correct this error , the slopes were reshaped , the roadway ditches were moved , and the subgrade was reshaped.
2011-01-27 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 11 | WHITLEY | Since paving for the mainline portion of the roadway was not included in the contract , access was blocked at the intersection with KY 546. | Items such as three Type III Barricades and one Road Closed sign had to be used.
2011-01-27 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 11 | WHITLEY | Since paving for the mainline portion of the roadway was not included in the contract , access was blocked at the intersection with KY 546. | Items such as three Type III Barricades and one Road Closed sign had to be used.
2011-01-27 | Design | Standard Drawings | RECONSTRUCTION(O) | 11 | WHITLEY | Two metal end sections were constructed at the entrance to the Maysville-Mason County Industrial Park. The Final Inspection Report required that the metal end sections be modified to meet the requirements for parallel pipe. | This item required removing the existing safety bars , installing the corrected type bars , and delivering the extra set of bars to the Mason County Maintenance Lot.
2011-01-27 | Design | Standard Drawings | RECONSTRUCTION(O) | 11 | WHITLEY | Two metal end sections were constructed at the entrance to the Maysville-Mason County Industrial Park. The Final Inspection Report required that the metal end sections be modified to meet the requirements for parallel pipe. | This item required removing the existing safety bars , installing the corrected type bars , and delivering the extra set of bars to the Mason County Maintenance Lot.
2011-01-27 | Drainage | Pipes | RECONSTRUCTION(O) | 11 | WHITLEY | Drainage from the original plans was changed due to clear zone criteria. | Sloped Box Inlet/Outlets were added to the ends of the entrance pipes at certain locations.
2011-01-27 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 11 | WHITLEY | All traffic using a certain portion of the roadway must enter and exit via reconstructed KY 8. | Certain items were necessary to provide additional traffic control items for the safety of the traveling public during construction of the new bridge.
2011-01-27 | Maintenance of Traffic | Omission | SAFETY-HAZARD ELIM(P) | 11 | WHITLEY | All traffic using a certain portion of the roadway must enter and exit via reconstructed KY 8. | Certain items were necessary to provide additional traffic control items for the safety of the traveling public during construction of the new bridge.
2011-01-27 | Construction | Contracts | RELOCATION(O) | 11 | LAUREL | Since funding for an existing HES project had been depleted , a decision was made to combine it with this project. | Collaboration and creativity , such as this , should be encouraged in similar types of situations to provide efficiency in project delivery.
2011-01-27 | Construction | Coordination | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified a traffic signal to be constructed at the intersection of KY 9 (AA Highway) and US 62. However , the separate paving contract for US 62 was not completed until the 1996 construction season. | This item was deleted from the contract.
2011-01-27 | Construction | Coordination | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified a traffic signal to be constructed at the intersection of KY 9 (AA Highway) and US 62. However , the separate paving contract for US 62 was not completed until the 1996 construction season. | This item was deleted from the contract.
2011-01-27 | Drainage | Ditches | RECONSTRUCTION(O) | 11 | WHITLEY | Due to the quality of rock encountered during roadway excavation , portions of the designed rock ditches were to be constructed using shot rock found on the project. | The shot rock was used instead of Channel Lining Class II and Channel Lining Class III saving the department money.
2011-01-27 | Drainage | Ditches | RECONSTRUCTION(O) | 11 | WHITLEY | Due to the quality of rock encountered during roadway excavation , portions of the designed rock ditches were to be constructed using shot rock found on the project. | The shot rock was used instead of Channel Lining Class II and Channel Lining Class III saving the department money.
2011-01-27 | Utilities | Existing Utilities | RELOCATION(O) | 11 | WHITLEY | An unidentified sanitary sewer needed to be relocated. | Have roadway design firm take on utility design work to improve coordination; SUE in urban locations.
2011-01-27 | Design | Coordination | RELOCATION(O) | 11 | LAUREL | Ramp grades for design of interchange did not consider matching future mainline pavement. | Ramp grades were raised to match the surfacing on a future rehabilitation project scheduled for mainline I-75. This did save the need to dig out under the bridge for a surfacing project scheduled at a later date.
2011-01-27 | Construction | Coordination | SAFETY-HAZARD ELIM(P) | 11 | WHITLEY | This project was let prior to the completion of the connector road to KY 8. The start of the project delayed from November 1994 until September 1995 when the work for the lighting phase of the contract could commence. Also , the signing phase was delay | A portion of Change Order 2 compensated the contractor for additional costs of materials incurred as a result of these delays.
2011-01-27 | Construction | Coordination | I-CHANGE RECONST(O) | 11 | WHITLEY | This project was let prior to the completion of the connector road to KY 8. The start of the project delayed from November 1994 until September 1995 when the work for the lighting phase of the contract could commence. Also , the signing phase was delay | A portion of Change Order 2 compensated the contractor for additional costs of materials incurred as a result of these delays.
2011-01-27 | Utilities | Relocation | I-CHANGE RECONST(O) | 11 | WHITLEY | Prior to the completion of the subgrade and bituminous pavement on the ramps to KY 8 (Connector Left) , four inch conduit was placed for the electrical cables to poles #2 and #3. Due to the subsequent widening of these ramps the ends of the conduit wer | A Change Order was established for the additional costs involved in locating and extending the conduit beyond the paving limits.
2011-01-27 | Utilities | Relocation | SAFETY-HAZARD ELIM(P) | 11 | WHITLEY | Prior to the completion of the subgrade and bituminous pavement on the ramps to KY 8 (Connector Left) , four inch conduit was placed for the electrical cables to poles #2 and #3. Due to the subsequent widening of these ramps the ends of the conduit wer | A Change Order was established for the additional costs involved in locating and extending the conduit beyond the paving limits.
2011-01-27 | Construction | Safety | RELOCATION(O) | 11 | LAUREL | To improve safety , slope adjustments were made. This action allowed guardrail to be removed and reset out of the clear zone. | This was part of the Design-Build process.
2011-01-27 | Design | Quantities | RECONSTRUCTION(O) | 11 | WHITLEY | Steel reinforcements were miscalculated as per the original plans. | This reinforcement steel became the property of the Transportation Cabinet and was delivered to the Mason County Maintenance lot.
2011-01-27 | Design | Quantities | RECONSTRUCTION(O) | 11 | WHITLEY | Steel reinforcements were miscalculated as per the original plans. | This reinforcement steel became the property of the Transportation Cabinet and was delivered to the Mason County Maintenance lot.
2011-01-27 | Utilities | Relocation | RELOCATION(O) | 11 | LAUREL | Unforeseen utility relocations were needed for the HES portion of this project. | None.
2011-01-27 | Geotechnical | Slides | RELOCATION(O) | 11 | WHITLEY | A slide caused the roadway to settle approximately 8 inches from the centerline to edge of fill slope. | The Geotech Branch suggested: excavate the entire settled area at least 10 feet below proposed roadway elevation. Proof roll and compact the remaining embankment and place an 8 inch perforated pipe along the vertical face of the existing wall. Then const
2011-01-27 | Drainage | Culvert | RECONSTRUCTION(O) | 11 | WHITLEY | The plans for this project required extending a culvert at Sta. 226+51.65 in order to widen the embankments in the area. Portions of the barrel on the inlet and outlet ends were to be removed and additional length to be constructed. | During construction it was determined that the side walls and the bottom slab of the existing culvert could be left in place , removing only the top slab and the wing walls.
2011-01-27 | Drainage | Culvert | RECONSTRUCTION(O) | 11 | WHITLEY | The plans for this project required extending a culvert at Sta. 226+51.65 in order to widen the embankments in the area. Portions of the barrel on the inlet and outlet ends were to be removed and additional length to be constructed. | During construction it was determined that the side walls and the bottom slab of the existing culvert could be left in place , removing only the top slab and the wing walls.
2011-01-27 | Geotechnical | Subsurface | RELOCATION(O) | 11 | WHITLEY | Coal seams and deep mine openings were encountered during excavation. Additional funding was needed for granular embankment; this item was overrun while excavating and replacing a 2' to 3' coal seam that was encountered. | Could do more extensive geotech exploration; however , this may cost more than just fixing it during construction.
2011-01-27 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified the use of a woven wire fence for right of way throughout the project. However , portions of the approaches along the AA Highway are in front of urban residential properties. | It was more suitable to use chain link fence in front of the urban residential properties so a Change Order was established to add the quantities needed to fence these areas using chain link fence.
2011-01-27 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified the use of a woven wire fence for right of way throughout the project. However , portions of the approaches along the AA Highway are in front of urban residential properties. | It was more suitable to use chain link fence in front of the urban residential properties so a Change Order was established to add the quantities needed to fence these areas using chain link fence.
2011-01-27 | Structures | Communication | RELOCATION(O) | 11 | LAUREL | Bridge beams on Single Point Urban Interchange (SPUI) were exposed. | After the design-build firm was selected , a decision was made to cover all exposed areas of bridge beams with bridge decking to improve aesthetics.
2011-01-27 | Construction | Contracts | RELOCATION(O) | 11 | LAUREL | Work began and landscaping costs were incurred in anticipation of change order being approved. | Funding should have been approved before any work began.
2011-01-27 | Design | Standard Drawings | RECONSTRUCTION(O) | 11 | WHITLEY | During the final inspection on this project it was noted that the bituminous curb had been constructed in accordance with Standard Drawing RPM-100-04. Standard drawing RPM-100-05 (the new standard) had been modified to decrease the height of the curb fro | Since this change in height was missed by both parties in the contract , it was agreed that the curb removal and replacement would be shared by both parties.
2011-01-27 | Design | Standard Drawings | RECONSTRUCTION(O) | 11 | WHITLEY | During the final inspection on this project it was noted that the bituminous curb had been constructed in accordance with Standard Drawing RPM-100-04. Standard drawing RPM-100-05 (the new standard) had been modified to decrease the height of the curb fro | Since this change in height was missed by both parties in the contract , it was agreed that the curb removal and replacement would be shared by both parties.
2011-01-27 | Design | Quantities | RELOCATION(O) | 11 | WHITLEY | Granular embankment undercutting was needed due to unstable roadway foundation material that was heavily saturated with water. | This may have been avoided if project was let at a different time of the year.
2011-01-27 | Design | Quantities | RECONSTRUCTION(O) | 11 | WHITLEY | The plan quantity for Structure Excavation Common was in error. | A Change Order was required to reflect field measured quantities.
2011-01-27 | Design | Quantities | RECONSTRUCTION(O) | 11 | WHITLEY | The plan quantity for Structure Excavation Common was in error. | A Change Order was required to reflect field measured quantities.
2011-01-27 | Maintenance of Traffic | Lighting | I-CHANGE RECONST(O) | 11 | WHITLEY | After completion of the grade and drain contract , the locations of the poles for the high mast lighting were not accessible to the contractor. | The contractor was compensated for the additional costs of constructing access ramps for equipment and restoring these areas after completion of the work. The ramps were left in a condition that provided access to the electrical controls for maintenance
2011-01-27 | Maintenance of Traffic | Lighting | SAFETY-HAZARD ELIM(P) | 11 | WHITLEY | After completion of the grade and drain contract , the locations of the poles for the high mast lighting were not accessible to the contractor. | The contractor was compensated for the additional costs of constructing access ramps for equipment and restoring these areas after completion of the work. The ramps were left in a condition that provided access to the electrical controls for maintenance
2011-01-27 | Construction | Revisions | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified an entrance to be constructed on the right of Sta. 51+75 at the Garrison Lane Approach. This entrance was widened and the grade was flattened to give better access to the property through Construction Revision No. 1. | Additional pipe was necessary for this revision.
2011-01-27 | Construction | Revisions | RECONSTRUCTION(O) | 11 | WHITLEY | The project plans specified an entrance to be constructed on the right of Sta. 51+75 at the Garrison Lane Approach. This entrance was widened and the grade was flattened to give better access to the property through Construction Revision No. 1. | Additional pipe was necessary for this revision.
2011-01-27 | Traffic | Lighting | RELOCATION(O) | 11 | LAUREL | Actual field conditions revealed that lighting was insufficient on a ramp. | The original lighting specifications could have been higher.
2011-01-13 | Geotechnical | Investigation | BRIDGE REPLACEMENT(P) | 10 | PERRY | Culvert (triple barrel ô non yielding foundation) elevation was lowered to better match site conditions (rock elevation.) | Additional cores at the structure location would potentially have prevented this field adjustment.
2011-01-13 | Geotechnical | Investigation | BRIDGE REPLACEMENT(P) | 10 | PERRY | Perforated pipe was used to drain an area of saturated material prior to fill placement. | Additional site investigation , accompanying plan note , and related bid items would have prevented this requiring a change order to mitigate.
2011-01-13 | Design | Omission | RECONSTRUCTION(O) | 10 | ESTILL | A metal end section type 3-15 was shown on the plans to be installed but no bid item was in the contract for this item. | A Change Order was necessary to establish a bid item for the metal end section.
2011-01-13 | Traffic | Omission | RECONSTRUCTION(O) | 10 | MORGAN | No Signalization was set up for the Somerset Bypass and KY 192 intersection. | A Change Order was necessary to increase signalization quantities in order to install signalization at this intersection.
2011-01-13 | Design | Guardrail | RECONSTRUCTION(O) | 10 | MORGAN | The guardrail end treatments in the plans did not meet the current safety and design standards for guardrail systems. | A Change Order was needed to install the correct guardrail end treatments throughout the project in accordance with the current safety and design standards for guardrail systems.
2011-01-13 | Design | Guardrail | RECONSTRUCTION(O) | 10 | MORGAN | The guardrail end treatments in the plans did not meet the current safety and design standards for guardrail systems. | A Change Order was needed to install the correct guardrail end treatments throughout the project in accordance with the current safety and design standards for guardrail systems.
2011-01-13 | Design | Quantities | RECONSTRUCTION(O) | 10 | ESTILL | A metal end section type 3-24 was originally set up in the contract but was not needed. | This item was deleted from the contract.
2011-01-13 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | Bore and Jack ô bid item omission for plan work (waterline work). Utility work that could not be done prior to construction was noted on plans , but contract items were not included to allow for the work. | A more thorough review of the plans may have caught this.
2011-01-13 | Right-of-Way | Easements | RECONSTRUCTION(O) | 10 | ESTILL | As part of a right-of-way concession , a parking lot was constructed for Western Kentucky University. | Additional quantities of Crushed Stone Base , Bituminous Base , and Bituminous Surface were added to the contract. Also , a bid item for site preparation was set up which consisted of clearing , staking , and site grading of the lot and a manhole wa
2011-01-13 | Pavement | Quantities | RECONSTRUCTION(O) | 10 | MORGAN | There was an underrun of bituminous base class K used on the project. | A Change Order was necessary to decrease the quantities of bituminous base class K.
2011-01-13 | Drainage | Omission | RECONSTRUCTION(O) | 10 | ESTILL | An existing 18 culvert pipe at approximately Station 32+07 in the intersection of Campbell Lane and Industrial Drive was shown to be safeloaded on the plans. However , no bid item was setup to accomplish this work. | The contractor submitted a bid for safeloading the pipe. Instead , upon further inspection of this pipe it was decided to remove the pipe and fill in this area.
2011-01-13 | Pavement | Quantities | RECONSTRUCTION(O) | 10 | MORGAN | There was an excessive underrun of Crushed Stone Base quantity actually used on the project. | The unit price for Crushed Stone Base was adjusted. The agreed unit price for this supplemental item was calculated using the excessive underrun formula as listed in Section 104.02.02 of the Standard Specifications.
2011-01-13 | Drainage | Coordination | RECONSTRUCTION(O) | 10 | ESTILL | Slotted Drain Pipe was setup in the original contract at Station 51+30 to Station 53+10. However this area passes through an entrance that is to be paved with bituminous pavement rather than entrance pavement in accordance with the right-of-way agreement | A bid item was established for PCC Pavement in order to provide a suitable surrounding for the installation of the slotted drain pipe.
2011-01-13 | Traffic | Omission | RECONSTRUCTION(O) | 10 | ESTILL | Removal of signal equipment at an intersection was shown on the contract plans but omitted from the bid items. | There was an increase in the bid item Remove Signal Equipment to allow the existing signal heads , messenger cable , and controller to be removed at this location.
2011-01-13 | Pavement | Thickness | RECONSTRUCTION(O) | 10 | ESTILL | The project was originally set up to have 5-3/4 inches of wedging throughout the length of the project. Actual field conditions warranted using approximately 8 inches of wedging in order to match the proposed grade. | Bituminous Base was increased 1435 tons in order to accomplish this work.
2011-01-13 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 10 | ESTILL | An existing junction box located at Station 53+81 was originally setup to remain in use on the project. However , the junction box was broken and cracked on the top and side slabs. | It was decided that the installation of the 24 culvert pipe would further damage the box beyond repair. Therefore , a new junction box with a top grate was installed at this location.
2011-01-13 | Design | Guardrail | RECONSTRUCTION(O) | 10 | MORGAN | The guardrail system in the plans did not meet current design and safety standards. | Additional guardrail was needed to construct a guardrail system that is in accordance with current design and safety standards.
2011-01-13 | Design | Guardrail | RECONSTRUCTION(O) | 10 | MORGAN | The guardrail system in the plans did not meet current design and safety standards. | Additional guardrail was needed to construct a guardrail system that is in accordance with current design and safety standards.
2011-01-13 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | Part width construction required full depth shoulder construction. The pavement quantity was accordingly adjusted. | The project would have benefitted from a Constructability Review. Best practices have been to pave shoulders in these cases full depth. If the pavement design for the temporary condition were developed for reduced speed , volumes , and other considera
2011-01-13 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 10 | PERRY | Guardrail changes were needed according to field conditions. | During design phase , guardrail needs of completed grade are very difficult to account for in all cases.
2011-01-13 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 10 | PERRY | Guardrail changes were needed according to field conditions. | During design phase , guardrail needs of completed grade are very difficult to account for in all cases.
2011-01-13 | Drainage | Pipe Sizing | RECONSTRUCTION(O) | 10 | MORGAN | During the final inspection of the project , it was noted that there was insufficient drainage capacity alongside the existing 24 inch pipe at an entrance Lt. Station 57+35 on the KY 769 approach. | A Change Order was needed to establish additional quantities of 24 inch entrance pipe to be placed alongside the existing 24 inch pipe.
2011-01-13 | Design | Omission | RECONSTRUCTION(O) | 10 | ESTILL | The typical sections show Bituminous Pavement Milling and Texturing required along the edge of the existing pavement. However this quantity was omitted from the bid items. | A Change Order was necessary to establish these items in order to construct the edge key as required in the contract plans.
2011-01-13 | Geotechnical | Sinkhole | RECONSTRUCTION(O) | 10 | ESTILL | An existing sinkhole was utilized for drainage on this project. This sinkhole had to be cleaned out to find the exact location of the throat. | Since this work was not set up in the original contract it was performed on a cost-plus basis.
2011-01-13 | Right-of-Way | Easements | RECONSTRUCTION(O) | 10 | MORGAN | There was a right of way dispute with Parcel No. 75. | An entrance was constructed Lt. Station 75+30 on the KY 192 approach. The construction of this entrance was required in the right-of-way settlement of Parcel No. 75 and required entrance pipe.
2011-01-13 | Drainage | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | Drainage adjustments outside the project limits were necessary to allow the drainage to function as it had prior disturbances from this project. | Further investigation of existing structures could potentially have discovered this issue.
2011-01-13 | Traffic | Omission | RECONSTRUCTION(O) | 10 | ESTILL | The contractor was asked after the completion of the project to install Left Turn Yield on Green signs at each leg of the intersection of Campbell Lane and Nashville Road. | These signs were not required by the plans and the contractor had to remobilize in order to install these signs.
2011-01-13 | Drainage | Existing Pipe | BRIDGE REPLACEMENT(P) | 10 | PERRY | Proposed fill in vicinity of approach road exaggerated drainage in an area prone to flooding. Culvert pipe was added to assist an existing 60 inch pipe. | Further investigation of existing drainage situation would have allowed the problem to have been addressed prior to letting.
2011-01-13 | Design | Quantities | RECONSTRUCTION(O) | 10 | ESTILL | The typical sections on the project showed Crushed Stone Base rather than DGA Base to be used throughout the project. However , the quantities for these items were bid in reverse. | A Change Order was necessary to reverse these quantities in order to reflect the intent of the typical sections.
2011-01-13 | Pavement | Design | RECONSTRUCTION(O) | 10 | MORGAN | The pavement design on this project was inadequate. There were concerns about the pavement bonding properly. | A Change Order was necessary to place a 1/2 inch thick bituminous concrete scratch course over the mainline driving lanes for the entire length of the project.
2010-12-02 | Maintenance of Traffic | Shoulders | DESIGN ENGINEERING(O) | 12 | JOHNSON | Shoulder pavement structure was insufficient for temporary traffic use as directed by MOT plan. Additional paving quantities were necessary to improve structure. | Coring of the existing shoulder for depth would facilitate MOT and establishment of necessary contract items.
2010-12-02 | Design | Slopes | RECONSTRUCTION(O) | 12 | JOHNSON | Several short 1:2 slopes were constructed on adjacent properties. These slopes are difficult for the property owners to maintain. | Consideration should be given to using small retaining walls instead of the 1:2 slopes. It was discussed that modular block retaining walls may be an alternative for these small walls.
2010-12-02 | Maintenance of Traffic | Plan | RECONSTRUCTION(O) | 12 | MARTIN | The traffic control plan had to be modified due to insufficient roadway width. | Check space requirements for traffic control plans.
2010-12-02 | Construction | Public Relations | RECONSTRUCTION(O) | 12 | JOHNSON | While over 90 entrances were maintained over 3-4 construction phases , and at no time was any adjacent property prevented access to US 127 , there were still newspaper articles written concerning construction impacts on local businesses. | More effort should be made to minimize impacts of construction on local businesses.
2010-12-02 | Geotechnical | Slides | BRIDGE REPLACEMENT(P) | 12 | FLOYD | Embankment failure as a result of groundwater from undetermined source and/or potentially karst conditions. Removed saturated material and installed 2 foot foundation for fill out of Crushed Aggregate No. 2's and geotextile fabric. | When site investigation indicates karst conditions and groundwater is anticipated , provide for means of drainage (in this case #2's and fabric.)
2010-12-02 | Maintenance of Traffic | Striping | RECONSTRUCTION(O) | 12 | JOHNSON | The amount of temporary striping in the contract was about one-half of the quantity actually needed. | More care should be taken when reviewing quantities before letting.
2010-12-02 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 12 | JOHNSON | Additional detour signage was necessary on the project. | Additional consideration should be given to detour signage during the design process.
2010-12-02 | Construction | Contracts | RECONSTRUCTION(O) | 12 | JOHNSON | Incentives were not thought to be a good idea because maintenance of traffic concerns restricted the contractor's working areas. | Incentives may have deserved more consideration during the pre-construction phase.
2010-12-02 | Utilities | New Utilities | RECONSTRUCTION(O) | 12 | JOHNSON | There were problems with signal pole and utility locations conflicting. | Traffic control plans should be begun earlier in the process and coordinated with the other plans.
2010-12-02 | Environmental | Asbestos | RECONSTRUCTION(O) | 12 | MARTIN | Asbestos was discovered on the site and had to be removed. | Unavoidable.
2010-12-02 | Construction | Contracts | RECONSTRUCTION(O) | 12 | JOHNSON | The project was let June 24 , 1994 and the work order was issued August 9 , 1994. This did not allow for the utilization of the full construction season , pushing more of the construction back to the winter months. | The timing of the letting and work order could have been completed earlier to utilize more of the construction season.
2010-12-02 | Design | Entrance | RECONSTRUCTION(O) | 12 | JOHNSON | Entrance pavement thickness was not given proper consideration. | Bituminous pavements should have thicker base courses at commercial entrances as compared to residential entrances. It must be noted that the Design manual indicates the minimum thickness of pavement for entrances; however , these designs should be inc
2010-12-02 | Pavement | Design | RECONSTRUCTION(O) | 12 | MARTIN | The Pavement design for the detour tie-in was not adequate. | Cement treated soil was used to stabilize the subgrade.
2010-12-02 | Construction | Public Relations | RECONSTRUCTION(O) | 12 | JOHNSON | Meetings with the contractor were held every Thursday , and representatives of the local Mayor's offices were invited. These representatives usually declined to attend the meetings. | More effort should be used to gain the involvement of local municipalities.
2010-12-02 | Pavement | Design | RECONSTRUCTION(O) | 12 | JOHNSON | High early strength concrete was considered a poor idea for the entire project because of the restricted work areas , however high early strength concrete was used in some areas to speed up construction. | Bituminous concrete pavements would have sped up construction , but they would have required more frequent maintenance , thus disrupting traffic in the future.
2010-12-02 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 12 | JOHNSON | There was no pay item for stop bars and arrows for temporary entrances. | A pay item for stop bars and arrows should be included for temporary entrances.
2010-12-02 | Design | Drainage | RECONSTRUCTION(O) | 12 | MARTIN | Under drains in the grade and drain contract would have been destroyed during the stabilization operation. | Include under drains in the paving contract.
2010-12-02 | Design | Access | RECONSTRUCTION(O) | 12 | JOHNSON | There was a lack of adequate detail for grades and superelevations on side roads. | Intersection details and cross-sections may need to run farther back.
2010-12-02 | Design | Omission | BRIDGE REPLACEMENT(P) | 12 | FLOYD | R/W Monumentation according to current policy (Type 1 and Witness Posts) was not provided for in contract bid items. | Plan Review process typically catches issues of this type.
2010-12-02 | Environmental | Underground Tank | RECONSTRUCTION(O) | 12 | MARTIN | Three underground storage tanks (USTS) were discovered , and had to be removed. | An environmental , or historical study of this site may have been able to determine the presence of these tanks. However in many cases UST's are not documented making this change unavoidable.
2010-12-02 | Construction | Coordination | RECONSTRUCTION(O) | 12 | JOHNSON | The project was extremely difficult to construct with the amount of development that had occurred through the area. Other sections of Alexandria Pike had been reconstructed in recent years , but this particular section had been delayed. | This section would have been easier to construct if it had been built before the increase in development in the area. The Cabinet should take rate of development into account when planning project dates to try to avoid this situation.
2010-12-02 | Design | Omission | RECONSTRUCTION(O) | 12 | JOHNSON | Critical items were missed. | Cross-sections should be provided in cluttered areas so that critical items are not missed.
2010-12-02 | Pavement | Design | RECONSTRUCTION(O) | 12 | JOHNSON | The subgrade was changed from mechanical stabilization to #2 stone because it is difficult to stabilize subgrades in the small construction segments required for maintenance of traffic. A non-treated drainage blanket was also used. These first two items | Pavement design should undergo a thorough constructability review before finalization to ensure that the design will not need to be altered during the construction phase.
2010-12-02 | Drainage | Ponding | RECONSTRUCTION(O) | 12 | MARTIN | Retaining wall in from of Red Lobster has caused a wetland situation. | Retaining wall could have possibly been eliminated , if that proved impractical then a plan for proper drainage of location to remove excess water.
2010-12-02 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 12 | JOHNSON | Several businesses along the project had moveable signs that indicated the location of their entrance. These signs were limited in size and could be moved as construction dictated. | The Cabinet may wish to consider providing or compensating businesses for these moveable signs , however some standards concerning size and construction must be developed.
2010-12-02 | Design | Communication | DESIGN ENGINEERING(O) | 12 | JOHNSON | Rumble Strips Type 1 (02693) specified , but were replaced with Milled-In Rumble Strips. | District staff recommend discontinued or limited use of Rumble Strips Type 1 because of maintenance problems , snow removal , and concerns about vehicle skids especially in horizontal curves as in this case.
2010-12-02 | Construction | Public Relations | RECONSTRUCTION(O) | 12 | JOHNSON | There were reports that the contractor had left the project for periods of time , however the contractor was never charged a working day when they were not on site. There were also reports that the contractor was going bankrupt , but there were no sign | More effort should be made to educate the public and manage perceptions about the construction project to garner more support.
2010-12-02 | Maintenance of Traffic | Entrances | RECONSTRUCTION(O) | 12 | JOHNSON | A note was included on the plans that required that two lanes be maintained on side roads at all times. This was not possible while also reconstructing the side road entrances. | All design notes should undergo a thorough constructability review before finalization to ensure that the design will not need to be altered during the construction phase.
2010-12-02 | Structures | Curved Steel Bridge | DESIGN ENGINEERING(O) | 12 | JOHNSON | Due to geometry , a structure design revision was necessary to provide a temporary anchor at the inside girder prior to deck installation in order to prevent uplift. | Efforts should be made to improve designer's awareness of the geometric impacts on structure designs as well as to increase awareness of the intermediate forces at play during the various phases of construction. At the very least , changes should be doc
2010-12-02 | Utilities | Inaccurate Location | RECONSTRUCTION(O) | 12 | JOHNSON | A change order for over $500 , 000 occurred because of waterline overruns. The waterlines of three old districts were to be combined into one new system There were no accurate records of the old line locations Also , some utilities were relocated inac | Greater oversight is needed during utility relocation and all relocated lines should be marked.
2010-12-02 | Design | Quantities | RECONSTRUCTION(O) | 12 | JOHNSON | Insufficient quantities of stone were set up to maintain traffic. The amount was off by about 50%. | More care should be taken when calculating quantities.
2010-12-02 | Design | Entrance | RECONSTRUCTION(O) | 12 | JOHNSON | Many of the entrances were on steep grades. Some of the fills for the entrances would have affected the buildings or other structures on the accessed property. Tie-ins on the periphery of the project were not detailed or were not clear. | Entrance details should be more closely investigated. Consideration should be given to temporarily paving major entrances in order to maintain them throughout the winter months.
2010-12-02 | Maintenance of Traffic | Changes | DESIGN ENGINEERING(O) | 12 | JOHNSON | MOT details provided per plan had to be changed during construction phase , providing for two additional lane closures as well as related contract items. | Traffic Management Plan policy has since been implemented. MOT plan changes are possible but extensive review/approval process is in place. Constructability Review during design phase is available and recommended. Using plan notes to make them incident
2010-12-02 | Design | Omission | DESIGN ENGINEERING(O) | 12 | JOHNSON | Chip seal and aggregate quantities (Items 00100 and 00103) were omitted from the original contract items. | More thorough review of plans. May have benefitted from a Constructability Review.
2010-12-02 | Design | CAP | RECONSTRUCTION(O) | 12 | MARTIN | Some right-of-way fence was not constructed due to requests from property owners. | Meet with property owners during design process.
2010-12-02 | Design | Adjacent Projects | RECONSTRUCTION(O) | 12 | JOHNSON | Rehabilitation of pavement on the ends of adjacent roadway sections and of sections to be turned over to local governments was not included in the initial contracts. | Rehabilitation of pavement on the ends of adjacent roadway sections and of sections to be turned over to local governments should be included in the initial contracts.
2010-12-02 | Construction | Public Relations | RECONSTRUCTION(O) | 12 | JOHNSON | The necessity to maintain traffic required the contractor to work in small sections. Constructing these small sections usually required the contractor to work different sections every day. This led to the misconception that the contractor did not work e | More effort should be made to educate the public and manage perceptions about the construction project to garner more support.
2010-12-02 | Design | Underground Tank | RECONSTRUCTION(O) | 12 | JOHNSON | Additional underground storage tank removals and their associated quantities were needed on the project. | More research should be done in the design phase to determine the number of underground storage tanks impacted by the project.
2010-12-02 | Construction | Contracts | RECONSTRUCTION(O) | 12 | JOHNSON | Diamond grinding of the pavement will be necessary to provide rideability. No rideability specification was included on this job , but it would have been difficult to enforce since it was necessary to construct the pavement in small sections. | Diamond grinding should be set up in the contract PCC pavement projects so that another contract does not have to be let. This also eliminates problems dealing with pavement markers during the diamond grinding. Having diamond grinding set up in the pavi
2010-12-02 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 12 | JOHNSON | Grade differences between the old and new pavements and how they affect the maintenance of traffic was not addressed in the plans. | Grade differences between the old and new pavements and how they affect the maintenance of traffic should be addressed in the plans.
2010-11-18 | Construction | Revisions | NEW ROUTE(O) | 1 | GRAVES | During construction , several areas of pavement adjacent to but outside the project limits were identified as significantly deteriorated and in need of resurfacing. | The decision was made to extend the paving limits to include the remainder of the interchange ramps to the mainline joints of New Circle Road as well as a section of US 68 to tie into a recent asphalt resurfacing project on the West side of Beaumont Centr
2010-11-18 | Design | Omission | NEW ROUTE(O) | 1 | CALLOWAY | The original design plans and calculations for bid item quantities did not include turning lanes and crossovers. | Turning lanes and crossovers should have been included in the original design plans.
2010-11-18 | Construction | Revisions | NEW ROUTE(O) | 1 | GRAVES | Plans illustrated a lane configuration of turning one of the three through lanes Eastbound into a left turn lane on Sheets R3 and R5 at Burbank Court/Members Way. The existing median crossover was indicated to be removed at Sta. 183+75. Business owners | The decision was made to provide a lane reduction down to two lanes , keep the existing median crossover and provide a left turn lane at the Burbank Court/Members Way/ US 68 intersection. Four additional lane reduction arrows were added to increase safe
2010-11-18 | Traffic | Quantities | NEW ROUTE(O) | 1 | GRAVES | Insufficient quantities were established in the contract to complete the electrical work as detailed in the Project Plans. The affected circuit detailed eight wires , but only one was included in the bid quantity. | Bid item quantities were adjusted appropriately in change order #2.
2010-11-18 | Design | Intersection | NEW ROUTE(O) | 1 | CALLOWAY | The design plans did not include items to transition into an intersection with 2 normal crowns to make a smoother ride. | Designers should consider tie-inÖs and add items for transition. All intersections that are signalized , or might be signalized , should be £Grade Developed¥.
2010-11-18 | Utilities | Inaccurate Location | NEW ROUTE(O) | 1 | GRAVES | During construction , two junction boxes were found to be in conflict with the proposed widened radius at the intersection of US 68 and Alexandria Drive. Plans did not indicate that these boxes would be impacted by construction. | Utility boxes were relocated to allow for intersection to be constructed as planned.
2010-11-18 | Design | Omission | NEW ROUTE(O) | 1 | CALLOWAY | Class II Channel Lining contract bid quantity was insufficient to provide for all areas necessary. | Additional Class II Channel Lining quantities should be included.
2010-11-18 | Traffic | Signs | NEW ROUTE(O) | 1 | GRAVES | Several issues involving signage on the project were encountered , including the use of non-standard signs. | Many changes were made as the project progressed and was opened to traffic. Flexibility in using non-standard signs should be considered especially in unique traffic configuration such as the DCD.
2010-11-18 | Construction | Public Relations | NEW ROUTE(O) | 1 | GRAVES | As a result of the utility delays and subsequent MOT changes , the project was opened to traffic with only two lanes in each direction through the DCD. Considering turning movements , effectively this reduced US 68 to one lane in each direction. Polic | Better communication with the traveling public could have been achieved by emphasizing that while the new configuration was open to traffic , construction through the DCD would continue and extensive delays should be expected. Modeling such changes in t
2010-11-18 | Traffic | Signals | NEW ROUTE(O) | 1 | CALLOWAY | Signals and poles were needed to be installed quickly for safety reasons. | Unavoidable.
2010-11-18 | Drainage | Temporary Drainage | NEW ROUTE(O) | 1 | CALLOWAY | A major flood event occurred that was estimated to exceed the 25-year storm design. Since the temporary crossing was in place at the time , debris built up at this constraint. Extensive bank erosion occurred before debris removal was complete. | Parameters for temporary crossings currently are not intended to provide for flood events similar to this example. On an individual basis , consider requiring larger drainage opening when feasible. Banks were stabilized in this case with durable rock.
2010-11-18 | Utilities | Delays | NEW ROUTE(O) | 1 | GRAVES | Numerous utility conflicts were disclosed at letting and an appropriate Utility Impact Note was included in bid documents. However , during construction , the deadline presented was not met by involved utilities and/or contractors. Additionally , sev | The Contractor filed claim and an administrative settlement was reached that compensated contractor for loss of productivity and changes in MOT. Contractor recommends Cabinet consider using Subsurface Utility Engineering (SUE) on future projects involvin
2010-11-18 | Maintenance of Traffic | Phasing | NEW ROUTE(O) | 1 | CALLOWAY | Considerable public pressure resulted in an earlier than planned reopening of a road that was closed during construction. | Items needed to reopen this road were added to this contract and deleted from the Surfacing contract.
2010-11-18 | Drainage | Ditches | NEW ROUTE(O) | 1 | GRAVES | Plans illustrated installing paved ditches in areas where steeper ditches could not be attained without significant impact on existing drainage systems. | Channel lining was used in these areas in lieu of paved ditches. As a general rule , District 7 PD&P prefers channel lined ditches over paved ditches when extremely flat slopes cannot be avoided. District PD&P involvement / comments should be solicited
2010-11-18 | Design | Elevations | NEW ROUTE(O) | 1 | CALLOWAY | A serious bust on the survey(s) for this project resulted in increased excavation for fill material and increased haul expenses. | Newer survey techniques should alleviate this type of survey bust.
2010-11-18 | Traffic | Coordination | NEW ROUTE(O) | 1 | GRAVES | The contract bid item for Install Sig controller Ty 2070 did not include furnishing the controller. At an earlier stage of the project development process , LFUCG was responsible for supplying the Cabinet with the appropriate equipment for this item of | A new bid item was negotiated that included both supplying and installing the Signal Controller.
2010-11-18 | Construction | Safety | NEW ROUTE(O) | 1 | GRAVES | During the ramp closures and the weekend US 68 closure , the desire to enhance work zone safety due to the special nature of the project and traffic needs became apparent. | The Cabinet and Contractor reached an agreement to allow for police presence during these phases of construction. Contractor suggested using Police presence in the contract as a bid item when conditions of high speed and road closures are necessary in th
2010-11-18 | Construction | Contracts | NEW ROUTE(O) | 1 | CALLOWAY | Full access to a nearby road was not approved during the design process. After the contract was awarded , a decision was made to allow access to the nearby road. This necessitated modifications to the drainage structure for that area. | Unavoidable.
2010-11-18 | Right-of-Way | Easements | NEW ROUTE(O) | 1 | CALLOWAY | Right of way provided was insufficient for necessary working platforms and construction equipment. | The recommended minimum for temporary construction use was 75 feet (footprint width throughout bridge length). Further recommended was an additional area suitable for use as a working platform when the bridge is over 180 feet total length or similar heig
2010-11-18 | Structures | Reinforcement Steel | NEW ROUTE(O) | 1 | CALLOWAY | Deck steel proposed dimensions were incorrect. | Review of Bill of Reinforcement and plan details will prevent this issue.
2010-11-18 | Design | Omission | NEW ROUTE(O) | 1 | GRAVES | An existing spotlight (property of PNC Bank) was in conflict with the proposed entrance for PNC Bank Lt Sta 189+90. The majority of the surveying for planimetric features was completed in 2007 and the light could have been installed at a later date. | An agreement was made to relocate the light and keep it in working order. A final field check review prior to plan delivery should have discovered this issue.
2010-11-18 | Design | Omission | NEW ROUTE(O) | 1 | CALLOWAY | Right of way monumentation per current policy (Monument Type I with Witness Posts) was not included in contract bid items. | Plan Review process will capture this issue.
2010-11-18 | Drainage | Culvert | NEW ROUTE(O) | 1 | CALLOWAY | A box culvert that had an old pipe was reconstructed with a new pipe. | Constructability Review.
2010-11-18 | Traffic | Markings | NEW ROUTE(O) | 1 | GRAVES | Plans illustrated all traffic markings to be installed as paint. | Due to the unique nature of the project , it was decided to use thermoplastic markings in order to enhance visibility and longevity. It was suggested that even if a corridor does not meet warrants for Thermo , sometimes unique traffic patterns themselv
2010-11-18 | Maintenance of Traffic | Changes | NEW ROUTE(O) | 1 | GRAVES | Due to utility delays and subsequent MOT changes , temporary lane delineation was necessary for safety during initial opening of the DCD. | Temporary type IV pavement markers were installed through the double crossover prior to opening the new configuration.
2010-11-18 | Design | Phasing | NEW ROUTE(O) | 1 | CALLOWAY | A box culvert that was originally included in the Surfacing contract was constructed under the Grade and Drain contract. This occurred because utilities had already been moved due to project phasing. | Constructability Review the whole project ô analyze timing / phasing.
2010-11-18 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 1 | GRAVES | During excavation , unstable soils were encountered in many locations along the project. These areas were outside the existing footprint of US 68 and no indications of soft soils were apparent prior to excavation. Due to the restrictive construction ti | Fabric wrapped Crushed Aggregate No. 2 stone was utilized in these areas to stabilize the subgrade. Soft soil conditions are difficult to predict until actual construction commences; therefore , change orders cannot be avoided in such situations.
2010-09-30 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 9 | ROWAN | During construction , a large vertical fault was encountered running parallel to the roadway , accompanied by a number of small erratic faults in front of the primary one. | Recommendations were made by the District Geotechnical Branch and Central Office Construction Liaison to revise the bench configuration to prevent potential slope failures. This resulted in a significant increase in quantity for Roadway Excavation.
2010-09-30 | Design | Elevations | RECONSTRUCTION(O) | 9 | ROWAN | Incorrect ground elevations were established by the Project Designer. | Project Designer firms hired by the KYTC should be liable for errors.
2010-09-30 | Right-of-Way | Communication | RELOCATION(O) | 9 | ELLIOTT | Additional quantities were needed to extend the newly constructed retaining wall for a home owner. | Better communication between the Right-of-Way agent and property owner.
2010-09-30 | Construction | Contracts | RELOCATION(O) | 9 | ELLIOTT | An additional 150 feet of sidewalk was added to provide tie-in to the town. | A policy is needed to allow construction beyond project limits.
2010-09-30 | Drainage | Ponding | RELOCATION(O) | 9 | ELLIOTT | Water was not sufficiently confined at the intersection to prevent it flowing into the travel lane. | A slotted drain pipe was added on the approach road to divert the water into the adjacent ditch and culvert.
2010-09-30 | Design | Entrance | RELOCATION(O) | 9 | ELLIOTT | The plans did not provide suitable access to the front entrance of a business. | Extend entrance to connect the planned entrance to the paved area in front of the business.
2010-09-30 | Utilities | Omission | RECONSTRUCTION(O) | 9 | ROWAN | A 16 inch water valve was not included as a bid quantity on the utility plans. | Better review of utility plans.
2010-09-30 | Utilities | Omission | RELOCATION(O) | 9 | ELLIOTT | Additional items were needed to comply with regulations involving the disturbance of waterlines located within 200' of a gas station. This was an oversight in utility design. | Utility designers need a better understanding of the Division of Water requirements.
2010-09-30 | Geotechnical | Safety | RECONSTRUCTION(O) | 9 | ROWAN | Construction encountered a cut that had a large fracture or fault line , which became unstable. Temporary concrete barrier wall was needed to minimize the amount of material that would block the roadway during blasting activities. | Including a bid item for temporary concrete barrier walls in blasting zones should become standard practice.
2010-09-30 | Utilities | Relocation | RECONSTRUCTION(O) | 9 | ROWAN | Utilities were incorrectly relocated. To avoid re-relocating the utility lines , steep grades were constructed. This contributed to slope failure. | Re-relocate utility lines and flatten slopes; or construct retaining walls.
2010-09-30 | Utilities | Omission | RECONSTRUCTION(O) | 9 | ROWAN | A city ordinance change required manhole seals on all sewer projects; however , this information was not shared with the KYTC. | The city should have been required to pay for the additional expense.
2010-09-30 | Utilities | Omission | RELOCATION(O) | 9 | ELLIOTT | There was a design omission by Utility Contractor. This is a recurring problem - KYTC pays for poor quality utility design. The Utility ContractorÖs original design for the relocation of waterlines resulted in an insufficient turnover of water in a water | KYTC needs expertise to review utility design plans; utility contractor should offer a warranty or guarantee for their design; make utility design part of roadway design.
2010-09-30 | Geotechnical | Slides | RELOCATION(O) | 9 | ELLIOTT | An embankment slide occurred during construction. | A possible solution would be to drill more core samples prior to letting.
2010-09-30 | Drainage | Omission | RELOCATION(O) | 9 | ELLIOTT | Two Sloped Box Inlet-Outlets were switched to sloped and flared box Inlet-Outlet to meet safety standards. This was an oversight during the design phase of the project. | A more thorough review of the drainage plans may have prevented this error.
2010-09-30 | Structures | Erosion Control | RECONSTRUCTION(O) | 9 | ROWAN | During an onsite inspection of the project , Division of Water representatives recommended using Cyclopean Stone Rip Rap to stabilize creek banks and prevent erosion. | Bridge designers should take into account erosion or scour along stream banks under bridges.
2010-09-30 | Design | Quantities | RELOCATION(O) | 9 | ELLIOTT | The original bid item quantities for undercut stabilization were inadequate. ***Note: this issue has occurred on numerous projects.*** | Increase bid item quantities (full width and depth).
2010-09-30 | Pavement | Design | RELOCATION(O) | 9 | ELLIOTT | After the disturbed pavement was patched , settlement occurred. This resulted in a rough roadway that would likely cause water to pond and freeze during the winter months. | Add Leveling & Wedging as a bid item for any significant grading project.
2010-09-30 | Pavement | Quantities | RECONSTRUCTION(O) | 9 | ROWAN | Bid item quantities for paving areas were incorrect. | Better review of quantities for bid items.
2010-09-30 | Design | Omission | RECONSTRUCTION(O) | 9 | ROWAN | A second variable message board was needed to improve safety by providing advance warning for both Northbound and Southbound traffic during construction. There was no bid item quantity for the second variable message board. | Plans that have a bid item for ÿVariable Message BoardÖ need to include quantities for both directions of traffic.
2010-09-30 | Maintenance of Traffic | Plan | RELOCATION(O) | 9 | ELLIOTT | The Contractor proposed a revised Maintenance of Traffic plan that would keep 2 lanes of traffic open during construction. | The Maintenance of Traffic plan suggested by the Contractor was approved and implemented.
2010-09-30 | Construction | Inspection | RECONSTRUCTION(O) | 9 | ROWAN | Deterioration occurred during a ten year delay in construction for an old bridge that was in need of repair. Due to a failure in the deck , emergency bridge repair was required. | Evaluate bridge prior to letting. Clarification is needed as to who is responsible for maintenance after letting.
2010-09-30 | Right-of-Way | Communication | RELOCATION(O) | 9 | ELLIOTT | Right-of-Way agent did not let designer know about trees to be cut. | Communicate all promises.
2010-09-30 | Construction | Contracts | RECONSTRUCTION(O) | 9 | ROWAN | This change order establishes liquidated damages as a bid item. | All plans should include a bid item for liquidated damages.
2010-04-26 | Environmental | Underground Tank | MAJOR WIDENING(O) | 2 | CHRISTIAN | A Statewide Letter Agreement was required for the removal of an unknown underground storage tank that was found on the project. | More communication between survey crews and residents; Increase communication with Right-of-Way staff; Future reference: Need to track person-hours , equipment usage , and other expenses associated with Statewide Letter Agreements.
2010-04-26 | Maintenance of Traffic | Phasing | MAJOR WIDENING(O) | 2 | CHRISTIAN | Not enough space for 2 lanes of traffic. The original MOT Plan provided 22Ö of pavement throughout construction; adjustments to the MOT Plan were made to better fit the ContractorÖs construction phasing. | MOT Plan should be reviewed by someone with constructability expertise; Increase communication between Developer of MOT Plan and Contractor; Developer of MOT Plan should meet with the Contractor to describe development of the MOT Plan.
2010-04-26 | Utilities | Relocation | MAJOR WIDENING(O) | 2 | CHRISTIAN | Location of many utility as-built plans were incorrect. Project involved the coordination of multiple utility companies. | Spot check utility locations to verify accuracy of plans prior to letting; Use Subsurface Utility Exploration (SUE) more often , especially in urban areas.
2010-04-26 | Design | Omission | MAJOR WIDENING(O) | 2 | CHRISTIAN | No line item set up for foundation preparation of the gravity wall. | More thorough review of line items.
2010-04-26 | Construction | Ride Quality | MAJOR WIDENING(O) | 2 | CHRISTIAN | Quantity for this line item usually needs to be increased. | Increase quantity for Ride Quality prior to letting.
2010-04-26 | Utilities | Stacked Utilities | MAJOR WIDENING(O) | 2 | CHRISTIAN | Urban location of project required larger disturbed area. Sometimes utilities not only are separated by horizontal distances , but vertical distances as well; hence the stacking of utilities to fit in urban areas. | Periodic Meetings with Utility Companies; Increase amount of Temporary or Permanent Easements for Utilities in urban areas; Increase District Utilities Staff or Generate Statewide Contract to alleviate overload of work.
2010-04-26 | Design | Drainage | MAJOR WIDENING(O) | 2 | CHRISTIAN | Drainage pipe outlet lower than ditch elevation. | Check surveyed elevations.
2010-04-26 | Design | Drainage | MAJOR WIDENING(O) | 2 | CHRISTIAN | Numerous culvert extensions were required. | Cutting wing walls and placing dowels into the existing concrete should be incorporated as standard practice for the extension of reinforced concrete box culverts on design plans.
2010-03-31 | Design | Access | RELOCATION(O) | 10 | BREATHITT | An approach road was moved further down from planned access. This was to help traffic control. Suggest contacting the designer/consultant regarding all VECPs to discuss before acceptance and implementation. | KRS and Design Manual states criteria for rural and urban access distances for safety. Although , in some case with engineering studies to justify the request , can be submitted to the State Highway Engineers Office for a variance of the spacing. By KRS
2010-03-31 | Design | Access | RELOCATION(O) | 10 | BREATHITT | An approach road was moved further down from planned access. This was to help traffic control. Suggest contacting the designer/consultant regarding all VECPs to discuss before acceptance and implementation. | KRS and Design Manual states criteria for rural and urban access distances for safety. Although , in some case with engineering studies to justify the request , can be submitted to the State Highway Engineers Office for a variance of the spacing. By KRS
2010-03-31 | Drainage | Pipes | RELOCATION(O) | 10 | BREATHITT | Pipes called out in the plans were corrugated storm sewer pipe , but in the best interest of the project treated bituminous pipe was exchanged in the median due to the water acidity in coal producing area. | In this region designers be aware of the ground acidity levels when choosing building materials such as the type of pipe selection for storm sewers that would have cross drain pipes that include off pavement drainage.
2010-03-31 | Drainage | Pipes | RELOCATION(O) | 10 | BREATHITT | Pipes called out in the plans were corrugated storm sewer pipe , but in the best interest of the project treated bituminous pipe was exchanged in the median due to the water acidity in coal producing area. | In this region designers be aware of the ground acidity levels when choosing building materials such as the type of pipe selection for storm sewers that would have cross drain pipes that include off pavement drainage.
2010-03-31 | Design | Quantities | RELOCATION(O) | 10 | BREATHITT | Project had a large back slope cuts in a curve and the radius with stationing was not correct to give accurate quantities. The normal calculation based on the baseline station cross sections failed to accurately quantify the amount of rock excavation. | Designers consider the larger radius in calculating materials for accuracy. Pay particular attention to earthwork calculations in curved , sidehill conditions. Create a standard procedure for calculation.
2010-03-31 | Design | Quantities | RELOCATION(O) | 10 | BREATHITT | Project had a large back slope cuts in a curve and the radius with stationing was not correct to give accurate quantities. The normal calculation based on the baseline station cross sections failed to accurately quantify the amount of rock excavation. | Designers consider the larger radius in calculating materials for accuracy. Pay particular attention to earthwork calculations in curved , sidehill conditions. Create a standard procedure for calculation.
2010-03-31 | Drainage | Culvert | RELOCATION(O) | 10 | BREATHITT | A culvert extension was requested as opposed to the planned culvert replacement. A pre-construction meeting concluded that the culvert replacement would affect the MOT with a diversion to be constructed. | Designers should give increased attention to the condition of existing culverts and extend rather than replace when they are structurally and hydraulically adequate.
2010-03-31 | Drainage | Culvert | RELOCATION(O) | 10 | BREATHITT | A culvert extension was requested as opposed to the planned culvert replacement. A pre-construction meeting concluded that the culvert replacement would affect the MOT with a diversion to be constructed. | Designers should give increased attention to the condition of existing culverts and extend rather than replace when they are structurally and hydraulically adequate.
2010-03-30 | Drainage | Existing Pipe | BRIDGE REPLACEMENT(P) | 10 | MAGOFFIN | Existing 24 pipe that was to be used during construction phase for drainage. It was not functioning properly due to silt build up. A new ditch had to be built with fabric and channel lining. | A field site visit by designers to inspect usable existing drainage when creating design plans. Follow up by processing any permits need to create any new ditching necessary in the plans.
2010-03-30 | Design | Plan Processing | RECONSTRUCTION(O) | 10 | MORGAN | Substantial construction delays caused by insufficient permitting and archeological study taking place. Project was let while archeological dig was in process. | Current plan processing of having all plans , permitting , studies , etc. submitted/completed/approved properly alleviates this issue.
2010-03-30 | Design | Specifications | BRIDGE REPLACEMENT(P) | 10 | MAGOFFIN | No specifications detailing river crossings during construction on projects. | This item has been currently updated as specifications have been implemented to give guidance to contractors. In addition , contractors are held responsible when they create their bid for river crossings.
2010-03-30 | Utilities | Communication | RECONSTRUCTION(O) | 10 | MORGAN | Waterline relocation to an existing line from a local water plant replaced in kind a larger pipe to match existing pipe size. | Better communication up front to ensure quality and fairness of charges and payments. A reimbursement type procedure in needed for cases like this for Betterment.
2010-03-30 | Design | Omission | RECONSTRUCTION(O) | 10 | MORGAN | No bid items were set up for structures (3-span bridge , 4'x3' culvert and 10'x5' culvert). | Review plans for this type of omission.
2010-03-30 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 10 | MORGAN | Project had a large back slope cuts. These slopes were steep and the soil material caused land slides to occur. Erosion control blankets were used to remedy the situation. | If large cuts are made with steep slopes having unsuitable soils exposed , make sure plans have quantities set up for erosion control. It is noted that Erosion Control Blankets are underutilized and could be automatically regionally used in design plans
2010-03-30 | Maintenance of Traffic | Slides | RECONSTRUCTION(O) | 10 | MORGAN | The original route was being used for maintenance of traffic but landslides occurred blocking traffic. Due to the rugged terrain , blasting on the project site and a river on one side of the roadway , a detour was created using KY 1161 and KY 172 which | Designers anticipate this type of occurrence and have an alternative MOT plan when landslides may exists due to terrain and construction blasting.
2010-03-05 | Design | Communication | RELOCATION(O) | 12 | PIKE | DGA was called out for approach entrances for access. A change order was issued to use asphalt. | Discuss at Project Team meetings where to gain accesses.
2010-03-05 | Design | Waste Areas | RELOCATION(O) | 12 | PIKE | Controlled and Maintenance Fill Embankment with 3' lifts are being utilized in this region of KY for economic growth and development. | Several suggestions were discussed: 1. Designers communicate throughout the whole process , i.e. , geotechnical reports , ROW plans , design plans through construction , 2. Create a Special Note in proposal , 3. Define with details on plans , and 4
2010-03-05 | Structures | Hold-in-Place Steel | RELOCATION(O) | 12 | PIKE | Extra steel was used to help keep structural steel in place for the pier caps. It is not explicit in structure plans how steel is placed and controversy occurs to what contractors can use to hold the steel in place when erecting the cages and pouring con | In structure designs show guidance in how to hold-in-place steel during construction. Additionally , give guidance on what acceptable materials can be used to hold structural steel in place.
2010-03-05 | Geotechnical | Settlement | RELOCATION(O) | 12 | PIKE | Settlement occurred at both ends of NB and SB approaches of the bridges causing maintenance issues. No approach slabs were in the plans but were added to the project as a change order , but settlement still occurred. | Several suggestions were discussed: 1. When using semi-integral end bents use approach slabs , 2. Further analysis of settlement to large fill areas where structures are involved , and 3. Create a check list for similar areas and call out approach sl
2010-03-05 | Design | Omission | RELOCATION(O) | 12 | PIKE | Settlement platforms were needed on the project and was written in the geotechnical report but not in the Plans. | Review plans for constructability.
2010-03-05 | Utilities | Existing Utilities | RELOCATION(O) | 12 | PIKE | Gas well was discovered in the project area when coal was removed. A landslide occurred but to date not clear how to fix the landslide due to owner negotiations. | Propose to buy more Right-of-Way in the region's area to have access when issues like this occur.
2010-03-05 | Traffic | Lighting | RELOCATION(O) | 12 | PIKE | Highmast lighting was set up for this project , but one mast was placed on a bench on the traffic plans. This was moved to another nearby site for suitable access. | Review plans for constructability and accessibility. Submit lighting plans in a timely fashion for review.
2010-03-05 | Structures | Communication | RELOCATION(O) | 12 | PIKE | Class A concrete was called out on substructures that were above cap line. Traditionally , Class AA is used for above cap line concrete , therefore it was changed to use Class AA concrete. | Cost savings can be made if Class A is used for above cap line wings. Refer to KYTC Structural Design guidance. If Class A can be used , place note , Contrary to specification... for further information.
2010-03-05 | Pavement | Design | RELOCATION(O) | 12 | PIKE | Thickness of shoulders were less than desirable for a coal route. The shoulder thickness were increased to accommodate coal trucks. | When coal trucks are travelling on these routes use full depth pavement design.
2010-03-05 | Geotechnical | Top of Rock | RELOCATION(O) | 12 | PIKE | Double Barrel culvert had loose rock when excavated to the suggested elevation. Had to use mass concrete to remedy the situation. | A thorough investigation for geotechnical data for areas where structures are involved. More borings are suggested when structure layout is established.
2010-03-05 | Geotechnical | Top of Rock | RELOCATION(O) | 12 | PIKE | Structure at Pier 1 (SB) had loose rock when excavated to the suggested elevation. Had to use mass concrete to remedy the situation. | A thorough investigation for geotechnical data for areas where structures are involved. More borings are suggested possibly when substructure is designed and footer dimensions are known.
2010-03-05 | Structures | Stop Blocks | RELOCATION(O) | 12 | PIKE | Structure plans showed stop blocks at piers due to high grade (6%). | Positive feedback with use of stop blocks in the substructure's design. Conditions of high slopes and a sloped cap on pier must exist for the stop blocks to be effective.
2010-03-04 | Geotechnical | Investigation | NEW ROUTE(O) | 12 | FLOYD | Layer of shale was found under layer of rock causing rock fall when exposed. | More borings are suggested using step-borings down the mountainside. The geotechnical report should be able to show details.
2010-03-04 | Drainage | Retention Basin | NEW ROUTE(O) | 12 | FLOYD | Retention basins were used throughout the project but caused maintenance issues to the roadway as the road settled. It was observed that water is seeping through the fill areas causing this settlement. | Several suggestions were discussed: 1. Designers look at global picture to understand the drainage effects to the surrounding areas , 2. Develop footprint with Right-of-Way limits , 3. Look at other alignment alternatives , and 4. Include drainage in d
2010-03-04 | Structures | Omission | BRIDGE REPLACEMENT(P) | 12 | FLOYD | The bridge was on the crest of a vertical curve and approximately 8 of haunch was not accounted for in the Class AA concrete bid item. | Designers check quantities when this situation occurs on a structure especially when the slopes are large and center of bridge is in the crest.
2010-03-04 | Utilities | Plans | NEW ROUTE(O) | 12 | FLOYD | Utility Plans were not completed prior to the project being let causing delays during relocation of utilities. | Currently it is being requested by KYTC - Central Office that all plans (i.e. , roadway , structure , MOT , ECP , right-of-way , utilities , etc.) are submitted by the Project Manager merged together for plan processing.
2010-03-04 | Drainage | Ditches | NEW ROUTE(O) | 12 | FLOYD | Project had several steep side-slope ditches that called for Channel II lining. It was observed from heavy rains that the Channel II rock washed away and maintenance issues arise. | Several suggestions were discussed: 1) Increase rock size to Channel III or IV , 2) Use Gabion baskets or mattresses , 3) Create a design standard , and 4) Develop a hydraulic range with pipe size that corresponds to what type of Channel lining to use
2010-03-04 | Design | Diversion | BRIDGE REPLACEMENT(P) | 12 | FLOYD | Contractor requested to move the temporary diversion on the upstream side of the project because their structure would layout better squared rather than skewed , but KYTC did not allow this due to the owner's yard. | General consensus was to have designers be aware that most contractors would like to have diversions squared rather than skewed if possible.
2010-03-04 | Drainage | Ditches | NEW ROUTE(O) | 12 | FLOYD | Project showed v-ditch used parallel to roadway , then called for filling the ditches with Channel II lining causing shoulders of roadway to be steep and v-ditch shape changed to a flat bottom. | When using v-ditches , make sure the contractor maintains the V shape. Otherwise , if required by hydraulics to use a 2-foot flat bottom ditch , then design should show this on the plans and maintain the typical section configuration for the ditch for
2010-03-04 | Geotechnical | Soils | NEW ROUTE(O) | 12 | FLOYD | Project had been undercut near lake area finding Blue Mud clays which were unsuitable materials for sub-grade. Use of geotextile fabric and suitable fill were used. | A thorough investigation for geotechnical data in certain areas that have suspect soils. More borings are suggested. A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for specific projects.
2010-02-25 | Design | Communication | RELOCATION(O) | 6 | KENTON | Project limits stopped and an existing city road (Lily Drive) was left with no connection. The change order requested by the local officials was to resurface and extend the city road for beautification and was paid by the locals. | Designers look at the whole project and meet with the locals to address issues of connection early on in the design process.
2010-02-25 | Design | Omission | BRIDGE REPLACEMENT(P) | 6 | GRANT | At the end of the bridge , the 25' guardrail transition was omitted in the plans. It was noted that on other projects the 25 LF of curb on each corner of a bridge is required to keep the guardrail bridge attachments legal. | Designers review plans and quantities. Could include this item on Plan Processing Check List.
2010-02-25 | Erosion Control Plan | Communication | BRIDGE REPLACEMENT(P) | 6 | GRANT | The above issue of topdressing fertilizer caused a communication gap between the Prime Contractor/Sub-contractor and KYTC personnel. Issues of charges and payment came about with all parties. | Better communication with all three entities to ensure quality and fairness of charges and payments.
2010-02-25 | Geotechnical | Soils | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Sub-grade soils were very inconsistent throughout the project. Project area has very little clay and more silt materials. | Suggest cement stabilization to be set up for certain areas around the state with known unstable soils. Make notes in Geotechnical reports.
2010-02-25 | Traffic | Omission | RELOCATION(O) | 6 | KENTON | School signals were not on the original plans. As KYTC personnel was going through attrition , the Traffic Plans came later. | Coordination and timing of having roadway plans and traffic plans reviewed during final inspection and communicate if plans are lagging.
2010-02-25 | Design | Communication | RELOCATION(O) | 6 | KENTON | Project limits stopped and an existing city road (Lily Drive) was left with no connection. The change order requested by the local officials was to resurface and extend the city road for beautification and was paid by the locals. | Designers look at the whole project and meet with the locals to address issues of connection early on in the design process.
2010-02-25 | Structures | Flowable Fill | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Flowable fill was used to backfill at the bridge ends instead of structure granular backfill that was shown on the plans. Maintenance issues causing short and long term settlement have been ongoing with the use of structure granular backfill along with t | Designers need to investigate future use of using granular backfill vs. flowable fill or a mixture of both materials to alleviate settlements at the ends of the bridges.
2010-02-25 | Traffic | Omission | RELOCATION(O) | 6 | KENTON | School signals were not on the original plans. As KYTC personnel was going through attrition , the Traffic Plans came later. | Coordination and timing of having roadway plans and traffic plans reviewed during final inspection and communicate if plans are lagging.
2010-02-25 | Design | Omission | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Temporary Barrier Wall was shown on structure plans but not on roadway plans. | Review plans.
2010-02-25 | Structures | Handrail | RELOCATION(O) | 6 | KENTON | Handrail was shown on plans to be placed on top of the retaining wall that abutted to a sidewalk. It was unclear the practical use of the handrail and KYTC district personnel decided to put fencing for safety purposes since there was a 16' drop to the ba | Designers look at the overall picture that may include safety issues especially when sidewalks are near structures.
2010-02-25 | Structures | Handrail | RELOCATION(O) | 6 | KENTON | Handrail was shown on plans to be placed on top of the retaining wall that abutted to a sidewalk. It was unclear the practical use of the handrail and KYTC district personnel decided to put fencing for safety purposes since there was a 16' drop to the ba | Designers look at the overall picture that may include safety issues especially when sidewalks are near structures.
2010-02-25 | Erosion Control Plan | Slope Protection | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Due to saturated slopes slipping near the Ohio River , it was recommended by Geotech and Central Office that fabric and cyclopean stone rip-rap (Channel lining CLIII) be used to stabilize slopes. | Review ECP to make sure quantities reflect the plans.
2010-02-25 | Design | Radius | RELOCATION(O) | 6 | KENTON | Roadway plans showed standard radius for intersections but heavy truck traffic causes trucks to encroaches on curb and sidewalks when making a turning movement. Saw cut curb/sidewalks to alleviate encroached areas. | Designers review truck traffic and be conscience of industrial use when designing turns and use increased radius for industrial needs in designs. In addition , develop a standard to address the issue of radii associated with truck traffic and grade brea
2010-02-25 | Design | Radius | RELOCATION(O) | 6 | KENTON | Roadway plans showed standard radius for intersections but heavy truck traffic causes trucks to encroaches on curb and sidewalks when making a turning movement. Saw cut curb/sidewalks to alleviate encroached areas. | Designers review truck traffic and be conscience of industrial use when designing turns and use increased radius for industrial needs in designs. In addition , develop a standard to address the issue of radii associated with truck traffic and grade brea
2010-02-25 | Erosion Control Plan | Omission | BRIDGE REPLACEMENT(P) | 6 | GRANT | Topdressing fertilizer was necessary to fertilize the project seeding. This was not addressed as a Lump Sum Item and required a change order. | Review ECP to make sure quantities reflect the plans.
2010-02-25 | Geotechnical | Soils | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Geotextile fabric was need to stabilize soils on site. Soils were saturated due to seasonal weather making construction delays. | Have options for when considering projects start date , i.e. , summer season (drier) as opposed to early spring with wetter weather persisting. Consider contracts with working days instead of fixed contract times. Have Geotextile Fabric quantities buil
2010-02-25 | Maintenance of Traffic | Quantities | RELOCATION(O) | 6 | KENTON | DGA was shown on plans but not enough quantities were set up to cover all entrances. The change order called for Traffic Bound Base. | Review quantities on MOT reflect the plans when entrances have to be built. Create bid items; one for DGA and one for Traffic Bound Base.
2010-02-25 | Maintenance of Traffic | Quantities | RELOCATION(O) | 6 | KENTON | DGA was shown on plans but not enough quantities were set up to cover all entrances. The change order called for Traffic Bound Base. | Review quantities on MOT reflect the plans when entrances have to be built. Create bid items; one for DGA and one for Traffic Bound Base.
2010-02-25 | Utilities | Existing Utilities | SPOT IMPROVEMENTS(O) | 6 | CARROLL | Existing waterline and gas line were not located where the plans had them. | Communication with Utility Companies , KYTC and Consultants to work together for complete Utility Plans. Early information on locating existing utilities for projects.
2010-02-25 | Geotechnical | Soils | BRIDGE REPLACEMENT(P) | 6 | GRANT | Sub-grade soils were very inconsistent throughout the project. Project area has very little clay and more silt materials. This affected the MOT for this rural roadway. | Suggest cement stabilization to be set up for certain areas around the state with known unstable soils. Make notes in Geotechnical reports. Alternatively , give options written in the contract for road-base.
2010-02-25 | Geotechnical | Soils | RELOCATION(O) | 6 | KENTON | Project alignment went through several cut slopes. These slopes were on a 2:1 , but the soil material was unsuitable and caused land slides to occur in certain areas. Geotextile fabric , granular embankment with perforated pipe were used to remedy the | If large cuts are made with steep slopes having known unsuitable soils exposed in certain areas of the state have quantities set on plans and include in roadway typical sections. Other design suggestion could be used with a cut using 1:1 slope then back
2010-02-25 | Geotechnical | Soils | RELOCATION(O) | 6 | KENTON | Project alignment went through several cut slopes. These slopes were on a 2:1 , but the soil material was unsuitable and caused land slides to occur in certain areas. Geotextile fabric , granular embankment with perforated pipe were used to remedy the | If large cuts are made with steep slopes having known unsuitable soils exposed in certain areas of the state have quantities set on plans and include in roadway typical sections. Other design suggestion could be used with a cut using 1:1 slope then back
2010-02-23 | Erosion Control Plan | Communication | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Erosion of the stream bank adjacent to the roadway. Maintenance of the bank was made a year later to control the bank erosion. | Discussions of the overall project , the global effects and concerns need to be made during design phase.
2010-02-23 | Design | Excavation | NEW ROUTE(O) | 6 | KENTON | Cross-sections and Earthwork Totals were incorrect on the plans. Project was set up as an Embankment in Place , but due to errors in quantities excess excavation was produced and waste areas were provided by KYTC on the project site (2 in ROW , 1 at Eat | Review cross-sections in final inspection and use technology with modeling for project balancing.
2010-02-23 | Design | Striping | NEW ROUTE(O) | 6 | KENTON | The permanent striping details on the plans were not in accordance to MUTCD standards and Pave Marking - Pref Thermo Yield was needed to complete this in accordance to MUTCD standards for Round-Abouts. | Review KYTC standards for striping Round-Abouts according to MUTCD. Make sure quantities for striping are spelled out in Bid Items and include signing.
2010-02-23 | Design | Striping | NEW ROUTE(O) | 6 | KENTON | The permanent striping details on the plans were not in accordance to MUTCD standards and Pave Marking - Pref Thermo Yield was needed to complete this in accordance to MUTCD standards for Round-Abouts. | Review KYTC standards for striping Round-Abouts according to MUTCD. Make sure quantities for striping are spelled out in Bid Items and include signing.
2010-02-23 | Structures | Seeping | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Gap between the abutments and diaphragms causing water and silty materials to seep through. One-Step Membrane was used to counter the issue. | Division of Construction is currently requiring the One-Step Membrane to address the issue. Confer with the Division of Structural Design to include this item as a Bid Item or Incidental.
2010-02-23 | Structures | Guardrail | NEW ROUTE(O) | 6 | KENTON | The end treatments for the guardrail between the bridges were set up as Type 2A. These are not crash worthy end treatments in this instance. They were changed to Type 7. | Designers review the connection for guardrail to barrier end treatments when sidewalks are on structures and for crash worthiness.
2010-02-23 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | At the time the plans had Structure Excavation of Common and there was an overrun. Currently , Foundation Site Preparation is being used as a Lump Sum. | Consistency for projects that are being Let to check the current procedures on how items are to be paid out.
2010-02-23 | Structures | Fencing | NEW ROUTE(O) | 6 | KENTON | Fencing was added to Abutment Walls for safety purposes since there was a 30 foot drop from the top of wall creating a hazard to pedestrians. | Designers look at the overall picture that may include safety issues especially when sidewalks are on structures.
2010-02-23 | Construction | Specifications | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | No Containment measures were described for painting on the project. The contractors and KYTC personnel came up with their own Painting Containment of New Structures Plan. | Review Specifications to include guidance of Painting Containment for New Structures. Currently there are specifications for containment of existing structures but none for new structures.
2010-02-23 | Design | Lighting | NEW ROUTE(O) | 6 | KENTON | Lighting details and plans were the responsibility of Fidelity. This was agreed upon early in the design process. | Suggest notice in Contract for contractors to know that agreements were made ahead of time.
2010-02-23 | Design | Omission | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Omitted entrance pipe for driveway where a ditch was called out on the plans. | Review plans thoroughly to calculate quantities for project.
2010-02-23 | Structures | Guardrail | NEW ROUTE(O) | 6 | KENTON | Guardrail End Treatment Type A was shown in the plans , but the guardrail did not work since the bridge had sidewalks. The district personnel changed the type to Guardrail End Treatment Type D. This was to accommodate the sidewalks on the bridge. | Designers review the connection for guardrail to barrier end treatments when sidewalks are on structures.
2010-02-23 | Structures | Communication | NEW ROUTE(O) | 6 | KENTON | The sidewalk's cross-slope on the bridge was changed to the opposite direction. It was planned as the water to drain away from the road , but it was changed to drain onto the road. This was to match the cross-slope of the roadway's sidewalk. | Communication with structural and roadway designers to make consistencies where structure and roadway tie in together.
2010-02-23 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Signage and Barricade - Type II were insufficient quantities to properly maintain and control traffic. | Review MOT in constructability reviews or at final inspection. Make sure Bid Items are set up with good estimated quantities.
2010-02-23 | Structures | Painting | BRIDGE REPLACEMENT(P) | 6 | BRACKEN | Weathering steel was used for the steel on the replacement of the pony truss. It was called out on the plans to paint the steel on this project. | Consistency and guidance for materials used. Investigate why paint weathering steel if the intended use for that material is not to paint and let the steel naturally form it's barrier to guard against the weather.
2010-02-23 | Erosion Control Plan | Omission | NEW ROUTE(O) | 6 | KENTON | Topdressing fertilizer was necessary to fertilize the project seeding. This was mentioned in the erosion control inspection report for the entire project but not addressed as a Lump Sum Item and required a change order. | Review ECP to make sure quantities reflect the plans.
2010-02-12 | Geotechnical | Investigation | ROCKFALL MITIGTN(P) | 11 | CLAY | Project had a budgeted amount of funds and no geotechnical investigation was performed as part of minimizing costs. | A thorough investigation for geotechnical data. A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for projects.
2010-02-12 | Geotechnical | Cut-Slope | MAJOR WIDENING(O) | 11 | LAUREL | Encountered no rock on a cut-slope which is common when the drill core is an open-face log. | A thorough investigation for geotechnical data. A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for projects possibly through underground radar detection devises.
2010-02-12 | Geotechnical | Cut-Slope | MAJOR WIDENING(O) | 11 | LAUREL | Encountered no rock on a cut-slope which is common when the drill core is an open-face log. | A thorough investigation for geotechnical data. A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for projects possibly through underground radar detection devises.
2010-02-12 | Design | Alignments | MAJOR WIDENING(O) | 11 | LAUREL | Northbound and southbound alignments had separate vertical alignments. This was based on cost for splitting differences and leveling. | Objective is to balance quantities including pavement.
2010-02-12 | Construction | ROW | ROCKFALL MITIGTN(P) | 11 | CLAY | Project had a budgeted amount of funds and no Right-of-Way easements were reviewed as part of minimizing costs. | Review project area if more Right-of-Way is needed to construct the project.
2010-02-12 | Geotechnical | Elevations | MAJOR WIDENING(O) | 11 | LAUREL | Plans gave wrong elevation for top of rock. Occurred at least once on each cut. | A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for projects possibly through underground radar detection devises.
2010-02-12 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | Omitted steel quantities for culvert extension in the summary. | Review structure plans thoroughly to calculate quantities of steel for project.
2010-02-12 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | Omitted steel quantities for culvert extension in the summary. | Review structure plans thoroughly to calculate quantities of steel for project.
2010-02-12 | Pavement | Seeping | MAJOR WIDENING(O) | 11 | LAUREL | Northbound and southbound of the interstate , 1/2 way down the hill from the bridge has water seeping through the pavement. Suspected existing sub-surface pavement on a steeper slope is carrying water then stopped at the tie-in and has nowhere to go bu | Transverse drains may need to be place to correct this issue. Other suggestion was to lay an impervious surface. Possible research project for KY Transportation Center (KTC).
2010-02-12 | Pavement | Seeping | MAJOR WIDENING(O) | 11 | LAUREL | Northbound and southbound of the interstate , 1/2 way down the hill from the bridge has water seeping through the pavement. Suspected existing sub-surface pavement on a steeper slope is carrying water then stopped at the tie-in and has nowhere to go bu | Transverse drains may need to be place to correct this issue. Other suggestion was to lay an impervious surface. Possible research project for KY Transportation Center (KTC).
2010-02-12 | Design | Alignments | MAJOR WIDENING(O) | 11 | LAUREL | Northbound and southbound alignments had separate vertical alignments. This was based on cost for splitting differences and leveling. | Objective is to balance quantities including pavement.
2010-02-12 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 11 | LAUREL | During the design phase , time constraints and designer's parameters of keeping 2 lanes open to traffic were confined to the MOT plans. An adjacent rehab project was let after this project which could not maintain 2 lanes of traffic in each direction. | Invite construction personnel to final inspection meetings to review MOT. If future adjacent projects are known , consider MOT with the current project.
2010-02-12 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 11 | LAUREL | During the design phase , time constraints and designer's parameters of keeping 2 lanes open to traffic were confined to the MOT plans. An adjacent rehab project was let after this project which could not maintain 2 lanes of traffic in each direction. | Invite construction personnel to final inspection meetings to review MOT. If future adjacent projects are known , consider MOT with the current project.
2010-02-12 | Geotechnical | Elevations | MAJOR WIDENING(O) | 11 | LAUREL | Plans gave wrong elevation for top of rock. Occurred at least once on each cut. | A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for projects possibly through underground radar detection devises.
2010-02-09 | Geotechnical | Communication | I-CHANGE RECONST(O) | 9 | BOYD | Same issue as above. No perforated pipe set up for embankment benching because it was not called for in the geotechnical notes. | Subsequent geotechnical notes call for the use of perforated pipe on the uppermost bench. Work on consistency in the geotechnical notes.
2010-02-09 | Maintenance of Traffic | Signage | I-CHANGE RECONST(O) | 9 | BOYD | Installed signs twice during this project and paid for them twice. | Review MOT and permanent signing plans to see if conflicting relocations are made.
2010-02-09 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 9 | BOYD | Striping was called out in the MOT , but the removal of temporary striping was not included as a bid item. | A constructability review must be performed to catch details that could be omitted. Create MOTs in a fashion that is similar to the current Erosion Control Plans (ECP).
2010-02-09 | Design | Communication | I-CHANGE RECONST(O) | 9 | BOYD | Rock roadbed typical section was not prepared as outlined in the Standard Specifications. This was done deliberately and coordinated with the Central Office , but it was not conveyed and therefore caused confusion and was labeled as plan error. | If changes to a specification by designer is warranted , detail in the General Notes as , Contrary to Specifications Also , during final inspection , designer should make light of the changes so everyone knows this upfront.
2010-02-09 | Design | CAP | SAFETY(P) | 9 | FLEMING | Owners were not contacted by designers for easements on their property in the project area. | Communicating All Promises (CAP) are the responsibility of the Project Manager. The CAP is included in the Proposal , but an alternate method of making this document available is to post on ProjectWise.
2010-02-09 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 9 | BOYD | For interstate median crossovers end treatments were not considered and the replacement of all trailing ends was not included in the plans. | Create a checklist for items to look for or consider during designing crossovers in MOT. Should check during a constructability review.
2010-02-09 | Design | Omission | I-CHANGE RECONST(O) | 9 | BOYD | No perforated pipe set up for embankment benching that was outlined in the plans as engineers discretion. | An estimated maximum amount of quantities should be set in the bid and used by engineer's discretion.
2010-02-09 | Construction | Specifications | SAFETY(P) | 9 | FLEMING | Encasement of pipe was set up for the project but , Boring and Jacking was called out and no bid item was set for this procedure. There is no guidance that shows how to pay for this. | Specify in a separate bid item. Propose as part of the description in Specifications.
2010-02-09 | Structures | Omission | I-CHANGE RECONST(O) | 9 | BOYD | Omitted steel quantities for superstructure mats. Additional quantity of steel was added to the plans as a result of an error in the spreadsheet used to calculate this quantity. | Review barbills thoroughly to calculate quantities of steel for project.
2010-02-09 | Utilities | Relocation | SAFETY(P) | 9 | FLEMING | It was stated that 75% of the change orders were from utility relocation issues. More than often underground utilities are not well documented and causes delays and additional costs to projects. | Review the whole process on how utility plans are created to ensure better quality. Encourage local officials through possible incentives to allow Roadway Designers to correspond/consult with Utility Designers when crafting Utility Plans.
2010-02-09 | Structures | Specifications | I-CHANGE RECONST(O) | 9 | BOYD | No pay item was considered for the removal of material on the rehab structures. There were 4 structures and one removal bid item. | Thorough review for bid items on projects and clarification on definition for removal of structures in KYTC Specifications.
2010-02-09 | Pavement | Median Crossover | I-CHANGE RECONST(O) | 9 | BOYD | Plans had substandard pavement design for median crossover in an Interstate Highway situation. | An investigation is suggested for the duration of material used in median crossovers on Interstates.
2010-02-09 | Design | Utility Agreements | SAFETY(P) | 9 | FLEMING | Poor quality of utility plans are sometimes paid through KYTC Design in full and if corrections need to be made , it's almost impossible to follow-up with the utility companies to make changes. | KYTC paying invoices for utility companies work may hold a certain percentage (i.e. , 30-50%) as a retainer until the plans are completed to satisfaction for full payment.
2010-01-29 | Drainage | Bridge Ends | BRIDGE REPLACEMENT(P) | 1 | TRIGG | There were no bridge end drainage on the plans. Flume inlets were used in a change order request. | Several types of end drainages are being used as this is a roadway item; i.e. , Inlet drop boxes , Flumes and Slotted drains. A possible survey from all districts to see what they are doing to come to a consensus on what is the best (See Solution 7)
2010-01-29 | Structures | Alignments | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Bridge and roadway alignment did not match-up. | Highway Design and Structure Design need to work together to make sure plans line up for centerline alignment. A constructability review to catch miss-alignments is recommended for all projects with structures involved.
2010-01-29 | Maintenance of Traffic | Diversions | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Weather conditions caused flooding and damage to the Diversion (temporary bridge) to be less effective. This slowed the project's construction and added cost to both contractor and KYTC. | Better definition on how options for diversion vs. detour are selected for projects. Notes used for the responsibility of maintaining diversions are used and enforceable.
2010-01-29 | Structures | Wing Walls | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Wing Walls were designed where the length encroached into the diversion. | Highway Design and Structure Design need to work together to make sure plans roadway plans and structure layouts correspond and are constructible when construction areas are tight.
2010-01-29 | Design | Phasing | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Culvert plans did not show any phasing that corresponded with roadway phasing. | If roadway phasing occurs , check if structures need to be reviewed for phasing during a constructability review or at final inspection.
2010-01-29 | Maintenance of Traffic | Diversions | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Weather conditions caused flooding and damage to the Diversion (temporary bridge) to be less effective. This slowed the project's construction and added cost to both contractor and KYTC. | Better definition on how options for diversion vs. detour are selected for projects. Notes used for the responsibility of maintaining diversions are used and enforceable.
2010-01-29 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Type 1 guardrail end treatments may be unnecessary and excessive in some cases. | Many of these locations can be justified to install Type 4A or Type 7 end treatments , which are more cost efficient.
2010-01-29 | Design | Guardrail | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Type 1 guardrail end treatments may be unnecessary and excessive in some cases. | Many of these locations can be justified to install Type 4A or Type 7 end treatments , which are more cost efficient.
2010-01-29 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Overhead utility lines were not relocated at the time construction was to start. No work days were charged until utilities were relocated. | Correspond with Utility Companies in advance (several times if need be) to make them be aware the project will be starting in the near future.
2010-01-29 | Maintenance of Traffic | Entrances | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Maintaining entrance access for property owner was problematic since access to owner's property was on the project site. Changes of grade cause multiple maintenance upkeep. | Responsibility for maintenance for entrances should be well defined in contract whether it is in the MOT or the contractor's responsibility.
2010-01-29 | Geotechnical | Karst | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Additional work was required because of sinkholes found on project site. | Known karst areas may require additional geotechnical investigation. A need to undergo a cost analysis for investigation costs vs. change order costs.
2010-01-29 | Design | Phasing | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Culvert plans did not show any phasing that corresponded with roadway phasing. | If roadway phasing occurs , check if structures need to be reviewed for phasing during a constructability review or at final inspection.
2010-01-29 | Maintenance of Traffic | Entrances | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Maintaining entrance access for property owner was problematic since access to owner's property was on the project site. Changes of grade cause multiple maintenance upkeep. | Responsibility for maintenance for entrances should be well defined in contract whether it is in the MOT or the contractor's responsibility.
2010-01-29 | Structures | Wing Walls | BRIDGE REPLACEMENT(P) | 1 | MARSHALL | Wing Walls were designed where the length encroached into the diversion. | Highway Design and Structure Design need to work together to make sure plans roadway plans and structure layouts correspond and are constructible when construction areas are tight.
2010-01-29 | Structures | Dimensions | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Dimensions given for bridge superstructure were shown from centerline of survey. | Contractor requests showing distances from the long chord for efficiency in constructing.
2010-01-29 | Erosion Control Plan | Channel Lining | BRIDGE REPLACEMENT(P) | 1 | TRIGG | Encountered highly erodible materials during project. In addition , ditches were deep cuts and would incur heavy run off during construction. | Review ECP and geotechnical report to counter the materials known on the project.
2010-01-28 | Design | Evaluations | RECONSTRUCTION(O) | 1 | GRAVES | Selection of Consultants are sometimes rushed during the Selection Process and might not be right for the project. | Produce accurate evaluations that coincide with the work of consultants. Revamp the selection categories to have substance to select qualified consultants. Use a tracking tool or Lessons Learned Database.
2010-01-28 | Design | Communication | RECONSTRUCTION(O) | 1 | GRAVES | Issues arise that cause construction to ask questions about the design. The availability to ask those questions are in question , i.e. ask the consultant or KYTC design? | Communication is needed to address issues with a design to have a positive result upon completion of a project. A Cradle to Grave approach can be used for designers to stay involved with projects should design issues occur.
2010-01-28 | Utilities | Relocation | RECONSTRUCTION(O) | 1 | GRAVES | Utilities were not relocated in timely fashion. | Follow up with utility companies to see if utilities can be relocated before Letting. Contractor can sometime work in areas not affected by utilities. Legislation needed to motivate utility companies to cooperate more effectively.
2010-01-28 | Structures | Omission | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Top and Bottom mats of steel for superstructure were omitted from the quantities on the Bill of Reinforcement. | Review of barbills in the design process to accurately show quantities needed for structure.
2010-01-28 | Design | Piping | SAFETY-HAZARD ELIM(P) | 1 | MCCRACKEN | Plans called for drainage pipe length to end at end of project limits and was not conducive to property owner's drainage that overlapped the project edge. The Cabinet had to extend piping past project area to make drainage more effective. | Designers look at overall drainage to make project work and consider entrances for property owners.
2010-01-28 | Design | Piping | SAFETY-HAZARD ELIM(P) | 1 | MCCRACKEN | Plans called for drainage pipe length to end at end of project limits and was not conducive to property owner's drainage that overlapped the project edge. The Cabinet had to extend piping past project area to make drainage more effective. | Designers look at overall drainage to make project work and consider entrances for property owners.
2010-01-28 | Construction | Evaluations | RECONSTRUCTION(O) | 1 | GRAVES | Evaluations used to recommend contractors are not being used efficiently. | Relook at the current evaluation process to see if there could be better categories to reflect the topics to show results from projects constructed in the past. Use a tracking tool or Lessons Learned Database.
2010-01-28 | Design | Omission | RECONSTRUCTION(O) | 1 | GRAVES | Several Items were shown in the Plans such as entrances , removal of drop boxes and pipes , but those quantities were not reflective in the bid items. | Review plans and bid items to ensure quantities needed reflect in the bid items.
2010-01-28 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Lack of cooperation from Railroad companies concerning scheduling of flagmen and information needed from the railroad to get current charges for personnel. | Legislation may be needed to motivate Railroad to be more cooperative in overseeing cost charges to projects.
2010-01-28 | Construction | Railroads | BRIDGE REPLACEMENT(P) | 1 | MCCRACKEN | Rates concerning work completed by Railroad personnel are expensive and may not be accurate when contractors bid for projects. | KYTC communicate with Railroad Companies for current personnel rates during the construction procurement stage. Create an upfront charge that can be biddable to contractors.
2010-01-28 | Structures | Wing Walls | RECONSTRUCTION(O) | 1 | GRAVES | Wing wall on culvert extended past Right-of-Way delineation. | Once ROW Plans are created , Structure Designers should have access to them to review and see if the layout of the structure fits in the ROW limits.
2010-01-28 | Design | Plans | SAFETY-HAZARD ELIM(P) | 1 | MCCRACKEN | Layers on rural plans were very busy considering urban setting and were set on a 20 scale. | When plans are of this nature , set scale to 50.
2010-01-28 | Design | Plans | SAFETY-HAZARD ELIM(P) | 1 | MCCRACKEN | Layers on rural plans were very busy considering urban setting and were set on a 20 scale. | When plans are of this nature , set scale to 50.
2010-01-19 | Construction | Inspection |  |  |  | During this painting project , it was discovered an anchor bolt sheared and had to be repaired before the project could be completed. | Before bridge painting projects , a thorough investigation of the subject bridge for repairs be made prior to completing a painting contract.
2010-01-19 | Maintenance of Traffic | Plan |  |  |  | MOT was not ideal for this project. Inadequate time to properly create a plan. | Require MOT plan for specific larger projects and refer to KYTC and FHWA.
2010-01-19 | Construction | Contracts |  |  |  | Maintenance has separate funding for repairs and painting. This may cause split controversy for both entities such as the above issue where extra funding had to be found for repairs and a change order was issued. | Combine maintenance/repair & painting contracts for projects concerning structures. Secure funds to make the repairs before painting. Schedule process accordingly for use of effective cost management.
2010-01-19 | Utilities | Pipe Sizes | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Existing pipe were to be tied in to new pipe extensions but did not match-up to new ones since there were slight size differences and junction boxes had to be used to tie pipes together. | Better information concerning existing materials , utilities , drainage , etc Revision to manual making sure that all revised plans are submitted and recorded for future use.
2010-01-19 | Design | Communication | PAVEMENT REHAB-INT(P) | 5 | SHELBY | During construction phase the Resident Engineer is not sure who to contact with design concerns. | Contact Construction Liaisons , Consultant Designers or KYTC Structural Design concerning bridge design. Contact District or CO Highway Design for roadway issues. A directory of personnel is recommended.
2010-01-19 | Construction | Inspection | BRIDGE REHAB(P) | 5 | SHELBY | Piers 1 & 4 on KY 395 overpass were constructed without the required amount of reinforcement shown on the plans. | More attention to detail in overseeing contractors work during construction of structures and placement of reinforcement.
2010-01-19 | Design | Communication | BRIDGE REHAB(P) | 5 | SHELBY | During construction phase the Resident Engineer is not sure who to contact with design concerns. | Contact Construction Liaisons , Consultant Designers or KYTC Structural Design concerning bridge design. Contact District or CO Highway Design for roadway issues. A directory of personnel is recommended.
2010-01-19 | Construction | Inspection | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Piers 1 & 4 on KY 395 overpass were constructed without the required amount of reinforcement shown on the plans. | More attention to detail in overseeing contractors work during construction of structures and placement of reinforcement.
2010-01-19 | Construction | Inspection | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Piers 1 & 4 on KY 395 overpass were constructed without the required amount of reinforcement shown on the plans. | More attention to detail in overseeing contractors work during construction of structures and placement of reinforcement.
2010-01-19 | Design | Communication | PAVEMENT REHAB-INT(P) | 5 | SHELBY | During construction phase the Resident Engineer is not sure who to contact with design concerns. | Contact Construction Liaisons , Consultant Designers or KYTC Structural Design concerning bridge design. Contact District or CO Highway Design for roadway issues. A directory of personnel is recommended.
2010-01-19 | Design | Omission | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Lighting was omitted for ramps B & D but was considered for ramps A & C for KY 395. Additional bid item for installation of these lighting features. | Ensure that items included in contract notes are also included in bid items.
2010-01-19 | Design | Omission | BRIDGE REHAB(P) | 5 | SHELBY | Lighting was omitted for ramps B & D but was considered for ramps A & C for KY 395. Additional bid item for installation of these lighting features. | Ensure that items included in contract notes are also included in bid items.
2010-01-19 | Geotechnical | Slides | PAVEMENT REHAB-INT(P) | 5 | SHELBY | After construction of KY 417 overpass , embankment failure occurred. Existing rails were used and had to be excavated and replaced with granular embankment as per Geotech's memo 5/9/08. | When structures are involved , perform an in-depth geotechnical investigation. Buried rails or other materials need to be addressed on previous As-Builts.
2010-01-19 | Geotechnical | Slides | BRIDGE REHAB(P) | 5 | SHELBY | After construction of KY 417 overpass , embankment failure occurred. Existing rails were used and had to be excavated and replaced with granular embankment as per Geotech's memo 5/9/08. | When structures are involved , perform an in-depth geotechnical investigation. Buried rails or other materials need to be addressed on previous As-Builts.
2010-01-19 | Geotechnical | Slides | PAVEMENT REHAB-INT(P) | 5 | SHELBY | After construction of KY 417 overpass , embankment failure occurred. Existing rails were used and had to be excavated and replaced with granular embankment as per Geotech's memo 5/9/08. | When structures are involved , perform an in-depth geotechnical investigation. Buried rails or other materials need to be addressed on previous As-Builts.
2010-01-19 | Design | Omission | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Lighting was omitted for ramps B & D but was considered for ramps A & C for KY 395. Additional bid item for installation of these lighting features. | Ensure that items included in contract notes are also included in bid items.
2010-01-19 | Construction | Contracts | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Discrepancy of KY 714 bridge to be closed on certain dates in the MOT but the Notice to Proceed was issued at a later date and the prescribed dates had to be extended for construction to begin. | Review contract pertinent dates including specified milestones within the projects and create a window where adjustment for those dates can be incorporated until the Notice to Proceed date is known.
2010-01-19 | Construction | Contracts | BRIDGE REHAB(P) | 5 | SHELBY | Discrepancy of KY 714 bridge to be closed on certain dates in the MOT but the Notice to Proceed was issued at a later date and the prescribed dates had to be extended for construction to begin. | Review contract pertinent dates including specified milestones within the projects and create a window where adjustment for those dates can be incorporated until the Notice to Proceed date is known.
2010-01-19 | Construction | Contracts | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Discrepancy of KY 714 bridge to be closed on certain dates in the MOT but the Notice to Proceed was issued at a later date and the prescribed dates had to be extended for construction to begin. | Review contract pertinent dates including specified milestones within the projects and create a window where adjustment for those dates can be incorporated until the Notice to Proceed date is known.
2010-01-19 | Utilities | Pipe Sizes | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Existing pipe were to be tied in to new pipe extensions but did not match-up to new ones since there were slight size differences and junction boxes had to be used to tie pipes together. | Better information concerning existing materials , utilities , drainage , etc Revision to manual making sure that all revised plans are submitted and recorded for future use.
2010-01-19 | Utilities | Pipe Sizes | BRIDGE REHAB(P) | 5 | SHELBY | Existing pipe were to be tied in to new pipe extensions but did not match-up to new ones since there were slight size differences and junction boxes had to be used to tie pipes together. | Better information concerning existing materials , utilities , drainage , etc Revision to manual making sure that all revised plans are submitted and recorded for future use.
2010-01-19 | Design | Communication | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Design projects that have specified dates for whatever reason are written in on plans as notes and sometimes overlooked. | A Cradle to the Grave approach could be taken by project managers and KYTC personnel in order have a more hands-on consistency of communication for the projects. In addition , highlighting/bolding notes on plans.
2010-01-19 | Design | Quantities | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Barrier wall that was calculated on the plans were not enough to complete the project. | When calculating length of barrier walls consider not using only stationing as a measuring tool but account the vertical and horizontal alignment to calculate accurate lengths.
2010-01-19 | Design | Quantities | BRIDGE REHAB(P) | 5 | SHELBY | Barrier wall that was calculated on the plans were not enough to complete the project. | When calculating length of barrier walls consider not using only stationing as a measuring tool but account the vertical and horizontal alignment to calculate accurate lengths.
2010-01-19 | Design | Quantities | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Barrier wall that was calculated on the plans were not enough to complete the project. | When calculating length of barrier walls consider not using only stationing as a measuring tool but account the vertical and horizontal alignment to calculate accurate lengths.
2010-01-19 | Design | Communication | BRIDGE REHAB(P) | 5 | SHELBY | Design projects that have specified dates for whatever reason are written in on plans as notes and sometimes overlooked. | A Cradle to the Grave approach could be taken by project managers and KYTC personnel in order have a more hands-on consistency of communication for the projects. In addition , highlighting/bolding notes on plans.
2010-01-19 | Design | Communication | PAVEMENT REHAB-INT(P) | 5 | SHELBY | Design projects that have specified dates for whatever reason are written in on plans as notes and sometimes overlooked. | A Cradle to the Grave approach could be taken by project managers and KYTC personnel in order have a more hands-on consistency of communication for the projects. In addition , highlighting/bolding notes on plans.
2010-01-08 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 3 | EDMONSON | Upon relocation of utilities , water meters boxes that were planned to be removed and reset to a new location were already damaged and could not be used. Therefore , they needed replacement. | Provide a more flexible fund for removal and replacement of utilities.
2010-01-08 | Utilities | Existing Utilities | RECONSTRUCTION(O) | 3 | EDMONSON | Overlooked ATM service during initial relocation of electrical and telephone utilities had to be relocated and compensated. | More cooperation from utility companies with better communication. Area Development Districts (ADDs) to assist with mapping layout of utility location and documentation.
2010-01-07 | Drainage | Drop Box Inlets | MAJOR WIDENING(O) | 3 | WARREN | Design called for open throat curb inlet boxes in the radius of entrances. Replaced with grated drop boxes (Type16). | Past analysis of truck traffic using entrances with radius curb box inlets are more prone to damage than grated drop box (Type16) drainage.
2010-01-07 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 3 | WARREN | Best Management Practice Plan was not included in original estimate. KYTC allowed contractor to establish BMP. | Future ECPs for projects should be included contractor's estimate.
2010-01-07 | Maintenance of Traffic | Diversions | PAVEMENT REHAB-INT(P) | 3 | BARREN | Phasing called for a one lane operational traffic use during project. | For interstate projects adding temporary shoulder width in order to maintain two lanes of traffic would increase productivity , cause less delay and improve safety.
2010-01-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 3 | BARREN | Type of guardrail end treatments chosen in design were inadequate due to space of entrances; caused additional bridge work. | During design process , invite construction and share information before final plans are produced. Invite design to construction processes and share information to better serve next design.
2010-01-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 3 | BARREN | Type of guardrail end treatments chosen in design were inadequate due to space of entrances; caused additional bridge work. | During design process , invite construction and share information before final plans are produced. Invite design to construction processes and share information to better serve next design.
2010-01-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 3 | BARREN | Type of guardrail end treatments chosen in design were inadequate due to space of entrances; caused additional bridge work. | During design process , invite construction and share information before final plans are produced. Invite design to construction processes and share information to better serve next design.
2010-01-07 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 3 | BARREN | Type of guardrail end treatments chosen in design were inadequate due to space of entrances; caused additional bridge work. | During design process , invite construction and share information before final plans are produced. Invite design to construction processes and share information to better serve next design.
2010-01-07 | Maintenance of Traffic | Diversions | PAVEMENT REHAB-INT(P) | 3 | BARREN | Phasing called for a one lane operational traffic use during project. | For interstate projects adding temporary shoulder width in order to maintain two lanes of traffic would increase productivity , cause less delay and improve safety.
2010-01-07 | Construction | Coordination | MAJOR WIDENING(O) | 3 | WARREN | Communication in several areas including drainage , ROW , and utilities was needed for the completion of this project. | Incorporating a monthly status update meeting with all parties involved in order to sight issues before they become problems.
2010-01-07 | Design | Coordination | PAVEMENT REHAB-INT(P) | 3 | BARREN | Misunderstanding or improper communication regarding Value Engineering (VE) proposal caused changes in construction with a request for VE Construction Proposal (VECP). | Implement VE study proposal during the design phase; while still providing incentives for contractor to pursue VECPs when necessary.
2010-01-07 | Design | Coordination | PAVEMENT REHAB-INT(P) | 3 | BARREN | Misunderstanding or improper communication regarding Value Engineering (VE) proposal caused changes in construction with a request for VE Construction Proposal (VECP). | Implement VE study proposal during the design phase; while still providing incentives for contractor to pursue VECPs when necessary.
2010-01-07 | Structures | Masonry Coating | MAJOR WIDENING(O) | 3 | WARREN | Bid Item was omitted for retaining wall on front face exposed to public sight. | Add description for use of masonry coating on retaining walls in the standard specifications or standard drawings. Include item as a Bid Item.
2010-01-07 | Geotechnical | Karst | MAJOR WIDENING(O) | 3 | WARREN | Sinkholes were found on the project area. Therefore , additional work needed for sinkholes to be filled. | A thorough investigation for geotechnical data in areas with karst. A study to get cost benefits/savings if a more detailed geotechnical survey is needed versus change orders for specific projects with karst.
2010-01-07 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 3 | WARREN | Conduits were installed at shallow elevations and interfered with installation of drainage. | A more constant and effective line of communication with utility companies before and during projects.
2010-01-07 | Pavement | Striping | PAVEMENT REHAB-INT(P) | 3 | BARREN | Raised pavement markers were in the original plans but were replaced with a new product to test for reflectivity in painted striping. | Provide more information concerning new products and communicate new ideas during design phase.
2010-01-07 | Pavement | Striping | PAVEMENT REHAB-INT(P) | 3 | BARREN | Raised pavement markers were in the original plans but were replaced with a new product to test for reflectivity in painted striping. | Provide more information concerning new products and communicate new ideas during design phase.
2010-01-07 | Right-of-Way | Coordination | MAJOR WIDENING(O) | 3 | WARREN | Lack of coordination with Funeral Home regarding relocation and restoration of decorative pond. | Negotiations must be completed before project begins construction through more effective communication concerning ROW.
2009-12-10 | Drainage | Pipe Sizing | MAJOR WIDENING(O) | 6 | SCOTT | Pipe size difference in field compared to plans. | Conduct a field investigation and review plans to ensure consistency.
2009-12-10 | Drainage | Pipe Sizing | MAJOR WIDENING(O) | 6 | SCOTT | Pipe size difference in field compared to plans. | Conduct a field investigation and review plans to ensure consistency.
2009-12-10 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 6 | SCOTT | Steel on culvert footers did not have enough cover. | Designer review plans thoroughly before submission. Then do another review prior to or during the inspection meetings.
2009-12-10 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 6 | SCOTT | Steel on culvert footers did not have enough cover. | Designer review plans thoroughly before submission. Then do another review prior to or during the inspection meetings.
2009-12-10 | Pavement | Shoulders | MAJOR WIDENING(O) | 6 | SCOTT | DGA on shoulders in some super-elevated sections washed out for this project. This washout was more severe than normally encountered in past experience. The cause isn't apparent. | Consider wedge curbs and flumes , earth wedges instead of DGA , or larger aggregate during the design process.
2009-12-10 | Structures | Phasing | MAJOR WIDENING(O) | 6 | SCOTT | Construction of bridge endbents needed additional piling during phasing. | Communication between roadway and bridge design to show constructability of structure during phasing construction. A constructability review panel made early before construction with contractors.
2009-12-10 | Structures | Phasing | MAJOR WIDENING(O) | 6 | SCOTT | Construction of bridge endbents needed additional piling during phasing. | Communication between roadway and bridge design to show constructability of structure during phasing construction. A constructability review panel made early before construction with contractors.
2009-12-10 | Erosion Control Plan | Topdressing Fertilizing | MAJOR WIDENING(O) | 6 | SCOTT | Topdressing was not included in the project. | This item should be a bid item for ECP as permanent topdressing fertilizing.
2009-12-10 | Pavement | Shoulders | MAJOR WIDENING(O) | 6 | SCOTT | DGA on shoulders in some super-elevated sections washed out for this project. This washout was more severe than normally encountered in past experience. The cause isn't apparent. | Consider wedge curbs and flumes , earth wedges instead of DGA , or larger aggregate during the design process.
2009-12-10 | Erosion Control Plan | Topdressing Fertilizing | MAJOR WIDENING(O) | 6 | SCOTT | Topdressing was not included in the project. | This item should be a bid item for ECP as permanent topdressing fertilizing.
2009-12-10 | Geotechnical | Piling/Drilled Shaft | MAJOR WIDENING(O) | 6 | SCOTT | Placement of piling to rock elevation was not encountered at plan elevations. They were at a much lower elevation. | Conduct a more thorough geotechnical investigation of the areas where structures are going to be constructed.
2009-12-10 | Geotechnical | Piling/Drilled Shaft | MAJOR WIDENING(O) | 6 | SCOTT | Placement of piling to rock elevation was not encountered at plan elevations. They were at a much lower elevation. | Conduct a more thorough geotechnical investigation of the areas where structures are going to be constructed.
2009-12-10 | Pavement | Coordination | MAJOR WIDENING(O) | 6 | SCOTT | Milling was needed prior to overlay due to the variances in elevations due to normal/super areas with cross slope and existing elevations. No bid item set up for this | Item needs to be addressed in the contract as a bid item. Designers must be aware that this occurrence happens more often than not and a survey should be made prior to construction to detect any differences in elevations
2009-12-10 | Pavement | Coordination | MAJOR WIDENING(O) | 6 | SCOTT | Milling was needed prior to overlay due to the variances in elevations due to normal/super areas with cross slope and existing elevations. No bid item set up for this | Item needs to be addressed in the contract as a bid item. Designers must be aware that this occurrence happens more often than not and a survey should be made prior to construction to detect any differences in elevations
2009-12-10 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 6 | SCOTT | Unsuitable material was found on site and had to exchange Channel Lining Class IV to Channel Lining Class II & III for subgrade. | Conduct an in-depth geotechnical survey.
2009-12-10 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 6 | SCOTT | Unsuitable material was found on site and had to exchange Channel Lining Class IV to Channel Lining Class II & III for subgrade. | Conduct an in-depth geotechnical survey.
2009-12-10 | Design | Omission | MAJOR WIDENING(O) | 6 | SCOTT | Embankment quantities were omitted on plan sheets X19 & X20. | Designer review plans thoroughly before submission. Then do another review prior to or during the inspection meetings.
2009-12-10 | Pavement | Striping | MAJOR WIDENING(O) | 6 | SCOTT | Durable tape (150mm-Type I) was used in lieu of Thermo-plastic pavement striping for the bridge. Past experience with paint and thermo-plastic markings do not adhere to concrete as well as durable tape. | Use of Durable Tape for sections with concrete surfaces. In past experience , there have been no maintenance issues that may affect the longevity with this type of striping on concrete.
2009-12-10 | Pavement | Striping | MAJOR WIDENING(O) | 6 | SCOTT | Durable tape (150mm-Type I) was used in lieu of Thermo-plastic pavement striping for the bridge. Past experience with paint and thermo-plastic markings do not adhere to concrete as well as durable tape. | Use of Durable Tape for sections with concrete surfaces. In past experience , there have been no maintenance issues that may affect the longevity with this type of striping on concrete.
2009-12-10 | Design | Omission | MAJOR WIDENING(O) | 6 | SCOTT | Embankment quantities were omitted on plan sheets X19 & X20. | Designer review plans thoroughly before submission. Then do another review prior to or during the inspection meetings.
2009-12-10 | Design | Shelved Plans | MAJOR WIDENING(O) | 6 | SCOTT | Milled rumble strips Note not in the plans when plans were produced. A change of policy for rumble strips were made and was not called out. | Review plans to make sure updated policies have been applied to plans that may have been shelved for an extended period of time
2009-12-10 | Design | Shelved Plans | MAJOR WIDENING(O) | 6 | SCOTT | Milled rumble strips Note not in the plans when plans were produced. A change of policy for rumble strips were made and was not called out. | Review plans to make sure updated policies have been applied to plans that may have been shelved for an extended period of time
2009-12-10 | Utilities | Relocation | RECONSTRUCTION(O) | 7 | FAYETTE | Gas line needed to be relocated. | Would normally be considered in Pre-construction process.
2009-12-10 | Structures | CAP | RECONSTRUCTION(O) | 7 | FAYETTE | Apply natural cut stone veneer to faces of barrier walls. Communicate All Promises (CAP) | Would normally be considered in Pre-construction process.
2009-12-10 | Construction | Temporary Fencing | RECONSTRUCTION(O) | 7 | FAYETTE | Temporary orange construction fencing placed in areas for archaeological sites and woven wire fencing with vinyl site board place on UK's property for equestrian compliancy. | Unavoidable.
2009-12-10 | Environmental | Archaeological Study | RECONSTRUCTION(O) | 7 | FAYETTE | Perform Archaeological Phase 2 Study on sites. | Funding needed to be established. Would normally be considered in Pre-construction process.
2009-12-10 | Utilities | Relocation | RECONSTRUCTION(O) | 7 | FAYETTE | Waterline needed to be relocated. | Would normally be considered in Pre-construction process.
2009-12-10 | Design | Relocation | RECONSTRUCTION(O) | 7 | FAYETTE | Avoiding break in services to customers. | Unavoidable.
2009-12-10 | Construction | Earthwork | RECONSTRUCTION(O) | 7 | FAYETTE | Waterline needed to be relocated but the excavated material had asbestos and was unsuitable fill and had to be removed and replaced. | Unavoidable.
2009-12-04 | Erosion Control Plan | Sodding | RECONSTRUCTION(O) | 4 | MARION | Sodding is not bid throughout the project. This begs for legitimate public complaint. | Bid sodding uniformly throughout the project area or do not bid sodding.
2009-12-04 | Drainage | Temporary Pipes | RECONSTRUCTION(O) | 4 | MARION | Insufficient temporary pipe quantities bid on part-width projects. | Bid sufficient temporary pipes equal to the number of existing and future entrances on part-width projects. Unused pipes may be deleted whereas required pipes result in change orders.
2009-12-04 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 4 | MARION | DGA used for maintenance of driveways had been left off from the plans. | Provide a separate bid item for DGA for maintenance of driveways and entrances. Bid 10 to 20% over the needed quantity to prevent a change order for this item. Unused quantity may always be deleted.
2009-12-04 | Environmental | Vegetation | RECONSTRUCTION(O) | 4 | MARION | Daylighting in areas with extensive rock roadbed will impede vegetative growth. | Use rock roadbed under surfaced areas and shoulders only. Use CSB from the edge of shoulder to the bottom of rock roadbed or ditch. CSB is more workable and will sustain vegetation in a matter of years.
2009-12-04 | Construction | Contracts | RECONSTRUCTION(O) | 4 | MARION | Minor unforeseen change orders may delay the construction completion date. | Include a discretionary bid item for a limited lump sum to enable the resident engineer to handle urgent field problems expediently without having to go through the change order approval process.
2009-12-04 | Pavement | Shoulders | RECONSTRUCTION(O) | 4 | MARION | DGA on shoulders in super-elevation sections wash out. | Place larger rocks in affected areas. Install properly constructed flumes.
2009-12-04 | Maintenance of Traffic | Tie-ins | RECONSTRUCTION(O) | 4 | MARION | Lack of MOT items such as a temporary diversion at the tie-in of the new and existing road make for difficult and possibly hazardous construction conditions. | Provide MOT at the tie-ins. Putting a set of Draft plans with a disclaimer on the Web for longer than 3 weeks prior to letting may allow a contactor to ask relevant questions that will identify and eliminate potential change orders.
2009-12-04 | Construction | Earthwork | RECONSTRUCTION(O) | 4 | MARION | Handling earthwork on projects that are almost balanced can be problematic for the contractor. | Specify the volumes of embankment and excavation on the General Summary Sheet on projects that are balanced. This will enable the contactor to handle earthwork more effectively.
2009-12-03 | Design | Shelved Plans | MAJOR WIDENING(O) | 4 | MEADE | Original designs that go to letting after an extended period of time without an in-depth review may contain potential for change orders due to newly constructed structures or general permitted disturbances while the plans were on the shelf. | Conduct both a detailed review of the plans and a thorough field inspection preferably by a set of new eyes/team unfamiliar with the project to effectively identify the conflict areas hence revise the plans accordingly to avoid costly change orders.
2009-12-03 | Pavement | Striping | MAJOR WIDENING(O) | 4 | MEADE | Thermo-plastic pavement striping is subject to possible damage by snow plowers in areas with substantial snowfall during winter months. | Use permanent paint striping in areas where thermo-plastic striping may be subject to damage by snow plowers.
2009-12-03 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 4 | MEADE | Due to an oversight a Fire Vault supplying water to sprinklers in several adjacent businesses had not been located on the plans. The Fire Vault was relocated since it was located in the ditch line and could not be worked around. | Conduct a field walk on all projects. A more thorough field investigation/walk should locate all utility features within the project area.
2009-12-03 | Pavement | Design | MAJOR WIDENING(O) | 4 | MEADE | Pavement thickness inadequate in areas supporting heavy such as school bus traffic. | Review the pavement design before the project is let. If plans have been on the shelf for an extended period of time , closely review ESAL to ensure it reflects current and accurate heavy traffic count.
2009-12-03 | Right-of-Way | CAP | MAJOR WIDENING(O) | 4 | MEADE | Permits issued; i.e. , for an entrance within the project area , before the project is let or while the project is being designed may result in conflicts during construction. | Permits and/or promises made to businesses should be documented and sent to notify the project manager to prevent an otherwise avoidable change order.
2009-12-03 | Drainage | Berms | MAJOR WIDENING(O) | 4 | MEADE | Clogged berms and channel lining placed in sinkholes do not drain and result in standing water which can be a health hazard by being the breeding grounds for mosquitoes capable of transmitting diseases harmful to humans. | Purchase additional right-of-way to enable the Maintenance personnel to access the affected areas to employ remedial measures.
2009-12-03 | Drainage | Sheet Flow | MAJOR WIDENING(O) | 4 | MEADE | Sheet flow across super-elevation section created unsafe driving conditions. | Add drainage blanket to the super elevation sections. Increase the DGA quantity. Install non-perforated and perforated pipe as needed.
2009-11-13 | Design | Underground Tank | NEW ROUTE(O) | 8 | PULASKI | Removal of septic system on property during construction was not specified on plan. | Designers be aware if a property has a dwelling on it to check with property owners in locating septic systems and show the location on the plans.
2009-11-13 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 8 | PULASKI | Planned MOT was not used. An alternate plan was used to adequately handle the maintenance of traffic due to phasing of project. Use of Flashing arrow for lane closure. | A consensus was made to treat MOTs separately and the MOT Plan to be made on-site at the discretion of the Resident Engineer to coordinate with the Contractors.
2009-11-13 | Pavement | Coordination | MAJOR WIDENING(O) | 8 | PULASKI | Milling was needed for the variances in elevations due to a prior overlay in the time between finished Design and start of Construction. | Item needs to be addressed in the contract. Communication during a constructability review and communication/check that maintenance overlay was made in project area.
2009-11-13 | Structures | Geotextile Fabric | NEW ROUTE(O) | 8 | PULASKI | Geotextile fabric was not a bid item on the structure plans. | Roadway Plans vs. Structural Plans need to address this item early in the design process to identify who's responsibility it is to call out this quantity.
2009-11-13 | Traffic | Raised Pavement Markers | MAJOR WIDENING(O) | 8 | PULASKI | For a divided highway , there was no clarification on who was to place the raised pavement markers on the roadway. It was not in the plan. It was said that this item was to be placed by State Contracts. | Communicate to construction the responsibility of raised pavement markers during a constructability review.
2009-11-13 | Utilities | Existing Utilities | NEW ROUTE(O) | 8 | PULASKI | Wrong pipe size on the existing waterline was given on the plans. New waterline was to tie in to the existing line. | Check with utility companies.
2009-11-13 | Design | Adjacent Projects | NEW ROUTE(O) | 8 | PULASKI | Matching centerline alignment to tie into adjacent projects. | Coordination between consultants to tie-in centerline alignments and physically shoot in the centerlines for consistency.
2009-11-13 | Design | Adjacent Projects | NEW ROUTE(O) | 8 | PULASKI | Waste Material vs. Fill Material on adjacent projects. | The use of the materials could have been more efficient when separating projects into small projects.
2009-11-13 | Design | Underground Tank | MAJOR WIDENING(O) | 8 | PULASKI | The septic lines and tank were shown on the plans based on the property owner's recollection. During construction , removal of this septic system was needed due to inaccurate information. ***This is a reoccurring problem*** | Designers be aware if a property has a dwelling on it to check with property owners in locating septic systems and show the location on the plans. Make note if area is not exact , write approximate or unknown.
2009-11-13 | Construction | Rumble Strips | NEW ROUTE(O) | 8 | PULASKI | Sawed-in rumble strips were placed. Controversy of having Rolled vs. Sawed-in rumble strips. | It was preferred that Sawed-in rumble strips are better to use. Generally , Sawed-in rumble strips have more uniform spacing , higher density and are more durable.
2009-11-13 | Design | Quantities | NEW ROUTE(O) | 8 | PULASKI | Unstable area was located in plans , but not enough granular embankment was called out due to unsuitable material. | General consensus is to continue to call out procedural estimated quantities. Contractor prefers underrun rather that overrun of items.
2009-11-12 | Utilities | Relocation | BYPASS(O) | 8 | ADAIR | Utilities were on the roadway plans but not exactly in the specified location. | Check with utility companies.
2009-11-12 | Structures | Granular Pile Core | BYPASS(O) | 8 | ADAIR | Granular Pile Core quantities were not specified on plan for two bridges. | Communication between geotech and structure designers to show if a granular pile core is needed for the structure. During plan processing the consultant plans and in-house plans check for these items. ***Investigate: Should this be a roadway or structur
2009-11-12 | Structures | Standard Drawings | BYPASS(O) | 8 | ADAIR | A retaining wall was built with standard drawings but no masonry coating was called out. | Call out in standard drawing and charge as incidental. In the meantime , place a note in the contract to clarify if not clear.
2009-11-12 | Pavement | Standard Drawings | BYPASS(O) | 8 | ADAIR | Concrete quantity was in the plans for RBB-001-07 as a roadway item. Initial settlement at the bridge approaches were observed at the shoulder. | After placement , settlement occurred and an asphalt overlay was added to remedy the bump onto the bridge. ***Investigate: Reviewing this standard drawing?***
2009-11-12 | Construction | Striping Removal | BYPASS(O) | 8 | ADAIR | Item was not spelled out as a pay item or incidental. | Place in Specifications explicitly how this item for payment should be handled. In the meantime , place a note in the contract to clarify if not clear.
2009-11-12 | Erosion Control Plan | Seeding | BYPASS(O) | 8 | ADAIR | Quantities were estimated by using the disturbed limit area which causes an underrun. | Estimate the seeding quantities to the Right-of-Way line.
2008-10-30 | Geotechnical | Top of Rock | RECONSTRUCTION(O) | 9 | FLEMING | Sound rock occurred approximately six inches below the proposed bottom of footing elevation for a portion of the footer. | It was decided to use mass concrete to compensate for the difference in elevation.
2008-10-30 | Design | Adjacent Projects | RECONSTRUCTION(O) | 9 | FLEMING | The adjoining project had been completed and as stated in the Maintenance of Traffic notes , approximately 300 striped drums became property of the Department and the maintenance of these devices became the responsibility of the Department. | Since it would be impractical for the Department to maintain these devices with State forces and since the Traffic Control for this project was still needed , it was agreed that the responsibility for maintaining these devices should be the Contractor's.
2008-10-30 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 9 | FLEMING | During phase construction , traffic was required to utilize the new shoulder pavement. The noise driving over formed rumble strips caused driver distraction and possible annoyance to surrounding neighborhoods. | In order to avoid this , it was agreed to omit the forming of the rumble strips and to subsequently construct Rumble Strips Type 3. It was the intent of this Change Order to utilize Rumble Strips Type 3 only when absolutely necessary and that future tem
2008-10-30 | Design | Special Note | RECONSTRUCTION(O) | 9 | FLEMING | The Special Note for Dense Graded Aggregate and Crushed Stone base was omitted from the project. The Special Note reflected a gradation change that had been incorporated into the 1994 Standard Specifications. | The Contractor requested that the Special Note for Dense Graded Aggregate and Crushed Stone base be incorporated into the project.
2008-10-30 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 9 | FLEMING | The existing typical section for Brown's Lane consisted of 10 foot shoulders constructed of 5 inches DGA. The maintenance of traffic plan illustrated the use of the shoulders for detour traffic. | It was decided that the shoulders were deficient in design and should be reconstructed with full depth.
2008-10-30 | Structures | Hold-in-Place Steel | RECONSTRUCTION(O) | 9 | FLEMING | The Contractor requested the use of stay in place forms for the construction of all the bridge decks on the project. | The request was granted resulting in a savings of $31 , 304.62 to the Cabinet.
2008-10-30 | Traffic | Lighting | RECONSTRUCTION(O) | 9 | FLEMING | When work began on this project , the existing lighting was not functional. The Contractor submitted a proposal to make the necessary repairs at a cost of $136 , 000.00 including maintenance. It was felt that this was a prohibitive expenditure. | Central Office , Division of Traffic recommended using high mast lighting in its final location. This would provide the necessary temporary lighting as well as permanent lighting. The high mast lighting also presented a savings over the proposed lighti
2008-10-30 | Construction | Public Relations | RECONSTRUCTION(O) | 9 | FLEMING | It was desired to mitigate the aesthetic impact of the reconstruction of I-264 at I-64 along the boundaries of the City of St. Regis Park. | It was agreed to construct a 26 inch barrier atop the retaining wall with traffic barrier and the concrete shoulder barrier at the following locations: Sta 21+00 to 29+19.54 Rt. Ramp 7 , Sta 205+39.25 to 217+50 Rt. I-64. The wall was bid Special Wall Ty
2008-10-30 | Utilities | Delays | NEW ROUTE(O) | 9 | LEWIS | In order to lower the sanitary sewer at Rt. Sta. 12+17 , a 30 inch water main had to be lowered. Lowering of the water main was controlled by the relocation of LG&E electrical poles to the southern right-of-way line. The proposed dates of relocation we | In order to expedite the work necessary to clear the electrical facilities and allow for the lowering of the water main , it was agreed to have the Contractor relocate the electrical service for Parcel 18 once the new LG&E poles were in place.
2008-10-30 | Design | Safety | RECONSTRUCTION(O) | 9 | FLEMING | There were concerns about the safety of the adjacent property owners along Ramp 7. The plans showed their backyards to be approximately 45 feet from the edge of shoulder. | In order to enhance safety , it was agreed to install Type 1 Shoulder Barrier from Station 7+50 to Station 19+00 Right as directed by Central Office.
2008-10-30 | Design | Omission | RECONSTRUCTION(O) | 9 | FLEMING | A Special Note for Staking was omitted from the proposal. The Contractor was responsible for staking right of way limits , establishing the project survey center lines , and establishing baselines of ramps and center lines of side roads and frontage ro | A Change Order added funds for the staking.
2008-10-30 | Structures | Approaches | RECONSTRUCTION(O) | 9 | FLEMING | There were concerns about potential pavement failures at bridge ends of Ramp 5 over I-264 and I-264 over Beargrass Creek due to unanticipated settlement of bridge backfill. | Approach slabs were designed for these bridges and it was agreed to construct them as detailed on the revised plans. The addition of approach slabs eliminated the need for armored edges and reduced the quantity of Class AA concrete in the backwalls and e
2008-10-30 | Maintenance of Traffic | Detours | NEW ROUTE(O) | 9 | LEWIS | In order to reconstruct Jeanine Drive , it was necessary to close Jeanine Drive to traffic. This was due to grades of the new sanitary sewer being located in the center of Jeanine Drive. Also , the grade difference between new Jeanine Drive and existi | Temporary signs were fabricated to establish a detour route during construction of Jeanine Drive.
2008-10-30 | Drainage | Omission | NEW ROUTE(O) | 9 | LEWIS | The roadway plans called for the construction of RCBC extensions for the double barrel elliptical storm sewer at Sta. 108+72 Fern Valley Road. Sheet 82 included the details; however , the quantities were omitted. | Unit price for culvert extensions was established with Change Order.
2008-10-30 | Structures | Retaining Walls/MSE | RECONSTRUCTION(O) | 9 | FLEMING | There were concerns about the project proposal's Special Provision 66J(91) involving backfill material for retaining walls. | It was agreed to substitute Special Provision 66K(91) in lieu of the project proposal's Special Provision 66J(91) at no additional cost. Special Provision 66K(91) involves backfill material for retaining walls and allowed the use of sand in lieu of stone
2008-10-30 | Drainage | Ponding | NEW ROUTE(O) | 9 | LEWIS | Prior to beginning the project , water would drain off the parking lot for Parcel 38 into the existing ditch. Upon building the header curb from Rt. Sta. 53+00 to Sta. 56+20 , ponding was observed on the parking lot. | It was agreed to install a sloped and flared headwall with a 10 inch pipe at the low spots along the header curb , which tied into the proposed 15 inch reinforced concrete pipe.
2008-10-30 | Maintenance of Traffic | Striping | RECONSTRUCTION(O) | 9 | FLEMING | When traffic was placed on the completed Ramp 7 , the right edge line was permanently taped. After eastbound I-64 traffic was placed on the new pavement in Phase 8 a merge condition existed with ramp 7 and eastbound I-64 , which was causing the ramp tr | To alleviate the traffic congestion , it was agreed to place the ramp traffic onto the shoulder pavement from Sta 209+00 to Sta 223+50 on eastbound I-64. This created an added lane entrance configuration for the ramp traffic that required an item for Re
2008-10-30 | Materials | Concrete Mix | RECONSTRUCTION(O) | 9 | FLEMING | Ramp 3 had to be closed in order to complete the construction of the collector-distributor road number 3 (CD 3) from Sta 194+50 to Sta 197+50. | To facilitate the construction of the PCCP and timely reopening of the ramp , it was agreed to modify the PCCP mixture to the Department's PCCP 72 hour mix to allow early opening of traffic.
2008-10-30 | Structures | Dimensions | RECONSTRUCTION(O) | 9 | FLEMING | The Louisville and Jefferson County Metropolitan Sewer District (MSD) expressed concerns that the proposed larger stream opening on the I-264 bridge over Beargrass Creek would aggravate downstream flooding , which would adversely affect properties downst | The structure was modified to reduce the upstream opening to what had previously existed. It was felt that the modification would only be in place for a short time because the MSD was performing drainage studies for the entire area and retention basins w
2008-10-30 | Construction | Coordination | RECONSTRUCTION(O) | 9 | FLEMING | Humana Hospital Suburban was building an addition to their hospital which required the addition of a turning lane off Dutchman's Lane. The design of the turn lane extends through the construction limits of Dutchman's Lane to the intersection with Brown's | In order to avoid possible conflicts between the Department's Contractor and the Contractor constructing the additional turning lane within the project it was agreed to have the Department's Contractor construct that portion of the turning lane within the
2008-10-30 | Maintenance of Traffic | Diversions | NEW ROUTE(O) | 9 | LEWIS | Plans indicated that temporary gravel diversions were to be constructed in order to build nine cross drains from Sta. 56+70 to Sta. 89+20. Diversions could not be built due to conflicts with existing utility poles as well as new curb box inlets being wit | Temporary pipe drainage was installed near the locations of the permanent cross drains using the drill and bore method with 20 casing. This method did not impact traffic.
2008-10-30 | Right-of-Way | Easements | NEW ROUTE(O) | 9 | LEWIS | The owner of Parcel 1 refused to sell the property to the Department necessary for a permanent drainage easement as shown on the contract plans. | It was decided to revise the proposed drainage which required a smaller permanent drainage easement.
2008-10-30 | Drainage | Pipes | RECONSTRUCTION(O) | 9 | FLEMING | After work began on boring and jacking a thirty inch culvert pipe at Sta 193+50 on I-64 , it was discovered that the existing fill had been constructed out of rock. This made the boring and jacking method impossible. | Given the existing fill conditions , the recommended installation method was tunneling. The original bid for boring and jacking was $204.00 per linear foot while the tunneling method was $497.40 linear foot. A total of 340 linear foot of pipe was to be
2008-10-30 | Design | Median | RECONSTRUCTION(O) | 9 | FLEMING | In reviewing the plans , no plantings were set up in the split median from Sta 193+50 to Sta 243+50 on I-64. However , the split median adjoining this newly constructed median was planted. | To continue the screening affect of the existing median it was agreed to plant Burning Bushes. It was agreed that six inches of aggregate should be utilized in lieu of mulch. Because the Burning Bushes grow best in acidic soil and the Crushed Stone Aggr
2008-10-30 | Traffic | Lighting | RECONSTRUCTION(O) | 9 | FLEMING | The wiring for the high mast lighting did not allow for adequate grounding. | Central Office Division of Traffic modified the wiring schedule for the high mast lighting , changing the ducted cable from the two conductor to three conductor in order to provide adequate grounding.
2008-10-30 | Environmental | Landscaping | RECONSTRUCTION(O) | 9 | FLEMING | During the initial planting inspection of the landscaping it was discovered that virtually all of the Burning Bushes , planted in the split median between approximate Sta 230+00 to Sta 244+00 I-64 , had perished. An examination of the root balls showed | It was agreed to remove the mulch and topsoil in the affected area and replace it with a loam type topsoil meeting the requirements of Section 827.09 of the Standard Specifications with some modifications.
2008-10-30 | Geotechnical | Settlement | RECONSTRUCTION(O) | 9 | FLEMING | Before the project was called complete , undesirable settlement occurred at the bridge ends for Ramp 5 over I-264 , Ramp 5 over I-64 , and WB I-64 over I-264. | Since all records indicated that the fill was constructed properly , it was agreed that the cost of correcting this settlement would be shared by the Department and Contractor. It was further agreed that the method of correction would be a foam injectio
2008-10-30 | Utilities | Relocation | RECONSTRUCTION(O) | 9 | FLEMING | During utility relocation , Louisville Gas and Electric relocated their transmission and distribution directly adjacent to the proposed storm sewer from Sta 20+45 Rt. Ramp 5 to Sta 692+00 Rt. I-264. The poles were anchored into solid rock and the storm | An alternate blasting plan had to be developed. It was agreed to remove rock at the affected locations by trenching. It was further agreed that the storm sewer would be encased with Class A concrete to the top of rock at the affected locations. The wor
2008-10-30 | Construction | Ride Quality | RECONSTRUCTION(O) | 9 | FLEMING | As per Section 501.24.02 of the 1991 Kentucky Standard Specification , outstanding work has been performed to achieve an exceptionally smooth pavement surface. | It was agreed that the Supplemental Unit Price for PCCP Bonus I shall be full compensation for satisfying the requirements for incentive payments contained in the Standard Specifications.
2008-10-30 | Geotechnical | Quantities | RECONSTRUCTION(O) | 9 | FLEMING | Several Embankments were constructed out of black shale. In these areas , the select granular embankment was not used. Also , the subgrade in many of the cut areas especially under the existing roadway , was very soft and had to be undercut approxima | These factors caused the plan quantity of embankment in place to increase.
2008-10-30 | Geotechnical | Unsuitable Material | NEW ROUTE(O) | 9 | LEWIS | Subgrade from Sta. 57+00 to Sta. 60+00 was prepared according to specifications and plans. Geogrid was placed with DGA. As construction continued , pumping and rutting was noticed. A Cone Penetrometer test indicated that a penetration of 2 feet below | The roadbed was modified using Portland cement , 16 inches deep with 7% cement. A special geotextile fabric was placed in order to decrease delays due to curing. A temporary solution of undercutting 1.5 feet and refilling with No. 3 Stone was utilized
2008-10-30 | Traffic | Safety | RECONSTRUCTION(O) | 9 | FLEMING | A review of the plans revealed that the design for the eastbound I-264 to I-64 movement was inadequate , based upon two previous projects with the same type of traffic plan. The same type of traffic plan led to numerous accidents at the Breckinridge Lan | To prevent a similar situation , it was agreed to redesign the traffic plan through a task force meeting with the Consultant. The revised traffic movement plan presented a savings of $256 , 634.95 over the old traffic plan.
2008-10-30 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 9 | FLEMING | The typical section for detour pavement showed an unpaved shoulder. However , there were concerns about potential maintenance problems with rutting on the shoulders and the difficulty in repairing any rutting. | It was agreed to pave the shoulders full depth , which resulted in an overrun in plan quantity.
2008-10-30 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 9 | FLEMING | The plans set up woven wire fence for the right of way and access control , but the area surrounding the project was developed. | It was agreed to utilize six foot chain link fence instead.
2008-10-30 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 9 | FLEMING | Phase 8 of the Maintenance of Traffic plans showed constructing westbound I-64 from Sta 217+00 to Sta 238+50 along with a portion of Ramp 5. This would have eliminated a dedicated lane for an exit ramp from westbound I-64 to I-264. After reviewing the t | The Contractor was directed to maintain the ramp traffic on its existing lane , construct westbound I-64 part width , and then move the ramp lane onto the new pavement to complete the work. The Contractor submitted a request for extra expenses incurred
2008-10-30 | Structures | Phasing | RECONSTRUCTION(O) | 9 | FLEMING | In order to form the deck for the proposed collector-distributor road (CD #3) over the I-264 structure , the overhang of the existing eastbound I-64 over I-264 had to be removed. | This necessitated the need to anchor the temporary barrier wall on the existing deck to prevent the wall from falling onto I-264 should it be hit.
2008-10-30 | Drainage | Error | RECONSTRUCTION(O) | 9 | FLEMING | In reviewing the proposed construction of the 12 inch slotted drain at Sta 684+50 to Sta 688+50 , two problems were discovered. The first problem was that the pipe was shown to drain with the stationing. This could be accomplished with a variable heigh | To alleviate this problem , it was agreed to utilize a riser of sufficient height to provide proper slope of the pipe. Further , a drainage review showed that 200 linear feet of 21 inch slotted drain was needed to handle the anticipated runoff.
2008-10-30 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 9 | FLEMING | While reviewing the functioning of the I-64 detour , it was apparent that the excessive speed of traffic was contributing to the frequency of accidents. Standard Reduced Speed Ahead and Speed Limit 45 mph signs were ineffective. | To reduce the excessive speed of the traffic , it was agreed to utilize off duty police officers and their vehicles to enforce the posited speed limit.
2008-10-30 | Utilities | Omission | NEW ROUTE(O) | 9 | LEWIS | The plans for a 10 inch ductile iron sewer crossing at Sta. 12+17 did not indicate that special backfill material was required. The Metropolitan Sewer District inspector directed that Type 1 (sand , flushed and jetted) was to be used. | It was agreed that #57 stone would suffice in lieu of sand and the supplemental unit price for #57 Stone Backfill was established.
2008-10-30 | Environmental | Landscaping | RECONSTRUCTION(O) | 9 | FLEMING | After reviewing the landscaping plans , it was decided to make changes to the plans. | Flowering trees were added , some non-native species were eliminated , and some additions to the landscaping adjacent to the hospital were made. It was also suggested that a commitment needed to be made for maintaining landscaping.
2008-10-30 | Drainage | Existing Pipe | RECONSTRUCTION(O) | 9 | FLEMING | While excavating for Abutment No. 2 of the eastbound I-264 bridge over Beargrass Creek , the trench of an abandoned 24 inch water main was encountered. The pipe was approximately four feet below the bottom of the footer elevation with a granular materia | It was decided that the trench backfill be removed to the pipe and be replaced with mass concrete.
2008-10-30 | Structures | Omission | NEW ROUTE(O) | 9 | LEWIS | A bid item for removing the existing Fern Valley Road Bridge over Fern Valley Ditch was omitted from the plan quantities. | Bit item Remove Existing Structure was added to contract with change order.
2008-10-30 | Pavement | Design | RECONSTRUCTION(O) | 9 | FLEMING | The Contractor requested the use of untreated drainage blanket in lieu of asphalt treated drainage blanket because phase construction with the treated blanket was causing severe tracking of Primer L. | It was agreed to utilize the untreated drainage blanket because of the cost savings ($96 , 000) with no decrease in pavement design. It was further agreed to use the untreated drainage blanket in areas where it will not longitudinally abut asphalt treate
2008-10-30 | Design | Omission | NEW ROUTE(O) | 9 | LEWIS | Contract plans included constructing 4 curb to barrier wall transitions , however no quantity was established. | Bit item Curb to Barrier Wall Transition was added to contract with change order.
2008-10-30 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 9 | FLEMING | It was desired to provide motorists entering downtown Louisville via I-65 Northbound with information regarding possible traffic congestion due to Kentucky Derby Festival activities along the river front. | The Variable Message Board was relocated from I-64 eastbound to Northbound I-65 at the St. Catherine Street exit.
2008-10-30 | Construction | Evaluations | RECONSTRUCTION(O) | 9 | FLEMING | A procedure for the field evaluation of maximum density and optimum moisture content involves the use of a one point field compaction test and of a family of moisture density curves. This procedure was requested by the Contractor. | The equipment used to perform the density tests was purchased from Soiltest and then delivered to the department for future use.
2008-10-30 | Drainage | Pipe Sizing | RECONSTRUCTION(O) | 9 | FLEMING | The plans indicated a Manhole Type B at Sta 12+04 Rt. Ramp 8 and Sta 14+60 Rt Ramp 8. The Standard Drawing RDM-005-02 indicated a maximum intercepting pipe of 27 inches. However , the intercepted pipe size at the above locations was 42 inches thus exce | A Manhole Type C was constructed at the aforementioned locations as shown by Standard Drawing RDM-010-03.
2008-10-30 | Design | Grade | RECONSTRUCTION(O) | 9 | FLEMING | The bituminous wedge curb was unworkable due to the super elevated section. This area was located in the area of a detention basin. | It was agreed to eliminate the wedge curb. A four inch standard integral curb was constructed in its place.
2008-10-16 | Design | Omission | SAFETY(P) | 8 | PULASKI | The primary entrance for the Black Oak Industrial Park located at Sta. 1852+00 was omitted from the plans. The original entrance was constructed after design work , but well before construction commenced. | The grade at the existing entrance was different than the new alignment at KY 8. Therefore , enough of the entrance was removed and rebuilt to match the new alignment. Entrance construction was performed using Cost Plus.
2008-10-16 | Structures | Quantities | RECONSTRUCTION(O) | 8 | ADAIR | Concrete Class A and Steel Reinforcement quantities (per plan summary for each structure) were correct; however , the bid quantities per contract were incorrect. | Quantities were overrun and change order was executed to adjust bid item quantities.
2008-10-16 | Geotechnical | Piling/Drilled Shaft | RECONSTRUCTION(O) | 8 | ADAIR | Special Provision 69 required rock pile core material on the project. However , the plans did not include a quantity for this application. | Contractor made a request to use crushed limestone (#2 aggregate) in the pile core of the bridge rather than clay core. The bid item was adjusted via change order.
2008-10-16 | Construction | Ride Quality | RECONSTRUCTION(O) | 8 | ADAIR | There were concerns about potential pavement segregation on the project. | A Change Order compensated the Contractor at state average unit bid prices for utilizing a MTV for asphalt placement. By using a MTV aggregate with thermal , segregation will be decreased , thus enhancing the overall project.
2008-10-16 | Geotechnical | Soils | SAFETY(P) | 8 | PULASKI | A silty sand soil was encountered from Sta. 100+00 to Sta. 111+00. | Based upon a recommendation from the Geotechnical Branch , the area was undercut to a depth of 3 feet and refilled with shot rock from the project. Perforated pipe was installed to drain water from the undercut areas to ditches outside of the cut area.
2008-10-16 | Erosion Control Plan | Slope Protection | SAFETY(P) | 8 | PULASKI | A cut slope on the project was approximately 1.5:1. Erosion Control Blanket was needed in order to stabilize the soil and control erosion until vegetation could be established. | Erosion Control Blanket was used in addition to Type 3 Seed mix on the cut slope.
2008-10-16 | Erosion Control Plan | Seeding | SAFETY(P) | 8 | PULASKI | The plan quantity of Seeding and Protection was inadequate to complete the project. | Quantities for this item was adjusted via change order. It was estimated nearly 250 , 000 yards of seeding were needed.
2008-10-16 | Design | Omission | RECONSTRUCTION(O) | 8 | ADAIR | The contract included Type 2 Rural and Municipal R/W Markers. However , Type 1 were needed for this project as directed by current standard drawings. | Bid items were added.
2008-10-16 | Geotechnical | Settlement | RECONSTRUCTION(O) | 8 | ADAIR | The Contractor was originally instructed to install settlement platforms and order the items accordingly. However , they were instructed not to use them after they had been delivered to the site. | The Contractor was reimbursed for restocking and freight.
2008-10-16 | Maintenance of Traffic | Diversions | RECONSTRUCTION(O) | 8 | ADAIR | A temporary diversion was needed to accommodate traffic during the part-width construction of a double box culvert at Sta. 506+260. Original MOT Plans did not provide adequate taper lengths to safely transition traffic around the construction area. | District 9 Design provided a MOT plan revision for the revised diversion.
2008-10-16 | Traffic | Markings | SAFETY(P) | 8 | PULASKI | Arrow and Stop Bar thermo markings could not be used to open the roadway for during the winter due to weather conditions. | Arrows and Stop Bars were painted and then replaced by thermo markings once the weather permitted. The temporary markings were just used to open the roadway during the winter.
2008-10-16 | Drainage | Flooding | SAFETY(P) | 8 | PULASKI | The construction of KY 3020 fill slopes forced an increased amount of water into the adjacent ditches and roadway of Sand Branch causing overflowing and washing away of the roadway. | A section of Sand Branch Road was elevated and rebuilt to eliminate overtopping and future potential washout. Work was performed using Cost Plus.
2008-10-16 | Pavement | Seeping | RECONSTRUCTION(O) | 8 | ADAIR | Subsurface drainage led to a problem involving water seepage through the asphalt pavement. | Perforated pipe was placed to drain the water outside the shoulder area. The Contractor was compensated using Cost Plus.
2008-10-16 | Structures | Masonry Coating | RECONSTRUCTION(O) | 8 | ADAIR | Masonry coating was needed for the front face of pier stems on the bridges over Flat Run and Peck's Ridge Roads per Standard Specifications. | The bid item was adjusted per change order.
2008-10-16 | Structures | Plans | RECONSTRUCTION(O) | 8 | ADAIR | An old abutment not in use with the existing bridge was in conflict with the construction activity of the new bridge at Rt. Sta. 508+100. | Old bridge abutment was removed and bid item added.
2008-10-16 | Geotechnical | Unsuitable Material | SAFETY(P) | 8 | PULASKI | Unsuitable material was encountered from Station 1862+50 to Station 1872+90 (LT) on KY 8. | Additional undercutting was performed.
2008-10-16 | Maintenance of Traffic | Striping | RECONSTRUCTION(O) | 8 | ADAIR | Temporary striping tape was needed for Fleming Creek Bridge due to partial width construction. Also , temporary pavement markers were necessary on the Bridge to provide delineation as temporary tape would not hold during winter conditions. | Bid items were added/adjusted via change order. Temporary paint could not be used for this application because its complete removal could damage the bridge deck.
2008-10-16 | Design | Omission | RECONSTRUCTION(O) | 8 | ADAIR | There were concerns about a lack of a smooth transition between the new pavement and existing pavement. | A bid item for an Edge key was established.
2008-10-16 | Drainage | Ponding | RECONSTRUCTION(O) | 8 | ADAIR | Water was ponding on an adjacent property owner's yard. | A French drain was installed to drain the water to the roadway ditch.
2008-10-16 | Traffic | Markings | SAFETY(P) | 8 | PULASKI | The contract called for the placement of pavement markings including arrows , stop bars , and words to be completed by the Department. However , state forces were unable to perform the work in coordination with opening the road to traffic. | Pavement markings were added to contract and the contractor performed work upon our request.
2008-10-16 | Geotechnical | Slides | SAFETY(P) | 8 | PULASKI | Small slides were identified from Lt. Sta. 104+00 to Sta. 105+59. | Additional Roadway Excavation was needed to complete the repairs.
2008-10-16 | Drainage | Headwalls | RECONSTRUCTION(O) | 8 | ADAIR | Modification to 900 mm Culvert Pipe at 508+514 was needed to improve tie-in conditions for next section of KY 11 N towards Flemingsburg. Current plans called for a Sloped & Flared Box Inlet-Outlet on the inlet of the culvert. However , this would have | It was decided that a MES would be a more cost effective solution and easier to remove on the next section of KY 11. A junction box was utilized at this location as well to allow for a more efficient tie-in when the culvert was extended on the next secti
2008-10-16 | Maintenance of Traffic | Entrances | RECONSTRUCTION(O) | 8 | ADAIR | The original contract quantity of Traffic Bound Base was insufficient for maintaining entrances. | Bid item quantities were adjusted via change order.
2008-10-16 | Design | Phasing | RECONSTRUCTION(O) | 8 | ADAIR | Additional items were needed on this contract due to project phasing and maintenance of traffic. The project contained temporary widening and detours to maintain traffic. However , once the proposed roadway was constructed , the widened sections and d | Asphalt Milling and Texturing was added to remove the associated asphalt and to correct cross-slopes where permanent pavement was placed as part of a detour but was installed on a slope that was different than the planned slope to provide a safer temporar
2008-10-16 | Design | Quantities | RECONSTRUCTION(O) | 8 | ADAIR | An entrance right of station 502+780 that required 15 , 720 cubic meters of roadway excavation was not included in the original bid quantity. The quantity was reflected on the cross sections but not added in the total. Also , an additional 35 , 692 cub | Additional Roadway Excavation was requested via change order.
2008-10-16 | Right-of-Way | CAP | RECONSTRUCTION(O) | 8 | ADAIR | Waterline relocation was requested by a property owner to address an unresolved problem during ROW negotiations. | Appropriate bid items were added to the contract via change order.
2008-10-16 | Design | Safety | RECONSTRUCTION(O) | 8 | ADAIR | A safety issue was identified from Station 505+780 to Station 505+960. This area contained a 2:1 cut slope that was nearly 10 meters deep in some places. Additionally , the top of cut was only a few meters from the adjacent property owner's storage bui | A chain link fence was installed along the top of cut as a safety precaution.
2008-10-16 | Pavement | Coordination | RECONSTRUCTION(O) | 8 | ADAIR | This project called for a 19.0mm asphalt base mix even though an adjacent project was using a 25.0mm asphalt base mix and was scheduled to be completed concurrently. | The Contractor requested changing base mix from 19.0mm to 25.0mm to match the adjacent project. This resolved production and placement issues and provided a more structurally sound base material at no additional cost.
2008-10-16 | Drainage | Flooding | SAFETY(P) | 8 | PULASKI | There were drainage issues at the entrances located at STA 69+50 LT and RT. These entrances were placed at the end of the cuts on both sides of the roadway. Each one received a cross drain that could not handle the water or eroded material from the cuts | Right-of-Way had to be purchased from the property owner (Parcel 4) in order to permanently remove the pipes , pavement , and entrances. Additionally , the ditches were rebuilt and lined with Class 3 channel lining and locked with concrete. A constru
2008-10-16 | Erosion Control Plan | Quantities | SAFETY(P) | 8 | PULASKI | Additional silt traps were needed to control the erosion on the project. | Quantity was adjusted via change order.
2008-10-16 | Structures | Reinforcement Steel | RECONSTRUCTION(O) | 8 | ADAIR | Quantities for Epoxy-Coated Steel Reinforcement were incorrectly established in the contract as 134 , 035 kg , when the plan quantity was 131 , 831 kg. The plan quantity for steel in the deck slab of the Flat Run Creek bridge was 7346.2 kg in excess of | Steel quantities were adjusted as needed. Since the Contractor had already received the material for the Flat Run Creek bridge , he was reimbursed invoice price for that portion.
2008-10-16 | Erosion Control Plan | Slope Protection | SAFETY(P) | 8 | PULASKI | Due to the sandy nature of the material on the project , several slopes were unstable and highly erodible. | In order to stabilize the slopes and promote vegetative growth , placement of 8 Silt Soxx (synthetic water break with enclosed compost) along the center of the sand slope located at Rt. Sta. 105+00 was needed. Also , 502 cubic yards of compost material
2008-10-16 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 8 | ADAIR | Due to the proximity of the existing roadway to proposed roadway from station 500+380 to 501+400 , a fully proposed typical could not be constructed until the existing roadway was removed. | A Change Order provided for full depth shoulder pavement on the southbound shoulder because the p\proposed northbound lane could not be completed. The plans did not provide this quantity.
2008-10-16 | Design | Guardrail | RECONSTRUCTION(O) | 8 | ADAIR | End treatments were needed for temporary guardrail installation. | Type 7 Modified End Treatments were added via Change Order.
2008-10-16 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 8 | ADAIR | Type III Barricades were omitted from the original contract bid items. | Type III Barricades were required for proper road closure and were added with change order.
2008-10-16 | Design | Guardrail | RECONSTRUCTION(O) | 8 | ADAIR | End treatments were needed for temporary guardrail installation. | Type 7 Modified End Treatments were added via Change Order.
2008-09-25 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The Louisville Water Company left a pressure reducing station connected to the 8 waterline crossing Westport Road at Lyndon Lane. | As this station was within the construction limits of the project , Louisville Water Company requested the Contractor disconnect and remove this station and tie the 8 line into the new 16 main. This work was paid for by Louisville Water Company.
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | An insufficient bid quantity was established for the contract item Law Enforcement Officer. | Bid item quantity was increased.
2008-09-25 | Utilities | Delays | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The Department acquired a parcel of land between the Watterson Expressway and Parcel 13. This parcel was obtained from the Louisville Water Company , and was the location of the former Pump House for the adjacent Water Tower. As part of the ROW agreeme | In order to continue the project and eliminate any possible delays , the Department agreed to allow the Contractor to do the demolition work.
2008-09-25 | Design | Special Note | SAFETY(P) | 10 | OWSLEY | Special Note for Blasting on plan sheet R2H was determined to be inadequate. | Special Note for Blasting was amended to allow blasting from 9:00 AM to 3:30 PM , and with written approval from the engineer , during daylight hours after 6:00 PM.
2008-09-25 | Design | Coordination | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Plans for the project required the installation of a 54 Storm Sewer beneath the Watterson Expressway as an outlet to the Detention Basin. The middle portion (210 feet) was in a steel encasement pipe , but the remaining pipe had to be direct buried on ei | To eliminate the need to remove and reinstall the pipe in the future , it was agreed upon to pay the Contractor to install Class 5 pipe in preparation for the future ramp construction.
2008-09-25 | Utilities | New Utilities | SAFETY(P) | 10 | OWSLEY | Project development team recognized the need for water service for the future tunnel. | A 24 steel encasement pipe was constructed with this project to facilitate future Louisville Water Company services.
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | It was determined that additional quantities of the Variable Message Sign-Port 3 line were needed to properly advise motorists of changed roadway conditions as they approached the work site. | Bid item quantity was increased.
2008-09-25 | Utilities | Relocation | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | LG&E relocated a gas line near 48 inch waterline. The initial cost was to establish money to pay for work completed by LG&E. Final invoice determined actual cost. | A Bid Item was established.
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The proposed document had set up a quantity of 6 , 940 linear feet for Pavement Joint Adhesive. Per the Special Note for Longitudinal Pavement Joint Adhesive , the Contractor was required to apply the adhesive to the face of longitudinal joints between | Bid item quantity was increased by 192 , 000 linear feet.
2008-09-25 | Design | Safety | SAFETY(P) | 10 | OWSLEY | An improvement in sight distance along the US 42 corridor was desirable to increase safety due to proximity of overhead electric utilities. | During construction , the rock cut between Sta. 39+50 to Sta. 39+75 was revised to remove additional material and thereby increasing sight distance. Approval was granted from the Geotechnical Branch based on the quality of the limestone cut. The revisi
2008-09-25 | Utilities | Quantities | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Plan quantities for utility items were insufficient for the necessary installations. | Quantities were adjusted per change order. All quantities were verified on-site with the Louisville Water Company.
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The current standard as interpreted by the Department requires that wooden spacer blocks be installed in place of the existing metal spacer blocks. This is outlined in DESIGN MEMORANDUM NO. 10-98. | A review of the project showed 175 metal spacer blocks needed to be replaced with the wooden spacer blocks.
2008-09-25 | Design | Phasing | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Plans for this project required the Contractor to install an initial lift of base material onto which the Standard Curb and Gutter would be installed , which would be difficult due to phasing and the confines of the work area. | Due to phasing and confined work area , it was agreed to allow the Contractor to remove the initial lift and thicken the curb and gutter section accordingly. Payment of the item Standard Curb and Gutter Modified paid the Contractor for the additional co
2008-09-25 | Drainage | Error | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The storm sewer pipe quantities on this project were calculated from center of box to center of box. The actual quantity of pipe needed should have been measured from edge of structure to edge of structure. Because these calculation errors were not real | Since this pipe was ordered specifically for the project , the Department agreed to pay the invoice price for these items and have them delivered to Middletown Maintenance for use by the Division of Operations.
2008-09-25 | Design | Plans | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Cross-sections provided in the contract documents for the Westbound Widening were not consistent with site conditions. The area consisted of a vertical curve as well as four drainage structures. | The Department agreed with the Contractor that new cross-sections and staking were required to fit the desired widening at the prescribed location. The roadside slopes were all changed due to horizontal differences. Four proposed guardrail Type 3 End T
2008-09-25 | Construction | Specifications | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The contract bid documents required that the diamond grinding was to achieve a 63 or less , IRI test result. The current standard , as interpreted by the Department was that if the desired IRI was not reached , the Department could accept the work at | The Department accepted the unit price bid proposal. It was therefore agreed upon to accept the diamond grinding of the JPC (PCC) at the reduced unit bid price of $2.49 I square yard.
2008-09-25 | Drainage | Temporary Drainage | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | As part of the Westport Road Expansion Project , the Department installed an interchange at I-264 and Westport Road. The Department agreed with the Contractor to place waste material from this project along the slopes of I-264 for use on the future int | It was agreed to create the Supplemental Item Culvert Pipe 15 Inch - CL V. It was further agreed upon that payment of the Supplemental Item was to be fully compensated for all materials , equipment , and labor needed to complete this needed pipe extens
2008-09-25 | Maintenance of Traffic | Striping | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The operations performed to place temporary striping consisting of either paint or tape were time consuming. The time taken to install the paint or tape delayed other Contractor operations. Placement of weekend traffic control resulted in large delays | Leaving temporary striping in place allowed reduction of further delays. The Contractor was directed to place the barrels with consistent spacing and in uniform alignment with respect to 6 inches from the edge lines.
2008-09-25 | Utilities | Delays | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | A claim was brought by the Contractor resulting from the delays associated with last minute design changes to the waterline and elevation conflicts with LG&E gas and BellSouth Telephone Conduits. | The District 5 Construction Engineer , in addition to the Resident Engineer , reviewed and calculated the costs associated with the Claim from the Contractor. The revised Claim of $288 , 203.64 was accepted by the Cabinet and the Central Office concurr
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The project allowed for speed limit reduction during all working hours. Law enforcement was only provided for bridge work (weekends) , ramp closures during paving , JPC replacement (weekends) , and operation with only a single lane open to traffic. H | KVE was given the work hour information and was unable to provide officers to cover the additional work hours. The Department compensated the Contractor for 50% of the hours used for law enforcement based on invoices provided.
2008-09-25 | Construction | Revisions | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | A modification was made to allow a 16 inch water main to be installed over 48 inch transmission main. This was credited because not as much rock was encountered with the change. | A Bid Item was established.
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The contract bid documents required the existing pavement edge elevations to have equal to or less than one inch drop-off as part of the original work. There were existing entrance and exit ramps that had outside shoulder drop-offs that exceeded the allow | It was agreed to complete this work as appropriate for the specific site conditions. It was further agreed that payment for the supplemental item Shouldering shall be full compensation for all equipment , labor and materials necessary to complete this
2008-09-25 | Design | Plans | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The cross-sections in the contract documents for the Westbound Widening were not consistent with the site conditions. The area consisted of a vertical curve as well as 3 drainage structures. Relocation of the median flow line was required due to the cha | The Department agreed with the Contractor that new cross-sections and staking were required to fit the desired widening at the prescribed location. The Department agreed to reimburse the Contractor for costs accrued to perform the additional design work
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Construction of an additional lane and shoulder adjacent to the existing asphalt pavement westbound between M.P. 18.428 to 19.187 was deemed necessary. | Removal of thirty-one inches of extra material was required.
2008-09-25 | Erosion Control Plan | Quantities | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The 2004 Standard Specifications required that an Erosion Control Blanket be installed in all non-rock lined Flat Bottom Ditches. | The Bid Item plan quantity for Erosion Control Blanket was adjusted.
2008-09-25 | Utilities | Inaccurate Location | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The existing sanitary sewer between Lt. Sta. 107+00 and 110+50 was in conflict with the new 42 storm sewer , which was contrary to the pre-project utility survey. | To install the new storm sewer , the existing live sanitary sewer had to be relocated north and reconnected to the existing system. Due to the existence of multiple utilities , including fiber optic conduits and high pressure gas , much of the excavat
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The quantities for Pave Striping- Temporary Removable Tape- W , Pave Striping- Temporary Removable Tape- Y , Pave Striping- Temporary Removable Tape- B were insufficient for the project. The traffic control was not sufficient to perform the work and n | It was necessary to compensate the Contractor for increased work. It was further agreed upon that the cost would be determined by the unit bid price per each item respectively. In addition , it was agreed that payment for each item shall be considered as
2008-09-25 | Design | Relocation | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Existing guardrail had to be removed and reset. During the process , the guardrail alignment had to be changed , which included end treatments. The guardrail and existing roadway lighting conduit were in conflict. | The Contractor had to relocate the required lengths of conduit and wire to allow the existing lighting circuits to remain active and working for the traveling public.
2008-09-25 | Drainage | Omission | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The plans required that the existing drainage ditches along the south side of the project be filled as part of the widening of the new roadway. However , since the new roadway was higher than the surrounding parcel , water would have drained from the y | A DBI Type 15 Modified was installed at Washburn , Fountain , and Finley to allow the water to drain into the new storm water system.
2008-09-25 | Construction | Ride Quality | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The project had existing abandoned traffic loops at westbound station 508+00. The traffic loop encapsulant utilized with the loops was some form of silicone. The actual encapsulant and how deep it was placed was not noticed during the night milling oper | Removal of all encapsulant , as well as removal and replacement of the Stone Matrix Asphalt (Exp) at the location was required for the longevity of the surface.
2008-09-25 | Design | Waste Areas | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | All waste material on project was placed on the slopes of the existing embankment of I-264 , south of Westport Road. In order to complete this work , the Contractor was required to clear and grub all lands within the boundaries of the existing Right-of | In order to compensate the Contractor for this additional work , it was agreed upon to create the Supplemental Item Clearing and Grubbing - Ramps. The Contractor benched the existing slopes of I-264 , relocated a portion of the Right-of-Way fencing ,
2008-09-25 | Design | Plans | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | During the clearing and grubbing operations for the project , a structure that had been demolished and buried near Rt. Sta. 80+00 was found in the center of what was to be the Detention Basin. Section 203 of the Standard Specifications states that the C | As this debris/structure was not called out on the plans , and was not easily recognizable to the Contractor , the Department agreed to split the cost of disposal for this material with the Contractor. In order to compensate the Contractor for the exca
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Section 701.03.06 of the Standard Specification Book requires that when backfill material is dissimilar from the surrounding materials , all backfill material must be wrapped in Geotextile Fabric Type IV. Section 701.05 specifies that if this item was n | Therefore , to allow for this specification to be met , it was agreed upon to create the Supplemental Item Geotextile Fabric Type IV - Pipe. It was also agreed upon that payment of this Supplemental Item would be fully compensated for all materials ,
2008-09-25 | Drainage | Curb Box Inlets | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Plans for this project required installation of CBI Type A throughout the project. On the north side of the project , two structures near Herr Lane required modifications due to limited cover. The use of standard CBI Type A could not be allowed for any | The bases and tops were modified by the precaster to alleviate the problem.
2008-09-25 | Construction | Ride Quality | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The contract bid documents required that the Stone Matrix Asphalt (Exp) being placed had to achieve a 76 or less IRI test result. The current standard as interpreted by the Department is that if the desired IRI is not reached , the Department can accept | Bid item Ride Quality Adjustment Asphalt was added to the project.
2008-09-25 | Traffic | Omission | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | As part of the Westport Road Expansion Project , the Department installed an interchange at I-264 and Westport Road. Because of this interchange , a Traffic Surveillance Camera would later be installed and integrated into the TRIMARC system. After sig | In order to install the camera it was necessary to create the Supplemental Items Pole Base-High Mast , Pole-80' with Lowering Device , Camera Interface Box , Dome PTZ Camera , CCTV Control Cable , Surge Suppression Device Type Ill , Enclosure Model
2008-09-25 | Design | Guardrail | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Guardrail end treatments were changed on the project resulting in relocation of the required recovery zones. | Twelve-hundred linear feet of 18 Culvert pipe was removed from the contract. It was necessary to compensate the Contractor for handling the culvert pipe. It was agreed upon that payment for the supplemental Culvert Pipe - 18 inch Restocking would be con
2008-09-25 | Design | Guardrail | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The contract bid documents required a double-faced guardrail to be placed in the center median between M.P. 18.428 to 19.187. The actual elevations and offsets of the proposed median did not allow for sufficient drainage while allowing correct placement | The proposed double-faced guardrail was changed to two separate lines of single-faced guardrail which were placed adjacent to the west and eastbound lanes respectively. This relocation required the Contractor to place approximately twenty-two guardrail p
2008-09-25 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The quantities for Random Crack Seal were insufficient for the project. The on-site conditions of the JPC (PCC) warranted a substantial increase in quantities. | Bid item quantity was increased.
2008-09-25 | Design | Guardrail | SAFETY-HAZARD ELIM(P) | 10 | PERRY | The contract bid documents required a double-faced guardrail to be placed in the center median between M.P. 18.428 to 19.187. The actual elevations and offsets of the proposed median did not allow for sufficient drainage while allowing correct placement | The proposed double-faced guardrail was changed to two separate lines of single-faced guardrail which were placed adjacent to the west and eastbound lanes respectively. This relocation required the Contractor to place approximately twenty-two guardrail p
2008-09-25 | Design | Guardrail | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Guardrail end treatments were changed on the project resulting in relocation of the required recovery zones. | Twelve-hundred linear feet of 18 Culvert pipe was removed from the contract. It was necessary to compensate the Contractor for handling the culvert pipe. It was agreed upon that payment for the supplemental Culvert Pipe - 18 inch Restocking would be con
2008-09-25 | Design | Special Note | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The plans for this project required the use of the MTV while placing all asphalt mixtures. Due to the multiple phases of construction , it was agreed that the MTV would be difficult to use during placement of the Asphalt Base. | It was agreed upon to eliminate the requirement for the use of the MTV for Asphalt Base and instead , only require it for the installation of the Asphalt Surface on the project.
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | PERRY | It was determined that ditching was needed on the project to address several clogged pipes and ditches. | Supplemental item Ditching Special/EB I-64 at Rt. Sta. 251+00 (+/-) to Rt. Sta. 254+00 was established by change order.
2008-09-25 | Construction | Delays | SAFETY(P) | 10 | OWSLEY | An unseasonably amount of rainfall occurred during the lifespan of the project , resulting in multiple non-working days for the contractor. | One hundred twenty-two days were added to the project completion date.
2008-09-25 | Design | Intersection | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | After the project was completed , the Department received numerous complaints concerning the proximity of the end of the western median on Mainline Westport to the intersection of Washburn. | To alleviate the concerns of the traveling public and make the intersection more user friendly , it was agreed to pay the Contractor to remove the first 15 feet of the median. Once this was removed , 5 feet had to be reinstalled with the proper nose ,
2008-09-25 | Design | Plans | SAFETY-HAZARD ELIM(P) | 10 | PERRY | Station numbers were inverted , in the opposite direction , and on the opposite side of the road. | This error should have been caught by a more thorough quality control check of the plans.
2008-09-25 | Utilities | Existing Utilities | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | After work commenced on the project , gas lines crossing mainline Westport at Herr Lane were found to be too high for the installation of the storm drainage. | In order to complete the project , it was agreed upon to reimburse LG&E for the cost of lowering and relocating the gas lines in conflict.
2008-09-25 | Design | Omission | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | No consideration was given to pedestrian traffic having to stand in mud , rain , etc. during construction of the project. | In urban settings such as this with significant pedestrian traffic , proper accommodations should be considered during the design process.
2008-09-25 | Design | Phasing | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | The plans for this project required the Contractor reconstruct the intersection of Westport Road and Herr Lane in multiple phases. After construction began , and Phase One was complete , it was realized that the mainline pavement was 5 feet lower than | In order to keep traffic flowing , the Contractor lowered the northern half of the intersection the same day traffic was shifted to the new mainline pavement on the south side of the project. It was agreed upon to pay the Contractor to work over that Fr
2008-09-25 | Erosion Control Plan | Quantities | SAFETY-HAZARD ELIM(P) | 10 | MAGOFFIN | Temporary Seeding was needed for future phases. | A Bid Item was added so Temporary Seeding could be stockpiled for future phases.
2008-06-27 | Design | Safety | PAVEMENT REHAB-INT(P) | 1 | TRIGG | The finished side slopes of the shoulders actually encroached upon the pedestals of the light posts creating a safety hazard since no guardrail was placed in front of them. In the event of a collision with the light post the unit would not have the break | The lighting on pavement rehabilitation jobs needs to be given more consideration during the design phase.
2008-06-27 | Design | Shoulders | PAVEMENT REHAB-INT(P) | 1 | TRIGG | There were concerns about how shoulders were being constructed on high volume roadways and the impact it has on detours and future projects. | Shoulders should be constructed the same as the mainline to expedite construction on high volume roadways. Full depth shoulders could be used for detours or for widening jobs in the future.
2008-06-27 | Design | Adjacent Projects | PAVEMENT REHAB-INT(P) | 1 | TRIGG | Issues involving the construction segment scheduling and phasing when developing highway plans were discussed. | The discussion included the importance of pre-planning the phasing of segments so that certain materials from one end of the job can be utilized at another location of the project without delays or extra costs. These items need to be looked at prior to a
2008-06-27 | Drainage | Edge Drains | PAVEMENT REHAB-INT(P) | 1 | TRIGG | There were concerns about edge drain inspection. | Edge drains should be camera inspected before acceptance.
2008-06-27 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 1 | TRIGG | Additional items were needed to facilitate drainage of the existing ditches. | A Change Order provided additional pipes and drop boxes needed to facilitate drainage of the existing ditches.
2008-06-27 | Design | Omission | PAVEMENT REHAB-INT(P) | 1 | TRIGG | Cut slopes and benches had to be cleaned. | A Change Order was issued for cleaning the cut slopes and benches.
2008-06-27 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 1 | TRIGG | There were concerns about the type of guardrail end treatments set up on this project and their impacts upon drainage structures. | Guardrail end treatments were changed from Type 3 to Type 1 , which resulted in the elimination of additional pipes and drainage boxes.
2008-06-27 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 1 | TRIGG | There were concerns about the type of guardrail end treatments set up on this project and their impacts upon drainage structures. | Guardrail end treatments were changed from Type 3 to Type 1 , which resulted in the elimination of additional pipes and drainage boxes.
2008-06-27 | Design | Quantities | PAVEMENT REHAB-INT(P) | 1 | TRIGG | There was an overrun of the estimated shoulder pavement removal quantity. | A Change Order established additional quantities for shoulder pavement removal.
2008-06-27 | Drainage | Headwalls | PAVEMENT REHAB-INT(P) | 1 | TRIGG | The double wall non-perforated pipe is not withstanding impact from maintenance equipment. | Adequate pipe end structures need to be used at ends of edge drain outlets.
2008-06-27 | Traffic | Lighting | PAVEMENT REHAB-INT(P) | 1 | TRIGG | A note on the original plans specified that the existing lighting would not be disturbed. However , washing and erosion of the existing earth slopes had left most of the existing conduit exposed and deteriorated. Due to construction and excavation of g | The lighting on pavement rehabilitation jobs needs to be given more consideration during the design phase. A Change Order was issued to pay for the additional work required to address the existing lighting conditions.
2008-06-27 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-INT(P) | 1 | TRIGG | The original pavement rehabilitation was set up in two sections with traffic control designed to maintain eastbound traffic on eastbound lanes and westbound traffic on westbound lanes , which restricted the work area to the interior median. | A VECP for a new maintenance of traffic scheme was submitted. The Contractors proposal treated the project as one section and allowing existing traffic to be transitioned to one side to create a larger work area. This method provided easier access for c
2008-06-27 | Design | Intersection | PAVEMENT REHAB-INT(P) | 1 | TRIGG | An upgrade of the existing I-275/KY 16 interchange was necessary to handle a large increase in traffic volume anticipated due to development in the area. However , this need was not considered in the initial rehabilitation project. | Turning lanes were added and the median between Stations 27+00 and 74+00 of KY 16 was removed by Change Order.
2008-05-29 | Environmental | Contaminated Material | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | Two contaminated sites were scheduled for remediation on this project; however , during construction the extent of contamination was greater than anticipated. | Follow up discussions with the Division of Environmental Analysis indicated that they had changed procedures to improve the evaluation of sites and lessen the possibility of these situations from occurring. In this case , extensive soil removal and repl
2008-05-29 | Right-of-Way | Coordination | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | Right-of-Way was not cleared before construction commenced. In one instance on this project the appropriate papers had not been filed , which created a difficult situation for the Resident Engineer who had to deal with the property owner. Also environm | Right of Entry was obtained before a Change Order for remediation could be issued.
2008-05-29 | Design | Evaluations | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | A basement was much larger than indicated on the plans. It extended well past the exterior walls of the building , which was not apparent from a visual inspection of the site. | A Change Order was issued to provide for the extra work necessary to demolish and backfill said basement.
2008-05-29 | Design | Quantities | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | Plan quantities of gabion mattresses , curb box inlets , and manholes were inaccurate. | The Contractor was reimbursed invoiced price for unused items.
2008-05-29 | Structures | Quantities | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | There was an overrun of structure granular backfill. | A Change Order was established to add additional quantities in order to correct the overrun.
2008-05-29 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | This project was located on a tight site with two bridges being replaced at a busy intersection. Maintenance of traffic was critical due to a nearby high school and impacts upon local businesses. The plan proposed that traffic be maintained on the exist | Closer coordination and review by the roadway and bridge designers would have identified this issue and allowed the Department to plan and inform people of the necessary closures and detours. As a result , a six mile detour was necessary. Change Orders
2008-05-29 | Environmental | Underground Tank | PAVEMENT REHAB-PRK(P) | 2 | HOPKINS | Two underground storage tanks were discovered in the contaminated area. | A Change Order included items of work for removal and disposal of the tanks and installation of two monitoring wells.
2008-05-29 | Design | Quantities | MAJOR WIDENING(O) | 5 | JEFFERSON | Due to construction revisions and errors in plan quantities , the Crushed Stone Base , CL2 Asphalt Base 1.50D PG64-22 , Roadway Excavation , Crushed Stone Base Underrun Adjustment , CL2 Asphalt Base 1.50D PG64-22 Underrun Adjustment , and Roadway Ex | Fair and equitable unit prices were negotiated by Division of Construction staff and the Contractor , per KYTC Standard Specification 104.
2008-05-29 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 5 | JEFFERSON | Signs and barricades needed on the job were not set up in the plans. | These items were added via change order.
2008-05-29 | Maintenance of Traffic | Signage | MAJOR WIDENING(O) | 5 | JEFFERSON | Blasting zone signs were not included in the estimate. | Approximately 25 temporary signs were needed including: Blasting Zone , End Blasting Zone , and Turn Off 2-Way Radios.
2008-05-29 | Construction | Delays | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | There were fabrication and procurement delays associated with the pole base adapters. | There was an extension of thirty calendar days for all items in the contract except for the median wall lights which were extended seventy-one calendar days beyond the current completion date of November 20 , 2006.
2008-05-29 | Pavement | Repair | MAJOR WIDENING(O) | 5 | JEFFERSON | An Official Order was written to extend the project limits westward four miles to the intersection of Hal Rogers / Daniel Boone Parkway MP 0.00. This order was commissioned so that emergency pavement repairs could be performed on KY 30 in various areas w | Class 2 Asphalt Base 1.50D PG64-22 , Class 2 Asphalt Surface 0.38D PG64-22 , Pavement Marker Type V-BY , Mobilization for Milling and Texturing with Patching , Asphalt Pavement Milling and Texturing Associated with Additional Patching due to Mine Subs
2008-05-29 | Maintenance of Traffic | Striping | NEW ROUTE(O) | 5 | JEFFERSON | Blackout tape was not utilized on project due to improper adhesion in transition locations within the paving limits of the project. | A Bid Item for Pavement Striping Removal - 6 inch was established on project.
2008-05-29 | Design | Quantities | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Additional quantity of Mountable Median Type 6A was needed to construct the median as shown on roadway plans from Van Meter Road STA 60+30 to 65+40. | Bid items were adjusted per change order.
2008-05-29 | Drainage | Elevation | MAJOR WIDENING(O) | 5 | JEFFERSON | There was an elevation error in the Contract Plans. | The pipe at Station 31+20 had to be lengthened and the headwall reset due to the slope extending further than indicated in the plan set.
2008-05-29 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Quantities of Pave Striping Removal - 6 inch and Pave Striping - Temp Paint - 4 inch were insufficient to maintain traffic because of phasing changes on I-64 and Van Meter Road needed to complete construction. Due to the increased grade elevation and the | Additional quantities of Pave Striping Removal - 6 inch and Pave Striping - Temp Paint - 4 were added to contract.
2008-05-29 | Traffic | Coordination | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The plans called for the Department to furnish pole bands , but the eleven pole bands furnished by the Department were the wrong size. Additional electrical disconnect service and accessories not addressed in the plans were needed at the top of Ramp D b | A lump sum item for Traffic Signal Work was established , which included the following items: Furnishing and installing pole bands , Furnishing and installing additional electrical disconnect and service cable , and Furnishing and installing 5/8 inch
2008-05-29 | Design | Intersection | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The City of Winchester requested measures be taken to facilitate pedestrian traffic at the intersection of US 60 and Van Meter located at STA 66+60. | The Chief District Engineer approved this request on January 30 , 2006 and items for Sidewalk Ramp Type 1 , Pavement Marking - Thermo X-Walk - 6 inch , and Relocate Signs were added. The work included removal of a single pole sign located in the locat
2008-05-29 | Structures | Flowable Fill | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | There were concerns about potential settlement at the bridge ends. | Flowable fill was added at the bridge ends to minimize settlement.
2008-05-29 | Drainage | Ditches | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns about erosion at locations where drainage structures were enhanced by replacement or lining of pipe. Approximate locations include MP 108.4 , 108.51 , 108.65 , 108.76 , 109.6 , 113.335 , 113.485 , 114.097 , 114.324 , 114.533 | Existing paved ditches were replaced with Channel Lining Class II.
2008-05-29 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 5 | JEFFERSON | Diversions were set up in the contract , but none of the items associated with them were part of the contract. | Items were added via change order.
2008-05-29 | Construction | Revisions | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | An old building was removed to the current Right-of-Way line before project was let; however , construction of the retaining wall from STA LT 42+60 to 44+90 required removal of the entire building. This building was within the Department's constructio | The Department and Contractor reached an agreement on removal and disposal of building. The agreed upon price included both removal and disposal.
2008-05-29 | Pavement | Type | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The binder used in the proposal is no longer produced and/or approved by KYTC. Item reflects unit price reduction for Cabinet approved use of the special note for Unsealed JPC Pavement and Shoulder Joints for the 12' JPC Pavement on this project. | The contractor used the higher grade binder for base and surface mixes PG 76-22 in lieu of PG 70-22. Bid items were adjusted per change order.
2008-05-29 | Construction | Safety | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The plans called for the bridge to be striped with permanent paint. The bridge was striped with the paint as per specifications several times prior to the final inspection and was found to be unacceptable. The condition of the striping at the time of in | The paint striping was removed and durable tape was used to remedy this situation by ensuring the turning lanes and multiple through lanes remained clearly marked.
2008-05-29 | Traffic | Lighting | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The strain poles ordered by Central Office Division of Traffic were larger than those in the contract plans. Nine of the special order poles required assembly because they were delivered in two pieces as well as larger 48 foundations to accommodate the l | A supplemental price was required to compensate the Contract for the additional work associated with the larger strain poles. The supplemental price accounted only for the additional work; therefore , the original Install Strain Pole item was paid as we
2008-05-29 | Design | Omission | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The contractor furnished Quality Control acceptance for all cement concrete placed on the project. Quality Control was performed in accordance with the current issue of the Department's Standard Specifications. | A QC bid item was added.
2008-05-29 | Maintenance of Traffic | Safety | NEW ROUTE(O) | 5 | JEFFERSON | Contractor decided to use a Law Enforcement Officer to enhance traffic control and safety. | The Department agreed to pay 50% of the total invoice cost.
2008-05-29 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Areas for curb placement were designated on the plans , however , some areas were overlooked. During the final inspection , deep washes at the edge of the DGA shoulder were noticed. The most critical was near a traffic signal junction box (Van Meter | Asphalt Wedge Curb and Type 2 Flume Inlets were installed at these locations to prevent the washing. Guardrail had already been installed and had to be removed and reset for the placement of the curb. Channel Lining Class II was used to protect the slop
2008-05-29 | Design | Alignments | MAJOR WIDENING(O) | 5 | JEFFERSON | There were concerns about how the proposed alignment tied into the previous KY 30 project. | Adjustments in both the Horizontal and Vertical Alignments were made to the project through Construction Revision #1. The accepted revision resulted in an equivalent alignment that tied into the previous KY 30 project better. It also minimized the amoun
2008-05-29 | Construction | Rumble Strips | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Milled rumble strips were incidental to work directly on I-64 but not on the adjacent approaches. | A bid item for milled rumble strips on Van Meter , Rockwell , and Revilo Roads was added to the project.
2008-05-29 | Structures | Retaining Walls/MSE | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Future maintenance of reinforcing the straps behind the proposed MSE wall located at Van Meter Road LT STA 40+60 to 44+90 would not be possible due to location of the straps under pavement area of gas station. A permanent construction easement would have | It was decided to construct a gravity retaining wall instead of the MSE wall , which required additional quantities of Structure Excavation - Unclassified , Concrete - Class B , Structure Granular Backfill , and Concrete Barrier Wall Modified Retaini
2008-05-29 | Construction | Revisions | MAJOR WIDENING(O) | 5 | JEFFERSON | Due to the profile change from Construction Revision #1 the old roadway was left in place to minimize pavement removal , risk to traffic , and expedite the tie-in. | A couple of stations required asphalt milling and texturing to allow for base tie-in and cross slope correction.
2008-05-29 | Utilities | Relocation | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The proposed water line was designed over the existing water line , but a temporary line had to be installed so the old line could be removed. | Bid items were added to contract for 1 , 925 linear feet of 6-inch PVC water line in order to provide uninterrupted service for local businesses and continuous fire safety protection.
2008-05-29 | Design | Striping | NEW ROUTE(O) | 5 | JEFFERSON | The project included a latex overlay on the bridge over Cane Run Creek. No striping quantities for lane delineation were set up in the bid quantities. | Bid items Pavement Striping - Durable Type 1-6 inch W and Pavement Striping - Durable Type 1-6 inch Y were established via change order.
2008-05-29 | Design | Striping | NEW ROUTE(O) | 5 | JEFFERSON | The project included a latex overlay on the bridge over Cane Run Creek. No striping quantities for lane delineation were set up in the bid quantities. | Bid items Pavement Striping - Durable Type 1-6 inch W and Pavement Striping - Durable Type 1-6 inch Y were established via change order.
2008-05-29 | Maintenance of Traffic | Safety | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | There were safety concerns about traffic being exposed to 2:1 slopes during traffic phasing. | A temporary guardrail bid item was added.
2008-05-29 | Pavement | Type | NEW ROUTE(O) | 5 | JEFFERSON | The original plans called for using Concrete Overlay-Latex Rapid Set for the Cane Run Bridge deck. However , the construction phasing was such that the strength at six hours provided by the Rapid Set product was not needed. Traffic would not be using t | Concrete Overlay-Latex Rapid Set was changed to Concrete Overlay - Latex Type III.
2008-05-29 | Design | Quantities | NEW ROUTE(O) | 5 | JEFFERSON | The Plan Quantity for Contract Incentive Adjustments ($595 , 000) did not cover the actual quantity ($1 , 134 , 000). | Additional funding was required to fulfill Contract Incentive Adjustments: Paris Pike Ramp 8: Ten days - Five days x $39 , 000/day = $195 , 000. Paris Pike Ramp A: Ten days - Six days = Four days x $16 , 000/day = $64 , 000. Mainline: Sixty d
2008-05-29 | Design | Entrance | MAJOR WIDENING(O) | 5 | JEFFERSON | An approach on the adjacent KY 30 project , left of Station 20+50 , was constructed at the planned 22% grade. However , property owners on this approach requested the Department to reconstruct the approach at a less steep grade. | A supplemental item was established for full compensation for all labor , equipment , and materials necessary to mobilize , perform all clearing , staking , earthwork , relocate utilities if necessary , and provide traffic control necessary to reco
2008-05-29 | Structures | Masonry Coating | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Retaining walls are to be masonry coated in accordance with 601.03.18 of the 2004 Standard Specifications for Road and Bridge Construction. However , no item was set up for the gravity wall located at I-64 LT STA 1700+00 to 1703+19 or the wall at Van Me | Design quantities for masonry coating were adjusted via change order.
2008-05-29 | Design | Adjacent Projects | MAJOR WIDENING(O) | 5 | JEFFERSON | The Contractor was required to do additional work to expedite the future tie-in to the next section of the roadway on the west end of the project. | The Contractor was required to do clearing , staking , redressing slopes , and re-grading the subgrade. The roadway was built as specified for the full typical section over the last four-hundred feet of the project to allow the tie-in with the next se
2008-05-29 | Erosion Control Plan | Quantities | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The original quantity of Temp Seeding and Protection was estimated as 10% of the Seed and Protect quantity when the project was let. Additional quantity was needed to temporarily cover and protect all exposed areas from erosion. Clearing and grubbing | An additional quantity of Temp Seeding and Protection was added to contract.
2008-05-29 | Traffic | Lighting | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | Median lighting junction box brochures were designated and approved by the Department. After installation in the median barrier wall , however , the electrical inspection noted that these boxes had the drain in the incorrect location and directed that | Since the boxes installed by the Contractor were the ones approved by the Department , a bid item was added to compensate the Contractor for correcting the error. This item included work to ensure positive drainage in junction boxes by drilling first at
2008-05-29 | Traffic | Lighting | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The lighting base detail in the lighting plans for mounting 40 ft light poles on the median wall along the center line of I-64 showed a bolt pattern too small to mount the poles. | A special order adapter plate was required to accommodate the larger pole base bolt pattern and mount the light poles on the previously constructed median wall. Central Office Division of Traffic agreed these plates were necessary to mount the poles.
2008-05-29 | Structures | Phasing | NEW ROUTE(O) | 5 | JEFFERSON | Adequate space was not provided per plan to allow for appropriate scaffolding to repair Pier #1 of Bridge #3 on the inside shoulder of the I-75 SB 2-lane section. | The Contractor relocated Crash Cushion Type 9T and Temporary Concrete Barrier Median Wall to the inside shoulder through this area.
2008-05-29 | Design | Waste Areas | MAJOR WIDENING(O) | 5 | JEFFERSON | There was too much excavation set up , but not enough to pay for a waste area. | The Contractor was reimbursed for the excavation waste site area.
2008-05-29 | Construction | Coordination | PAVEMENT REHAB-INT(P) | 5 | JEFFERSON | The proposed MSE wall was delivered to the job prior to District Division of Design's decision to change the wall at Van Meter Road LT STA 42+60 to 44+90 to a gravity type wall. | The Contractor was reimbursed for the cost of delivering the MSE wall pieces and straps. The Department was required to remove the material from it's stockpiled location on the project.
2008-05-15 | Right-of-Way | Coordination | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | The right of way was cleared by the city to build a gravity retaining wall. However , the adjacent property owner had conflicts with the city on reimbursement. | A Change Order was issued due to the delay needed to resolve the issue with the property owner before construction of the retaining wall in front of adjacent property could resume.
2008-05-15 | Design | Omission | I-CHANGE RECONST(O) | 7 | CLARK | The original plans did not contain all items necessary to install a Crash Cushion Type IX-A. | Forty cubic yards of roadway excavation were added for the installation of the Crash Cushion Type IX-A.
2008-05-15 | Design | Omission | I-CHANGE RECONST(O) | 7 | CLARK | The original plans did not contain all items necessary to install a Crash Cushion Type IX-A. | Forty cubic yards of roadway excavation were added for the installation of the Crash Cushion Type IX-A.
2008-05-15 | Pavement | Quantities | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | There were insufficient quantities in the original plans to complete the paving portion of the project , because the entrances and ramps needed more paving quantities than anticipated. | An increase was approved in the plan quantity for paving entrances and ramps.
2008-05-15 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 7 | CLARK | Maintenance of traffic on the Pennyrile Parkway during the removal and replacement of barrier walls on the Western Kentucky Parkway bridge was not considered in the original estimate when flashing arrows were considered. | The flashing arrows were purchased new and became property of the department. Also included with this change order was removable striping tape for the above mentioned traffic scheme.
2008-05-15 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 7 | CLARK | Maintenance of traffic on the Pennyrile Parkway during the removal and replacement of barrier walls on the Western Kentucky Parkway bridge was not considered in the original estimate when flashing arrows were considered. | The flashing arrows were purchased new and became property of the department. Also included with this change order was removable striping tape for the above mentioned traffic scheme.
2008-05-15 | Design | Evaluations | I-CHANGE RECONST(O) | 7 | CLARK | Insufficient attention was given to evaluating scour and erosion conditions around existing edge drain outlets. | Designers need to pay increased attention when evaluating scour and erosion conditions around edge drain outlets.
2008-05-15 | Design | Entrance | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | The entrance grade for an existing parking lot at Sta. 46+31 was constructed based upon standard drawings , but vehicles could not maneuver the entrance without contact of the chassis. | The entrance at Sta. 46+31 on Corporate Drive was removed and replaced.
2008-05-15 | Design | Evaluations | I-CHANGE RECONST(O) | 7 | CLARK | Insufficient attention was given to evaluating scour and erosion conditions around existing edge drain outlets. | Designers need to pay increased attention when evaluating scour and erosion conditions around edge drain outlets.
2008-05-15 | Design | Entrance | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | When the entrance was modified , a small drop off was created next to an existing sidewalk. | A handrail was installed to meet ADA considerations.
2008-05-15 | Drainage | Edge Drains | I-CHANGE RECONST(O) | 7 | CLARK | Common edge drain problems were discussed. There seems to be a problem with soil fines migrating into the pipe at the snap joint locations. | There should be provisions that #57 or #9 stone be placed around the snap joint location to prohibit migration of fines into pipe network , which would allow for a long pipe life. Also , only round pipe should be used for edge drains; the fin pipe tend
2008-05-15 | Drainage | Edge Drains | I-CHANGE RECONST(O) | 7 | CLARK | Common edge drain problems were discussed. There seems to be a problem with soil fines migrating into the pipe at the snap joint locations. | There should be provisions that #57 or #9 stone be placed around the snap joint location to prohibit migration of fines into pipe network , which would allow for a long pipe life. Also , only round pipe should be used for edge drains; the fin pipe tend
2008-05-15 | Design | Special Note | I-CHANGE RECONST(O) | 7 | CLARK | There is a need to clarify all notes that may be present on plans. Some notes are being omitted while others are excessive. | Pavement rehabilitation jobs need to have more notes pertaining to the issues of the pavement rehab job itself. There needs to be better correspondence on pavement rehabilitation jobs.
2008-05-15 | Design | Special Note | I-CHANGE RECONST(O) | 7 | CLARK | There is a need to clarify all notes that may be present on plans. Some notes are being omitted while others are excessive. | Pavement rehabilitation jobs need to have more notes pertaining to the issues of the pavement rehab job itself. There needs to be better correspondence on pavement rehabilitation jobs.
2008-05-15 | Design | Quantities | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | There were overruns in plan quantities. | A Change Order was necessary to provide additional quantities for overruns in plan quantities.
2008-05-15 | Design | Median | I-CHANGE RECONST(O) | 7 | CLARK | The steepness of existing medians on the Western Kentucky Parkway allows water to migrate into the driving lanes thus causing rain or slick ice conditions. | Flattening slopes in the median of the Western Kentucky Parkway to 4:1 slopes , for example , was suggested.
2008-05-15 | Construction | Contracts | I-CHANGE RECONST(O) | 7 | CLARK | The time frame for letting pavement rehabilitation projects tends to cause problems with the overlaying of bridge decks and maintenance of traffic. When pavement rehab jobs are let near the winter season , the bridge deck overlay has to be modified or d | When establishing a time frame for letting pavement rehabilitation projects that involve overlaying of bridge decks , consideration should be given to avoiding proximity to the winter season due to the issues it causes.
2008-05-15 | Design | Communication | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | Construction personnel are not aware of design exemptions until a correction is needed. | It was requested that Construction personnel obtain a copy of the Design Executive Summary and Line and Grade Inspection report.
2008-05-15 | Design | Special Note | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | A special note in the proposal required sealing joints and cracks in the concrete pavement but did not include a method of payment. | A change order was issued for the cost of sealing the existing pavement before overlaying with asphalt , which had to be negotiated due to unknown quantities.
2008-05-15 | Design | Median | I-CHANGE RECONST(O) | 7 | CLARK | The steepness of existing medians on the Western Kentucky Parkway allows water to migrate into the driving lanes thus causing rain or slick ice conditions. | Flattening slopes in the median of the Western Kentucky Parkway to 4:1 slopes , for example , was suggested.
2008-05-15 | Traffic | Lighting | I-CHANGE RECONST(O) | 7 | CLARK | There was insufficient lighting set up at the interchange of the Western Kentucky Parkway and the Pennyrile Parkway. | A change order was issued for a High Mast Lighting system at the interchange as set up by Central Office Traffic.
2008-05-15 | Traffic | Lighting | I-CHANGE RECONST(O) | 7 | CLARK | There was insufficient lighting set up at the interchange of the Western Kentucky Parkway and the Pennyrile Parkway. | A change order was issued for a High Mast Lighting system at the interchange as set up by Central Office Traffic.
2008-05-15 | Construction | Contracts | I-CHANGE RECONST(O) | 7 | CLARK | The time frame for letting pavement rehabilitation projects tends to cause problems with the overlaying of bridge decks and maintenance of traffic. When pavement rehab jobs are let near the winter season , the bridge deck overlay has to be modified or d | When establishing a time frame for letting pavement rehabilitation projects that involve overlaying of bridge decks , consideration should be given to avoiding proximity to the winter season due to the issues it causes.
2008-05-15 | Design | Safety | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | Safety problems with existing headwalls and slopes were not addressed within the project limits. | Existing problems with headwalls and guardrail should be addressed at the time of rehabilitation to eliminate the need for additional contracts in the future.
2008-05-15 | Design | Adjacent Projects | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | There was a 1 , 000 foot stretch of road between this project and a previously completed project that was not repaved. | An increase in paving quantities allowed paving to be completed on this stretch of road.
2008-05-15 | Pavement | Omission | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | There were concerns about potential rutting on US 68 due to high traffic volumes. | Rut Lessening Modifier (PMAC) was added in the top course of bituminous base and surface.
2008-05-15 | Utilities | Relocation | PAVEMENT REHAB-INT(P) | 7 | FAYETTE | Utilities are not being relocated correctly. | It was discussed to have resident engineer in charge of overseeing and setting dates for relocation of utilities. Different ways of charging utility companies for delays in relocation of utilities were also discussed. These included charging penalties f
2008-05-02 | Construction | Subsurface | RELOCATION(O) | 11 | WHITLEY | Pumping of subgrade occurred at Stations 891+00 , 910+35 , 914+00 , and 928+00. | Slabs had to be removed at Stations 891+00 , 910+35 , 914+00 , and 928+00 and these areas had to be undercut and rebuilt in order to stabilize the subgrade.
2008-05-02 | Design | Safety | RELOCATION(O) | 11 | WHITLEY | Existing median drain boxes would create safety hazards at the proposed left turn lane being added at Stations 870+16 , 891+00 , 899+00 , and 905+00. | These boxes were raised to eliminate hazards at these locations and meet roadside safety design standards.
2008-05-02 | Design | Omission | RELOCATION(O) | 11 | WHITLEY | The current super-elevation along the curve from Station 951+50 to Station 960+50 approached 8.5%. Reduction of the super-elevation was needed to facilitate constructability of the adjacent lane widening. | Class 3 Asphalt Base quantities were added to decrease the super-elevation along the curve. The Department elected to use asphalt base to decrease this super-elevation to around 4% , which met the design criteria for the posted speed limit.
2008-05-02 | Design | Safety | RELOCATION(O) | 11 | WHITLEY | Widening at Adams Road while maintaining the existing drainage would have created a 6 foot drop adjacent to the outside shoulder. | A lump sum item was established , which included removing two headwalls , extending the 18 inch culvert pipe from the Adams Road entrance and MarathonÖs parking lot into the adjusted drop box , providing fill material , and grading to drain. The lump
2008-05-02 | Pavement | Repair | RELOCATION(O) | 11 | WHITLEY | More pavement deterioration than anticipated was encountered on the project. | Change Order was written to secure funding to perform additional JPC repairs on the project.
2008-05-02 | Drainage | Existing Pipe | RELOCATION(O) | 11 | WHITLEY | Additional issues arose involving the 18 inch Culvert pipe being replaced at Station 956+35. Widening at this location required extending the outlet end of an 18 inch culvert pipe. However , drainage from the existing outlet was lower than the next exi | To correct the drainage , it was necessary to remove and replace 48 feet of the existing culvert pipe in order to raise the outlet so it would properly drain into the next inlet. The work took three days and was performed under traffic. The work also r
2008-05-02 | Design | Quantities | RELOCATION(O) | 11 | WHITLEY | There were not enough hook bolts with expansion anchors set up for the barricade. | Additional quantities were established through Change Order.
2008-05-02 | Right-of-Way | Omission | RELOCATION(O) | 11 | WHITLEY | Widening at Station 930+50 encroached upon a 15 foot concrete wall previously installed by a property owner on right-of-way , which created a roadside hazard. | The 15 foot concrete wall needed to be removed by Change Order.
2008-05-02 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | The Guardrail Posts established in the plans were inadequate for use at various locations along slopes. | Extra Length Guardrail Posts were added at these locations so the posts could be driven to a suitable depth to achieve proper stability.
2008-05-02 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | The Guardrail Posts established in the plans were inadequate for use at various locations along slopes. | Extra Length Guardrail Posts were added at these locations so the posts could be driven to a suitable depth to achieve proper stability.
2008-05-02 | Drainage | Omission | RELOCATION(O) | 11 | WHITLEY | Additional items not set up on the original contract were needed for the 24-inch culvert pipe at Station 953+00. | A Sloped & Flared box inlet-outlet 24-inch was added for the 24-inch culvert pipe. The safety headwall was needed to meet roadside design standards.
2008-05-02 | Construction | Revisions | RELOCATION(O) | 11 | WHITLEY | US 25E was built in mid-70Ös. This project started out as a rehab project with PCC repair and diamond grinding , but was changed to also include capacity improvements through added turning lanes. | Shoulders were milled and replaced with asphalt (10Ö paved outside , 4Ö paved inside). The material from the shoulder removal was used for turning lanes. An extra westbound lane was installed for trucks to turn into a truck stop.
2008-05-02 | Pavement | Design | RELOCATION(O) | 11 | WHITLEY | The entrance at Station 931+50 experiences large volumes of heavy truck traffic and there was no feasible alternative to accommodate these vehicles. | The 150 foot X 14 foot entrance pavement at Station 931+50 was changed to JPC 24-hour to minimize the disruption to traffic.
2008-05-02 | Construction | Revisions | RELOCATION(O) | 11 | WHITLEY | The left turn lane to East City Dam Road at the end of the project limits lacked a sufficient taper to merge traffic back into a two-way traffic scenario. | For safety reasons , the left turn lane to East City Dam Road at the end of the project limits was extended to provide a sufficient taper for merging traffic back into a two-way traffic scenario.
2008-05-02 | Design | Omission | RELOCATION(O) | 11 | WHITLEY | The traffic island as well as the surrounding curb needed to be removed on the American Greetings Road Approach because trucks were hitting the raised curb but this work was omitted from the original contract. | A Change Order was established and the traffic island was replaced with the JPC 24-hour mix paved flush.
2008-05-02 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | A Bridge End Connector , as shown in the Current Standard Drawing for TY , could not be used on this project. The older railing system along the existing bridges of this rehab project would not accept this type of attachment in a practical and safe man | Modified Bridge End Connectors TY A and A-1 were used to tie guardrail to the railing system. These modified versions did not use the strut as detailed in the current standard drawings.
2008-05-02 | Design | Guardrail | RELOCATION(O) | 11 | WHITLEY | A Bridge End Connector , as shown in the Current Standard Drawing for TY , could not be used on this project. The older railing system along the existing bridges of this rehab project would not accept this type of attachment in a practical and safe man | Modified Bridge End Connectors TY A and A-1 were used to tie guardrail to the railing system. These modified versions did not use the strut as detailed in the current standard drawings.
2008-05-02 | Pavement | Repair | RELOCATION(O) | 11 | WHITLEY | South Stewart Road was degraded by heavy tractor trailer traffic attempting to enter US 25E. | Repair work was performed on South Stewart Road via Change Order.
2008-05-02 | Pavement | Seeping | RELOCATION(O) | 11 | WHITLEY | Water was pumping through the pavement in some locations. | The 0.50 max aggregate asphalt mixture was changed to 0.38 max aggregate to keep water from pumping through the pavement.
2008-05-01 | Utilities | Omission | RELOCATION(O) | 11 | LAUREL | A sewer line was damaged by the Contractor while Connector #7 was being constructed at Approach STA 46+00. This sewer line was not shown on plans. | The Contractor hired a local licensed plumbing contractor to repair the line. The Contractor charged a separate fee for labor , equipment , backfill material , and excavation.
2008-05-01 | Construction | Revisions | RELOCATION(O) | 11 | LAUREL | The contractor was directed to install two 30-inch concrete pipe culvert headwalls on an entrance pipe. However , it was later discovered that these headwalls could not be installed due to their close proximity to a waterline. | The Contractor was reimbursed for 30-inch Culvert Pipe Headwall , Perforated Pipe Headwall TY 1-4 inch , and Drop Box Inlet Type 13G because the headwalls were eliminated by the Department.
2008-05-01 | Structures | Quantities | RELOCATION(O) | 11 | LAUREL | Design quantities of Steel Reinforcement and Steel Reinforcement -- Epoxy Coated were insufficient due to an error in the plans. | Adjustments of the design quantities for Steel Reinforcement and Steel Reinforcement -- Epoxy Coated were made via Change Order.
2008-05-01 | Pavement | Quantities | PAVEMENT REHAB-PRI(P) | 11 | LAUREL | The original quantities for full depth patching were inadequate. | A field inspection determined additional areas where full depth patching was needed. In order to obtain the maximum benefit of the diamond grinding , an additional 2 , 007 square yards of full depth patching was added.
2008-05-01 | Structures | Quantities | RELOCATION(O) | 11 | LAUREL | Steel reinforcement was delivered to project (per bill of reinforcement in plans) that was not needed. The bill of reinforcement on plans was incorrect. | Steel Reinforcement was added to reimburse Contractor for steel reinforcement delivered to project that was not needed. The unit prices was based on invoice prices plus handling for the material. The material became property of the Department.
2008-05-01 | Pavement | Repair | PAVEMENT REHAB-PRI(P) | 11 | LAUREL | Some of the concrete pavement that was repaired one year prior was already showing signs of cracking and displacement. Partial depth patches in some areas had help up very well while other spots had failed. The Contractor had performed the partial depth | Additional funding was provide via Change Order to repair the partial depth patches. The specified date of completion was changed from May 25 , 2006 to June 30 , 2006.
2008-05-01 | Geotechnical | Unsuitable Material | RELOCATION(O) | 11 | LAUREL | Unstable material was discovered at footer locations for Abutment #1 STA 1141+45 and Pier #1 STA 1142+23. | Mass concrete was needed due to the unstable material that was discovered at the footer locations. The unstable material was excavated down to solid rock. As per Section 601.05 of 2004 Standard Specifications , two times the delivered cost of concrete
2008-05-01 | Design | Guardrail | RELOCATION(O) | 11 | LAUREL | The existing guardrail on old KY 61 interfered with construction of the embankment for Connector Rd. #6 Right Approach STA 57+10. This situation was not addressed in the plans. | The existing guardrail on old KY 61 was removed via Change Order.
2008-05-01 | Design | Guardrail | RELOCATION(O) | 11 | LAUREL | The existing guardrail on old KY 61 interfered with construction of the embankment for Connector Rd. #6 Right Approach STA 57+10. This situation was not addressed in the plans. | The existing guardrail on old KY 61 was removed via Change Order.
2008-05-01 | Structures | Omission | RELOCATION(O) | 11 | LAUREL | No quantity for £Structure Excavation-Solid Rock¥ was set up in plans at Abutment #1 STA 1141+43 but solid rock had to be excavated to construct the abutment and to allow for concrete beam clearance. | An additional quantity for Structure Excavation ô Solid Rock was established for Abutment #1.
2008-05-01 | Geotechnical | Elevations | RELOCATION(O) | 11 | LAUREL | Solid rock was encountered at a higher elevation than expected at Pier #1 STA 1142+23. | An additional quantity for Structure Excavation ô Solid Rock was established for Pier #1.
2008-05-01 | Pavement | Quantities | PAVEMENT REHAB-PRI(P) | 11 | LAUREL | Partial Depth Patching Latex quantities were severely underestimated. | A Change Order was needed to transfer funds between PO Lines to adjust for items that were overrun and underrun.
2008-05-01 | Design | Adjacent Projects | RELOCATION(O) | 11 | LAUREL | Delays were caused by the adjacent KYTC project for Item 8-162.61. The adjacent project had approximately 40 , 000 cubic yards of borrow excavation set up in plans to be excavated from this project between STA 1120+00 and 1125+00. Due to simultaneous co | Delay costs were discussed in a meeting between the Department and the Contractor on October 31 , 2006. The agreed upon compensation for the delays was approved by Central Office Division of Construction and paid via Change Order.
2006-07-28 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 8 | MCCREARY | Field conditions prevented installation of a Sanitary Sewer Manhole at 5.01-8.0 FT as per the plans. | The Sanitary Sewer Manhole was installed at 8.01-10.0 FT instead and the locations of the changes were noted on the as-built plans.
2006-07-28 | Utilities | Plans | MAJOR WIDENING(O) | 8 | MCCREARY | There were concerns about disruptions of service to the Owsley County Health Department , the Owsley County Board of Education , and numerous other individuals along the route due to waterline tie-ins within the project limits. | All tie-ins within the project limits were changed to a wet tap connection to reduce the shut off time involved with the utility work.
2006-07-28 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 8 | MCCREARY | Water and sewer plans showed relocating and connecting to existing water line within work area shown for the KY 3347 approach. However , the water line was not found at the location designated in the plans. | Connection work had to be shifted to another location where a known water meter existed along KY 3347 , which resulted in disturbance to a copper service line to a private residence. Additional copper pipe and PVC pipe were needed to reroute the line.
2006-07-28 | Utilities | Omission | MAJOR WIDENING(O) | 8 | MCCREARY | An existing fire hydrant at approximately RT STA 14+82 was omitted from the plans. | A Change Order provided the funding for the hydrant to be removed and reinstalled as close to the original plan as possible after the roadway widening was complete.
2006-07-28 | Utilities | Omission | MAJOR WIDENING(O) | 8 | MCCREARY | A school bus garage facility was omitted from Sheet 2.2 of the water and sewer line replacement plans. | Sewer pipe quantity was increased near and along Myers Road to hook up the school bus garage facility.
2006-07-28 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 8 | MCCREARY | The 43 feet of open cut in road and creek and steel encasement installation for a 6-inch water main under Marshall Street were insufficient to reach the desired location. | An additional 10 feet of open cut and encasement was necessary to reach the limits once measurements were gathered at the installation site.
2006-07-28 | Utilities | Omission | MAJOR WIDENING(O) | 8 | MCCREARY | A residential sewer connection was omitted from the plans. | A Change Order was established to connect the residence to sewer lines.
2006-07-28 | Utilities | Omission | MAJOR WIDENING(O) | 8 | MCCREARY | Sheet 2.1 of the water line replacement plans refers to a 200 foot radius near the KY 3347 approach where new installations were supposed to be encased or protected from the threat of fuel tank leakage. However , pay items were omitted from the plans to | Pay items for this work were approved by Change Order.
2006-07-28 | Utilities | Conflicting Information | MAJOR WIDENING(O) | 8 | MCCREARY | The 54 foot bore requirement on sheet 5.1 of the water line replacement plans near STA 28+10 conflicted with another new line installed as part of this contract. | The bore requirement on sheet 5.1 of the water line replacement plans near STA 28+10 was extended six additional feet to avoid conflict.
2006-07-28 | Drainage | Existing Pipe | MAJOR WIDENING(O) | 8 | MCCREARY | The plans proposed that a 48-inch existing cross drain at Station 27+75 , which was still in good condition , be removed. The depth of the pipe was 6 to 8 feet and would have necessitated a large trench excavation that would have caused traffic delays | To reduce traffic delay and expedite mainline construction in the City of Booneville , the pipe was left in place and filled with flowable fill and aggregate. The unit price established was comparable to other projects where flowable fill was utilized w
2006-07-28 | Utilities | Omission | MAJOR WIDENING(O) | 8 | MCCREARY | Sheet R7 of the plans noted a disputed property line along the KY 3347 approach. The disputed area was emphasized by cross hatches between Parcel 21 and Parcel 10. However , the Booneville Sewer and Water District requested installation of two service | The two service lines were added through Change Order.
2006-07-28 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 8 | MCCREARY | Relocation of a sewer line was supposed to be completed using the bore method. However , there were concerns that this approach might result in a disturbance to unidentified existing underground in the area. | The relocation of the sewer line was completed by open cut rather than the bore method to avoid any disturbance to existing lines located underground. The unit price established was based on a relatively small quantity and very delicate , time consuming
2006-07-28 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 8 | MCCREARY | Utility plans called for a road bore under KY 3347. However , since the accuracy of the utility lines located on the plans was inconsistent , there were concerns about possible disturbances to utility lines that were underground and not shown on the pl | The Department chose to open cut the road and install a steel encasement pipe instead. Asphalt pavement was placed after the open cut pip placement was complete.
2006-07-28 | Utilities | Quantities | MAJOR WIDENING(O) | 8 | MCCREARY | The original quantity was not sufficient for installing water service lines as per the plans at other locations within the project limits. | Additional quantities for installing water service lines were approved by Change Order.
2006-07-27 | Geotechnical | Soils | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were poor , wet soil areas within the new roadway that were not addressed in the original design. | Additional quantities of Structure Granular Backfill and Geotextile Fabric Type IV were approved to be used for rock drainage blanket and stabilization of poor , wet soil areas within the new roadway.
2006-07-27 | Right-of-Way | Fencing | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Removal and resetting of the chain link fence and gates in front of the KYTC Maintenance at the new Right-of-Way line would have caused irreparable damage. | A Change Order was issued to install new chain link fence and gates in front of the KYTC Maintenance at the new Right-of-Way line.
2006-07-27 | Geotechnical | Slides | BRIDGE REPLACEMENT(P) | 8 | PULASKI | A slope failure occurred near Sta. 4107+00 due to a wet shale seam located above the bench on a rock cut. | A Change Order was approved to excavate 3 , 066 cubic yards of material from the slide area. Structure Granular Backfill along with 6¥ Perforated Pipe and Fabric-Geotextile Type IV were used to stabilize the affected area.
2006-07-27 | Structures | Striping | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were no items for lane delineation on the bridge included in the original plans. | Durable pavement striping (TY 1-8 IN W and TY 1-8 IN Y) was added and placed on the bridge.
2006-07-27 | Utilities | Communication | BRIDGE REPLACEMENT(P) | 8 | PULASKI | The local Water District requested changes be made at the Elliott County Maintenance Barn. | A Sanitary Sewer Pump Station and Fire Hydrant were added at the Elliott County Maintenance Barn by Change Order.
2006-07-27 | Structures | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There was an area of slight superelevation where water would sheet flow across the bridge , but not drain properly , which caused standing water to accumulate on the bridge deck. | Pavement transitions from normal crown to super elevation on bridge projects should be reviewed carefully to eliminate the possibility of any sheet flow across the bridge. In this case , four deck drains were added to prevent accumulation of standing wa
2006-07-27 | Utilities | New Utilities | BRIDGE REPLACEMENT(P) | 8 | PULASKI | The hookup of a new water line to an old one as shown in the plans , would cause a disruption in service. | Four-inch and six-inch Retainer Glands were added and installed on the high pressure side of the force mains in addition with respective Wet Taps to avoid disruption in the water system.
2006-07-27 | Design | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Class 1 Asphalt Base 0.75 D PG64-22 had been included in the Pavement Summery but was inadvertently left off the bid proposal package. | A Change Order was written to add 2 , 578 tons of Class 1 Asphalt Base 0.75 D PG64-22.
2006-02-10 | Maintenance of Traffic | Striping | MAJOR WIDENING(O) | 9 | BATH | The project zone was in a congested area with high traffic volumes due to several businesses and a school within the work zone. However , temporary striping was not set up in the original contract. | Due to the phasing of the project , temporary striping had to be added to maintain a safe traffic flow.
2006-02-10 | Utilities | Quantities | MAJOR WIDENING(O) | 9 | BATH | Maintenance of traffic had to be performed separately for each utility phase including gas relocation , storm sewer installation , force main installation , and water line relocation. The utility work could not occurring simultaneously because it was | Additional DGA was needed to maintain traffic during the various utility phases.
2006-02-10 | Design | Excavation | MAJOR WIDENING(O) | 9 | BATH | Minor undercutting was needed during the roadway excavation work along mainline. | Additional DGA to fill the undercut areas was provided by Change Order.
2006-02-10 | Drainage | Pipes | MAJOR WIDENING(O) | 9 | BATH | The proposed storm sewer system provided inadequate drainage on the right side of the project where local businesses were located from approximately RT STA 20+00 to 20+60. | To achieve adequate drainage of the storm sewer system , the storm sewer pipe was extended beyond the limits shown to a drainage box near STA 20+00 which resulted in entrance disturbance to Parcel 10 that had to be replaced. Replacing the entrance requi
2006-02-10 | Design | Entrance | MAJOR WIDENING(O) | 9 | BATH | Larger voids than expected were encountered in some areas where the old asphalt and concrete entrance pavements were removed. | Additional DGA was established via Change Order to fill the voids.
2006-02-10 | Maintenance of Traffic | Entrances | MAJOR WIDENING(O) | 9 | BATH | Once curb installation began , additional items were needed to maintain access to businesses until paving or concrete placement could occur behind the curb. However , there was minimal TBB included in the original plans and it was priced at the same un | Additional DGA was established to maintain access to businesses during curb installation.
2006-02-10 | Drainage | Existing Pipe | MAJOR WIDENING(O) | 9 | BATH | The plans called for collecting new storm sewer drainage in a DBI Type 11 RT STA 39+60 and then carrying the water to a stream through existing drainage pipes that ran underneath the Citizens State Bank. However , the string of pipe under the bank was f | The drainage was rerouted away from the bank building to approximately RT STA 40+30 to a collection box , and the to the stream through a new 24-inch culvert pipe.
2006-02-10 | Maintenance of Traffic | Entrances | MAJOR WIDENING(O) | 9 | BATH | The access area in front of the commercial business at RT STA 42+60 (Parcel 22) during construction was narrower than before the project started and at a steeper grade. There were concerns that it would be unsafe for vehicles to traverse this entrance on | Discussion with District Design and Right-of-Way representatives on site led to the recommendation that concrete entrance pavement was necessary to improve access for the commercial traffic to the business.
2006-02-10 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 9 | BATH | There was storm sewer installation and water line relocation that occurred from RT STA 20+60 to approximately 28+60 on Parcel 10 that resulted in disturbances to the existing entrance pavement to a greater degree than the plans showed. | Additional quantities of entrance pavement and DGA were added to repair the areas of disturbance or damage.
2006-02-09 | Structures | Elevation Difference | RECONSTRUCTION(O) | 9 | ELLIOTT | Due to an error on the bridge plans , the construction elevation of the bridge was lower than the profile elevation of the roadway. | The roadway had to be lowered to meet the bridge at both bridge ends. Milling was added to lower the existing asphalt down to the new grade. Some of the milling extended down into the DGA. This work was performed from approximately station 3743+20 to 3
2006-02-09 | Pavement | Omission | RECONSTRUCTION(O) | 9 | ELLIOTT | There were concerns about potential separation of the top course of asphalt base and surface. | The use of a Material Transfer Vehicle to place the top course of asphalt base and surface was approved via Change Order.
2006-02-09 | Structures | Elevation Difference | RECONSTRUCTION(O) | 9 | ELLIOTT | The super elevation of the bridge did not match the rest of the roadway from stations 3738+78.81 to 3759+20.27. The new bridge had a cross slope of 6% while the existing pavement had a cross slope of approximately 5% in the truck lanes and 10% in the pas | Pavement wedging was added to correct the cross slope problem throughout the curve.
2006-02-09 | Structures | Phasing | RECONSTRUCTION(O) | 9 | ELLIOTT | Traffic had to be switched over to one side of the bridge to allow for part width construction. | The original traffic striping layout on both ends of the bridge had to be removed via Change Order for safety purposes and pavement striping temporary removable tape was added because temporary paint could not be used on the bridge deck. Temporary Raised
2006-02-09 | Maintenance of Traffic | Lane Closures | RECONSTRUCTION(O) | 9 | ELLIOTT | A traffic bottle neck was occurring at the temporary traffic signal near the bridge. | The bottle neck situation at the temporary traffic signal was eliminated by channeling traffic further back than the traffic control plans showed. Extra barrels were added in the truck lanes from Station 3740+50 back approximately 2 , 000 feet and from S
2006-02-09 | Structures | Dimensions | RECONSTRUCTION(O) | 9 | ELLIOTT | There was an error in the x-dimensions of the structures plans. The x-dimensions failed to address the bridge being on a 6% superelevation. | Corrections were made in the field in order to ensure an 8-inch deck across all beams , which required an added depth over some beams. A Change Order was approved to address the overrun of Class AA concrete.
2006-02-09 | Maintenance of Traffic | Phasing | RECONSTRUCTION(O) | 9 | ELLIOTT | There were four crash cushions installed during the first phase of construction. However , the plans did not address how to handle the crash cushions when the second phase of construction began. | When the second phase of construction started , the crash cushions had to be relocated by Change Order to correct the position for Phase II. The price included all materials , equipment , and labor for installment of this bid item.
2006-02-09 | Structures | Elevation Difference | RECONSTRUCTION(O) | 9 | ELLIOTT | The bridge was constructed in accordance with the project plans. However , the new bridge was approximately 8 inches lower than the existing pavement and the superelevation of the new structure did not match the superelevation of the existing roadway. | District Design was consulted and provided new roadway plans to correct the problem. Corrective work resulted in an overrun of asphalt quantities (including a switch from Base to Leveling & Wedging) , DGA (for shouldering) , striping removal , and rem
2006-02-09 | Design | Grade | RECONSTRUCTION(O) | 9 | ELLIOTT | There was a plan error involving the roadway grade. | The original pavement had to be removed and a new grade was established. Geotextile Fabric Type IV was needed in correlation with Crushed Aggregate size #2 to tighten soft spots in the subgrade to tighten soft spots in the subgrade from stations 3747+28
2006-02-09 | Structures | Quantities | RECONSTRUCTION(O) | 9 | ELLIOTT | The plan quantity of Class A concrete for Abutment 1 , Pier Caps , Columns , and End Bent 2 was calculated using approximate cut-off elevations shown in the plans. However , the deteriorated quality of concrete encountered in the field warranted addi | Additional quantities of Class A concrete were provided by Change Order.
2006-02-09 | Structures | Omission | RECONSTRUCTION(O) | 9 | ELLIOTT | Excavation behind abutment #1 and end bent #2 at STA 3745+69 and 3747+28 was needed in order to form up the new abutment and end bent. | Foundation Preparation and Structure Granular Backfill , which were not included in the plans , needed to be added due to the excavation behind the abutment and end bent.
2006-02-09 | Structures | Dimensions | RECONSTRUCTION(O) | 9 | ELLIOTT | The steel Stirrups for end bent #2 were too large to fit in the plan cap width , but the Contractor already had the steel at jobsite before error was realized. | Reimbursement of the steel for end bent #2 was necessary because of plan error. New steel had to be ordered.
2006-02-09 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 9 | ELLIOTT | Flex Delineator Posts were shown on the traffic control plans to be used as traffic control devices , but there were no bid items for them. | Flex Delineator Posts were added by Change Order and the price included all materials , equipment , and labor to install this bid item.
2006-02-09 | Structures | Plans | RECONSTRUCTION(O) | 9 | ELLIOTT | The plans showed where to put the bridge drains , but did not specify which type of drain to use. | Structural steel was added for galvanized steel drain pipes. It was determined that drain pipes were better suited for this particular bridge and the drains were certified and installed as per the standard drawing BGX-015-02.
2006-02-09 | Structures | Guardrail | RECONSTRUCTION(O) | 9 | ELLIOTT | Originally , the design called for a flume at the end of the bridge. However , the spacing of guardrail posts would not allow the bridge end treatment left of Station 3747+45 to match the standard drawings for the flume. | An island header curb was added to create the guardrail post spacing needed to match the standard drawing of the flume.
2005-07-29 | Environmental | Wells | MAJOR WIDENING(O) | 11 | LAUREL | An unknown water well was encountered 22 meters Rt. of Sta. 100+750. | A Change Order was issued to implement necessary plugging of the water well.
2005-07-29 | Environmental | Wells | MAJOR WIDENING(O) | 11 | LAUREL | An unknown water well was encountered 22 meters Rt. of Sta. 100+750. | A Change Order was issued to implement necessary plugging of the water well.
2005-07-29 | Structures | Quantities | MAJOR WIDENING(O) | 11 | LAUREL | Additional quantities of masonry coating were needed for the following areas: Pier #2 cap , strut , shear keys , and top portion of columns (down to 35' above footer). | Quantities of masonry coating were increased via Change Order.
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | The necessary quantities of granular material for end bent #2 were omitted from the original contract bid quantities. | A Change Order was approved to increase quantities of granular material that were necessary for end bent #2.
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | The necessary quantities of granular material for end bent #2 were omitted from the original contract bid quantities. | A Change Order was approved to increase quantities of granular material that were necessary for end bent #2.
2005-07-29 | Structures | Quantities | MAJOR WIDENING(O) | 11 | LAUREL | Additional quantities of masonry coating were needed for the following areas: Pier #2 cap , strut , shear keys , and top portion of columns (down to 35' above footer). | Quantities of masonry coating were increased via Change Order.
2005-07-29 | Construction | Subsurface | MAJOR WIDENING(O) | 11 | LAUREL | Unknown rubble and debris from building demolition was encountered below the subgrade elevation. | A Change Order established a lump sum item for removal of the rubble and debris from the building demolition.
2005-07-29 | Construction | Subsurface | MAJOR WIDENING(O) | 11 | LAUREL | Unknown rubble and debris from building demolition was encountered below the subgrade elevation. | A Change Order established a lump sum item for removal of the rubble and debris from the building demolition.
2005-07-29 | Construction | Delays | MAJOR WIDENING(O) | 11 | LAUREL | The contract for the project was let early. As a result , the construction methods of phases for Pier #2 were changed to yield an earlier completion date. However , delay costs associated with hindering the contractor from constructing Pier #3 for app | The delay costs that resulted in the construction of Pier #3 were offset by the savings due to elimination of the three coat painting system when materials were changed to weathering steel. The reduction in the cost included the elimination of galvanized
2005-07-29 | Construction | Delays | MAJOR WIDENING(O) | 11 | LAUREL | The contract for the project was let early. As a result , the construction methods of phases for Pier #2 were changed to yield an earlier completion date. However , delay costs associated with hindering the contractor from constructing Pier #3 for app | The delay costs that resulted in the construction of Pier #3 were offset by the savings due to elimination of the three coat painting system when materials were changed to weathering steel. The reduction in the cost included the elimination of galvanized
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | An item necessary for installation of pile points at end bent #2 of the bridge was omitted from the plans. | A Change Order was issued to add the item necessary for installation of pile points at end bent #2 of the bridge.
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | An item necessary for installation of pile points at end bent #2 of the bridge was omitted from the plans. | A Change Order was issued to add the item necessary for installation of pile points at end bent #2 of the bridge.
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | There were aesthetic and safety concerns about the appearance of Pier #2. | A Change Order was approved to apply coating to the entire concrete surface of Pier #2 and to install deflector plates to minimize staining of columns , clearance gauges , and warning signs.
2005-07-29 | Construction | Ride Quality | MAJOR WIDENING(O) | 11 | LAUREL | There were concerns about the ride quality across the bridge. | Diamond grinding throughout bridge truss was performed to improve ride quality.
2005-07-29 | Construction | Ride Quality | MAJOR WIDENING(O) | 11 | LAUREL | There were concerns about the ride quality across the bridge. | Diamond grinding throughout bridge truss was performed to improve ride quality.
2005-07-29 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | There were aesthetic and safety concerns about the appearance of Pier #2. | A Change Order was approved to apply coating to the entire concrete surface of Pier #2 and to install deflector plates to minimize staining of columns , clearance gauges , and warning signs.
2005-07-29 | Design | Special Note | MAJOR WIDENING(O) | 11 | LAUREL | Concrete for this project was of mass quantity , but the mass concrete note was not included in the plans. | The mass concrete note should have been made available in the plans. However , the Contractor did notice that the concrete was of mass quantity and bid for it accordingly.
2005-07-29 | Design | Special Note | MAJOR WIDENING(O) | 11 | LAUREL | Concrete for this project was of mass quantity , but the mass concrete note was not included in the plans. | The mass concrete note should have been made available in the plans. However , the Contractor did notice that the concrete was of mass quantity and bid for it accordingly.
2005-07-29 | Structures | Masonry Coating | MAJOR WIDENING(O) | 11 | LAUREL | Differentiation between requirements for masonry coatings for submerged areas of concrete should be noted. | Submerged coatings should be done in such a manner that allows for easier application.
2005-07-29 | Structures | Masonry Coating | MAJOR WIDENING(O) | 11 | LAUREL | Differentiation between requirements for masonry coatings for submerged areas of concrete should be noted. | Submerged coatings should be done in such a manner that allows for easier application.
2005-07-29 | Structures | Plans | MAJOR WIDENING(O) | 11 | LAUREL | A revision was made to the bridge design. | The revision required Pier #3 shear keys and thrust plates to be altered in order to prevent interference with the bottom strut. A decrease in contract items for concrete and steel resulted. However , an extra work item for labor , equipment , and ma
2005-07-29 | Geotechnical | Sinkhole | MAJOR WIDENING(O) | 11 | LAUREL | A large sinkhole was encountered Rt. Sta. 101+780. | Excavation and refill of the sinkhole was established via Change Order.
2005-07-29 | Geotechnical | Sinkhole | MAJOR WIDENING(O) | 11 | LAUREL | A large sinkhole was encountered Rt. Sta. 101+780. | Excavation and refill of the sinkhole was established via Change Order.
2005-07-29 | Right-of-Way | Coordination | MAJOR WIDENING(O) | 11 | LAUREL | A Right-of-Way agreement was made with a commercial property after the plans were created. | Additional quantities of entrance pipe , 2 metal end sections , DGA base , asphalt base , and asphalt surface were required to construct a commercial entrance at Rt. Sta. 100+509.78.
2005-07-29 | Right-of-Way | Coordination | MAJOR WIDENING(O) | 11 | LAUREL | A Right-of-Way agreement was made with a commercial property after the plans were created. | Additional quantities of entrance pipe , 2 metal end sections , DGA base , asphalt base , and asphalt surface were required to construct a commercial entrance at Rt. Sta. 100+509.78.
2005-07-29 | Structures | Plans | MAJOR WIDENING(O) | 11 | LAUREL | A revision was made to the bridge design. | The revision required Pier #3 shear keys and thrust plates to be altered in order to prevent interference with the bottom strut. A decrease in contract items for concrete and steel resulted. However , an extra work item for labor , equipment , and ma
2005-07-29 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 11 | LAUREL | Originally the plans lacked notes for sufficient erosion control on the project. | Supplemental items were needed for requiring placement and cleaning of temporary silt fencing.
2005-07-29 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 11 | LAUREL | Originally the plans lacked notes for sufficient erosion control on the project. | Supplemental items were needed for requiring placement and cleaning of temporary silt fencing.
2005-07-29 | Design | Survey | MAJOR WIDENING(O) | 11 | LAUREL | The actual field topography and the control points on this project did not always match. | It was recommended to field check the topography and control points to be sure they tie together. Also , State Plane coordinates with grid-factor should be shown.
2005-07-29 | Design | Survey | MAJOR WIDENING(O) | 11 | LAUREL | The actual field topography and the control points on this project did not always match. | It was recommended to field check the topography and control points to be sure they tie together. Also , State Plane coordinates with grid-factor should be shown.
2005-07-29 | Geotechnical | Quantities | MAJOR WIDENING(O) | 11 | LAUREL | It was necessary to correct the existing conditions of a slope located Rt. Sta. 101+960 to Sta. 102+100. | Additional excavation quantities were needed to make necessary slope revisions to correct the existing slope conditions.
2005-07-29 | Geotechnical | Quantities | MAJOR WIDENING(O) | 11 | LAUREL | It was necessary to correct the existing conditions of a slope located Rt. Sta. 101+960 to Sta. 102+100. | Additional excavation quantities were needed to make necessary slope revisions to correct the existing slope conditions.
2005-07-29 | Maintenance of Traffic | Detours | MAJOR WIDENING(O) | 11 | LAUREL | Old KY 90 , which was supposed to be used as a detour for KY 790 , was in inadequate condition to accommodate detour traffic. | Resurfacing Old KY 90 was necessary to accommodate detour traffic.
2005-07-29 | Maintenance of Traffic | Detours | MAJOR WIDENING(O) | 11 | LAUREL | Old KY 90 , which was supposed to be used as a detour for KY 790 , was in inadequate condition to accommodate detour traffic. | Resurfacing Old KY 90 was necessary to accommodate detour traffic.
2005-06-16 | Utilities | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The original design for the Grinder Pump Station did not take into account future maintenance needs. | Additional valves had to be added to the Grinder Pump Station to allow for the shutoff of flow to the pump for any future maintenance.
2005-06-16 | Geotechnical | Elevations | RECONSTRUCTION(O) | 2 | MCLEAN | Removal of unsuitable material around the location of a pond Rt. Sta. 208+900 , per a Geotechnical Note placed the existing cross-drain at Sta. 208+840 at a higher elevation than the bottom of the pond , which prevented any drainage. Conditions were no | Therefore , a Steel Encasement Pipe-300 mm was jacked and bored to allow pond drainage.
2005-06-16 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 2 | MCLEAN | The Maintenance of Traffic plan for Sta. 209+500 to 209+700 was found inadequate for project phasing and traffic safety. | As a result , the existing roadway left of the centerline was widened where Detour 2 was constructed to allow for adequate grade separation.
2005-06-16 | Drainage | Pipes | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The proposed drainage design did not match the existing fill slope at Rt. Sta. 1+471. | The pipe at this location had to be extended and the precast concrete headwall was removed and reset.
2005-06-16 | Drainage | Error | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The project plans provided a detail for the slotted drain aprons throughout the project that did not match the Standard Drawing. | Epoxy coated steel reinforcement was added for the slotted drain aprons throughout the project , as called for in Standard Drawing RDI-200-04.
2005-06-16 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Poor foundation material was encountered during pipe installation. | Pipe undercutting was performed and Geotextile fabric was used around the pipe bedding.
2005-06-16 | Drainage | Flooding | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | A building flooded when the drain became plugged up at Lt. Sta. 1+745. | The Contractor was reimbursed for cleaning up the flooded building.
2005-06-16 | Design | Survey | RECONSTRUCTION(O) | 2 | MCLEAN | The survey data was flown and not accurate in dense areas. As a result , the designated stations of several pipes as well as some inlet/outlet elevations were incorrect. Additionally , some contours were not accurate in the field. | It was recommended that sufficient field checks be performed to verify the accuracy of the DTM.
2005-06-16 | Drainage | Omission | RECONSTRUCTION(O) | 2 | MCLEAN | The original design provided inadequate drainage for the subgrade on the approaches. | Additional quantities of Crushed Stone Base were approved to use on approaches to allow for subgrade drainage.
2005-06-16 | Utilities | New Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Additional items not included in the plans were required until new lines were activated within the project area. | Temporary cutting and capping of existing lines was performed to allow the utility to loop in a different area , until new lines were activated within the project area.
2005-06-16 | Construction | Temporary Fencing | RECONSTRUCTION(O) | 2 | MCLEAN | There were concerns about the safety of the residents adjacent to the project area. | A temporary orange safety fence was added to improve the safety of the residents adjacent to the project area.
2005-06-16 | Drainage | Omission | RECONSTRUCTION(O) | 2 | MCLEAN | Fabric-Geotextile Type IV to be used to wrap the trench for the installation of pipes had been left off the bid proposal. | Additional quantities of Fabric-Geotextile Type IV were added by Change Order.
2005-06-16 | Utilities | Stacked Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There was an area where the required 450 mm vertical distance could not be maintained between the waterline and the force main line. | PVC pipe was added to be used as encasement where the required vertical distance separation could not be achieved.
2005-06-16 | Maintenance of Traffic | Entrances | RECONSTRUCTION(O) | 2 | MCLEAN | There was insufficient material setup to maintain safe access to all entrances within and adjacent to the project area. | Additional Traffic Bound base was provided via Change Order.
2005-06-16 | Utilities | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Two inch waterline at Lt. Sta. 2+295 was omitted from the utility plans. | Two inch waterline at Lt. Sta. 2+295 was provided via Change Order.
2005-06-16 | Construction | Earthwork | RECONSTRUCTION(O) | 2 | MCLEAN | During the undercutting of unsuitable material at Sta. 209+385 and 209+490 , the relocated waterlines were damaged. | The Contractor was reimbursed for the work involved to reestablish service and the waterlines were reconnected under traffic.
2005-06-16 | Drainage | Error | RECONSTRUCTION(O) | 2 | MCLEAN | Due to a discrepancy in the plans , 15.4 meters of pipe was bid in error in addition to the actual length of the pipe required at Sta. 208+543. | The Contractor was reimbursed for the restocking fee that resulted from this error.
2005-06-16 | Utilities | New Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The McCreary Water District needed additional pay items in order to allow for the coordination and opening of new lines within the existing system. | Pay items for steel encasement pipe , check valves , and force main cleanout were added by Change Order.
2005-06-16 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 2 | MCLEAN | Full depth Maintenance of Traffic areas on the northbound and southbound shoulders did not have sufficient quantities set up in the plans. | An additional 3 , 537 metric tons of Cl2 Asphalt Base 19.0D PG64-22 was supplied by Change Order.
2005-06-16 | Utilities | Existing Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were issues with the existing 1 inch water meters and service tubing for several businesses along the project. | A Change Order was approved to replace the existing 1 inch water meters and service tubing at the businesses.
2005-06-16 | Utilities | New Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | In order to keep services on , the new waterline had to be activated in small sections where no sampling points were available. | Additional temporary sampling points were required for the sampling of sections of waterline.
2005-06-16 | Maintenance of Traffic | Detours | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were concerns that a planned detour was unnecessary and cost inefficient. | A Change Order was issued to implement a Value Engineering Proposal , which the Division of Construction concurred with. The proposal involved replacing the detour with widening of the existing shoulder to accommodate traffic. The total decrease due to
2005-06-16 | Pavement | Quantities | RECONSTRUCTION(O) | 2 | MCLEAN | The plan quantities of Emulsified Asphalt RS-2 and Asphalt Seal Aggregate were insufficient to construct the typical sections as designed. | Additional quantities of Emulsified Asphalt RS-2 and Asphalt Seal Aggregate were approved by Change Order.
2005-06-16 | Utilities | Existing Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were changes in the detail sheets for the Force Main cleanouts. | The original bid pay amount was reduced and it was resubmitted with a new cost , which included having to install the cleanouts under wet conditions.
2005-06-16 | Drainage | Omission | RECONSTRUCTION(O) | 2 | MCLEAN | There was a drainage problem that needed to be addressed at Sta. 211+944. | Corrective work was performed at Sta. 211+944 , which consisted of installation of a drop Box Inlet Type 2-900 mm and a Junction Box 900mm , flattening of slopes , and elimination of guardrail.
2005-06-16 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Wet areas were encountered in the proposed roadway. | The wet areas were treated by removing the material and replacing it with Geotextile fabric Type IV and granular embankment.
2005-06-16 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 2 | MCLEAN | There were potential traffic safety issues involving a 1500 mm headwall from Rt. Sta. 208+840 during the future phases of construction. | The 1500 mm headwall was removed from Rt. Sta. 208+840 and the culvert extended under traffic. This work improved traffic safety through the following phases of construction.
2005-06-16 | Maintenance of Traffic | Quantities | RECONSTRUCTION(O) | 2 | MCLEAN | Pavement Striping-Temporary paint had been insufficiently bid for the lane shifts and other temporary traffic requirements. | Additional quantities of Pavement Striping-Temporary paint were added by Change Order.
2005-06-16 | Utilities | New Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There was a problem with installing a pipeline per plans due to differing site conditions. It was not feasible to avoid existing lines and an interruption of services while installing the new pipeline as originally intended. | Rock trenching was needed to allow the pipeline to be changed from one side of the roadway to the opposite side.
2005-06-16 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 2 | MCLEAN | There were insufficient quantities of erosion control items established in the original contract. | Additional quantities of Temporary Seeding and Protection and Temporary Silt Fence were established.
2005-06-16 | Utilities | New Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The proposed elevation of waterline being laid was inadequate to get the line under entrances and fill areas. | An extension of fire hydrants and valve boxes was required to increase the depth of the waterline in order to get beneath the entrances and fill areas.
2005-06-16 | Utilities | Existing Utilities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | If constructed per plans , there would be a temporary loss of utility service to the elementary school at Rt. Sta. 1+500. | In order to keep utility service to the elementary school at Rt. Sta. 1+500 field revisions were necessary.
2005-06-16 | Erosion Control Plan | Quantities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Additional items not included in the plans were needed for slopes steeper than 3:1. | Additional quantities of Special Seeding Crown Vetch were provided via Change Order.
2005-06-16 | Design | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Items needed at entrances were omitted from the plans. | A Change Order was issued to add the necessary quantities of entrance pipe.
2005-06-16 | Pavement | Approaches | RECONSTRUCTION(O) | 2 | MCLEAN | Additional paving items were needed to construct the tie-ins. | Leveling and Wedging was approved through Change Order and performed at the tie-ins.
2005-06-16 | Pavement | Omission | RECONSTRUCTION(O) | 2 | MCLEAN | Milled Rumble Strips were not bid on the project. | This item was added to the entire length of the project by Change Order.
2005-06-16 | Design | Phasing | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Most of the utility cost incurred due to working around construction and keeping service uninterrupted. There were design and construction phasing problems. Having utilities and construction working at the same time creates conflicts. | Utility works should have been completed prior to beginning construction.
2005-06-16 | Structures | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Items necessary for construction of the gravity retaining wall located at Sta. 2+974. were mistakenly omitted from the original contract bid items. | An item for Excavation of solid rock was added by Change Order.
2005-06-16 | Design | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The plans did not address how to handle existing guardrail during construction. | Existing guardrail had to be removed and taken to the McCreary County Maintenance Garage as per the Change Order.
2005-06-16 | Design | Excavation | RECONSTRUCTION(O) | 2 | MCLEAN | Inaccurate earthwork calculations cause problems with shortages of material and/or material haulage on the project. | It was recommended that when a new roadway is bisected by an existing roadway , earthwork calculations should be performed for separately for both sections of the new road to prevent problems with shortage of material and/or material haulage in either se
2005-06-16 | Environmental | Underground Tank | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The plans did not address a pump station tank at Rt. Sta. 1+840. | Septic tank treatment was required for pump station tank.
2005-06-16 | Construction | Rumble Strips | RECONSTRUCTION(O) | 2 | MCLEAN | There were concerns about inadequate milling of rumble strips and their durability. | Milled material should be removed from the strips. It was also recommended to apply chip seal on milled rumble strips in order to preserve and render the strips more durable over time.
2005-06-16 | Utilities | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Items needed for work on some waterlines were omitted. | PVC pipe , crushed aggregate No. 57 , steel encasement pipe , and ductile iron pipe were provided by Change Order.
2005-06-16 | Structures | Erosion Control | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were concerns about erosion of the roadway fill for Cora Cooper Road at the corners of the bridge wings. | Gabion baskets were provided at the corners of the bridge wings to hold the roadway fill in place for Cora Cooper Road.
2005-06-16 | Drainage | Ditches | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Wet material in the existing ditch Lt. Sta. 1+600 to Sta. 2+000 was present due to an existing spring. | Type III filter fabric and additional granular embankment were used to bridge over the wet material.
2005-06-16 | Design | Borrow/Waste | RECONSTRUCTION(O) | 2 | MCLEAN | Excavation operations within the project area revealed unusually deep topsoil resulting in limited availability of suitable material for the embankment. | Insufficient suitable material was identified by the Geotechnical Branch for the embankment on this project. Thus , 500 , 000 cubic meter of Borrow Excavation at a unit price of $1.00 was added to the project.
2005-06-16 | Design | Entrance | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Additional permitted entrances were added after the plans were prepared. The entrances were at the following locations: Lt. Sta. 3+032 , Lt. Sta. 3+103 , Lt. Sta. 3+191 , Lt. Sta. 3+223 , Lt. Sta. 3+464 , Lt. Sta. 3+560 , and Rt. Sta. 3+930. | Items necessary to construct these entrances had to be added via Change Order.
2005-06-16 | Right-of-Way | Coordination | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Changes were negotiated with property owners after the plans had been prepared. | Materials such as concrete pavement , entrance pipe , DGA base , and crushed aggregate No. 57 were added to create the negotiated entrances.
2005-06-16 | Drainage | Culvert | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were concerns that the specified culvert pipe at Sta. 3+391 , right and left of the centerline was not strong enough to withstand the extra embankment fill. | Geofoam (light-weight fill material) was added for the embankment fill around the culvert at Sta. 3+391.
2005-06-16 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | Unsuitable material was encountered at various areas of the project. | A Change Order was issued to replace the unsuitable material with Geotextile fabric Type III and granular embankment.
2005-06-16 | Drainage | Elevation | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | The slotted drains did not meet the Standard Drawing RDI-200-04 for 8 inch concrete gutters. | Additional Class A Concrete was added to make the slotted drains meet the Standard Drawing for 8 inch concrete gutters.
2005-06-16 | Utilities | Omission | RECONSTRUCTION(O) | 2 | MCLEAN | Due to an oversight in the plans , a waterline under the roadway had not been located. The waterline was in conflict with the new alignment of KY 11 , Rt. Sta. 211+200. | The Contractor was instructed to relocate the waterline and then was reimbursed for all costs through Change Order.
2005-06-16 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 2 | MCLEAN | There were concerns about insufficient safety precautions were taken to ensure safety of the traveling public various locations. | Additional quantities of temporary guardrail were added throughout the project phasing along with End Treatment Type 7 at various appropriate locations.
2005-06-16 | Design | Quantities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were insufficient quantities in the original plans for backfilling the bore pits that were inside the roadway. | An increase was approved in the plan quantity for No. 57 stone to be used for backfilling the bore pits.
2005-06-16 | Design | Entrance | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were entrances that were not shown on the plans. | Additional Class A Concrete was established for headwalls at the entrances that were not shown on the plans.
2005-06-16 | Utilities | Quantities | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were insufficient plan quantities to maintain service to the existing waterline at Sta.3+320. | A Change Order was issued to increase the plan quantity for steel encasement pipe in order to keep a loop feed for the existing waterline at Sta.3+320.
2005-06-16 | Drainage | Omission | PAVEMENT REHAB-PRI(P) | 2 | HENDERSON | There were concerns regarding potential saturation of the roadway by an underlying spring at Sta. 1+640. | A spring box and corresponding piped outlet to the ditchline was installed at Sta. 1+640. Excavation and backfill , No. 57 stone around the box , 12 meters of pipe , and 10 tons of asphalt for the temporary repair of roadway for traffic were also adde
2005-05-12 | Erosion Control Plan | Slope Protection | SURFACE(O) | 1 | CALLOWAY | Additional items were needed to stabilize a slope at the corner of Oak Hill Street and KY 136 W. | Type 1 Filter Fabric and Channel Lining Class II were added to stabilize the slope.
2005-05-12 | Drainage | Cross Drains | SURFACE(O) | 1 | CALLOWAY | A failing embankment over an exiting 24¥ cross drain was encountered just outside the project limit near the end of the project. | The failing embankment was effectively remedied by lining the pipe , replacing the pipe end sections , and adding a drop box at one end and a headwall at the other end of the cross-drain.
2005-05-12 | Design | Omission | SURFACE(O) | 1 | CALLOWAY | The quantity for Guardrail End Treatment Type 7 was omitted from the proposal. | A Change Order was written to include additional quantities of Guardrail End Treatment Type 7.
2005-05-12 | Design | Omission | SURFACE(O) | 1 | CALLOWAY | The plans did not include a sufficient transition from a 50-inch wall to a 32-inch wall. | Quantities of Concrete Median Barrier Type 12C1A-50 were increased to provide a sufficient transition between the walls.
2005-05-12 | Drainage | Elevation | SURFACE(O) | 1 | CALLOWAY | There was a plan elevation error at the location of a proposed Drop Box Inlet Type 16G. | A Riser for a Drop Box Inlet Type 16G was also added by Change Order.
2005-05-12 | Traffic | Omission | SURFACE(O) | 1 | CALLOWAY | Items needed for the relocation of lights were omitted from the original plans. | Two Electrical Junction Boxes had to be added for the relocation of lights.
2005-05-12 | Drainage | Ponding | SURFACE(O) | 1 | CALLOWAY | There was a lack of drainage on a flat section of the roadway , which caused pooling of water on the pavement. | Consideration should be given to draining run-off in zero grade areas to avoid pooling of water on the pavement. This can be accomplished by providing a slight grade (fall) to drainage structures.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | Guardrail End Treatment Type 1 was incorrectly set up in the plans due to the location of this item relative to a ramp. | Guardrail End Treatment Type 4A was added to replace the Type 1 End Treatment originally set up.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | Guardrail End Treatment Type 1 was incorrectly set up in the plans due to the location of this item relative to a ramp. | Guardrail End Treatment Type 4A was added to replace the Type 1 End Treatment originally set up.
2005-05-12 | Design | Radius | SURFACE(O) | 1 | CALLOWAY | The turning radii adjacent to an island on this project were not sufficient , which caused heavy (truck) traffic in particular to go over the island resulting in rapid wear. | Use of larger radii for the islands or painting the islands were indicated as possible solutions.
2005-05-12 | Structures | Quantities | SURFACE(O) | 1 | CALLOWAY | Insufficient quantities of Steel Reinforcement-Epoxy Coated were set up in the proposal. | A Change Order was established to increase the quantities of Steel Reinforcement-Epoxy Coated.
2005-05-12 | Maintenance of Traffic | Omission | SURFACE(O) | 1 | CALLOWAY | A necessary maintenance of traffic item was left off from the original plans. | £Relocate Crash Cushion¥ was added by Change Order.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | There were areas where the pavement edge drop-off did not accommodate normal length guardrail posts. | Extra Length of Guardrail Post were added via Change Order.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | There were areas where the pavement edge drop-off did not accommodate normal length guardrail posts. | Extra Length of Guardrail Post were added via Change Order.
2005-05-12 | Structures | Elevation Difference | SURFACE(O) | 1 | CALLOWAY | There was a discrepancy in a bridge elevation , which was not caught by the Bridge Office. The bridge design was performed by the Consultant , who had merely assumed an elevation. | The discrepancy in bridge elevation was noticed by the Resident Engineer , which resulted in substantial savings in Change Orders. A note should have been added to the plans to clearly indicate that the provided elevation was merely assumed and that it
2005-05-12 | Pavement | Thickness | SURFACE(O) | 1 | CALLOWAY | Insufficient quantities of Asphalt Pavement Milling & Texturing were bid because the thickness of the Asphalt Surface was unknown when plans were prepared. | The quantities of Asphalt Pavement Milling & Texturing were increased via Change Order.
2005-05-12 | Geotechnical | Unsuitable Material | SURFACE(O) | 1 | CALLOWAY | Unsuitable material (Blue Mud) was encountered in the area of a proposed pipe along US 431 from Rt. Sta. 13+20 to Sta. 15+20. | The material was undercut and Geotextile Fabric Type IV and Crushed Stone Aggregate No. 57 was used for stabilization.
2005-05-12 | Construction | Subsurface | SURFACE(O) | 1 | CALLOWAY | During the course of widening the shoulders , an electrical conduit was cut into inadvertently. The conduit was at the location where guardrail would be installed. | Work to relocate and replace the conduit and wires and raise the light pole bases was done on a Cost Plus basis.
2005-05-12 | Pavement | Repair | SURFACE(O) | 1 | CALLOWAY | Cracking and failing shoulders were encountered on the North and Southbound lanes. | A Change Order was approved to increase the quantities of Class 2 Asphalt Surface 0.50D PG64-22 in order to repair the cracking and failing shoulders.
2005-05-12 | Construction | Contracts | SURFACE(O) | 1 | CALLOWAY | Masonry Coating for the barrier wall at the base of the cemetery was inadvertently left off the bid proposal. | A Change Order was issued to add Masonry Coating for the barrier wall.
2005-05-12 | Maintenance of Traffic | Omission | SURFACE(O) | 1 | CALLOWAY | No Temporary Pavement Striping was set up on this project. | Temporary Paint 4-inch was added through Change Order.
2005-05-12 | Erosion Control Plan | Slope Protection | SURFACE(O) | 1 | CALLOWAY | Additional Erosion Control Items were needed to protect and stabilize a sliding bank in the southbound lane from Station 810+83 to Station 813+38. | Additional quantities of Channel Lining Class II were added to protect and stabilize the sliding bank.
2005-05-12 | Pavement | Thickness | SURFACE(O) | 1 | CALLOWAY | The Asphalt Base type did not match the criteria for 24Ö wide pavement. | The Asphalt Base type was changed from 0.75 inch to 1.00 inch at the same unit price.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | Crash Cushion set up on the job were Type VI D , which is used on 60 MPH roadways , but the design operational speed of this project was 45 MPH. | The Crash Cushion set up on the job was change from Type VI D to Type VI A.
2005-05-12 | Design | Guardrail | SURFACE(O) | 1 | CALLOWAY | Crash Cushion set up on the job were Type VI D , which is used on 60 MPH roadways , but the design operational speed of this project was 45 MPH. | The Crash Cushion set up on the job was change from Type VI D to Type VI A.
2005-05-12 | Structures | Omission | SURFACE(O) | 1 | CALLOWAY | Structure Granular Backfill had been omitted from the plans. | Structure Granular Backfill was added per standard drawing RGX-105-05.
2005-05-12 | Design | Quantities | SURFACE(O) | 1 | CALLOWAY | Insufficient quantities of Delineators for Barrier Walls were set up in the proposal. | A Change Order added the needed quantity.
2005-05-12 | Pavement | Omission | SURFACE(O) | 1 | CALLOWAY | The Asphalt Base quantity was shown on the roadway plans but omitted from the bid item total. | Two thousand eight-hundred tons of Asphalt Base were added by Change Orders.
2005-05-12 | Structures | Omission | SURFACE(O) | 1 | CALLOWAY | Concrete Barrier Wall Connectors were not supplied with the Barrier Walls or were possibly stolen. | Concrete Barrier Wall Connectors were added by Change Order.
2005-05-12 | Maintenance of Traffic | Shoulders | SURFACE(O) | 1 | CALLOWAY | During milling of the shoulder areas for shifting traffic unsuitable silty material incapable of sustaining asphalt equipment weight was encountered. | A Change Order was approved to implement additional quantities of Roadway Excavation.
2005-05-12 | Design | Striping | SURFACE(O) | 1 | CALLOWAY | The plans were designed with 6-inch Thermoplastic Pavement Striping , which did not match the existing striping and class of the roadway. | The width and type of Pavement Striping was changed from 6-inch Thermoplastic to 4-inch Paint.
2005-05-12 | Design | Striping | SURFACE(O) | 1 | CALLOWAY | The plans were designed with 6-inch Thermoplastic Pavement Striping , which did not match the existing striping and class of the roadway. | The width and type of Pavement Striping was changed from 6-inch Thermoplastic to 4-inch Paint.
2005-05-12 | Maintenance of Traffic | Safety | SURFACE(O) | 1 | CALLOWAY | There were concerns that there were insufficient measures taken to protect workers in median next to traffic. | Additional quantities of Concrete Barrier Wall Type 9T were installed to protect workers in median.
2005-05-12 | Geotechnical | Slides | SURFACE(O) | 1 | CALLOWAY | The plans contained a proposed rectangular paved ditch and barrier wall at a slide area below a cemetery along US 431 at Rt. 27+50. There were concerns that damage to the cemetery could have occurred during construction of the paved ditch and the barrier | A Change Order eliminated the rectangular paved ditch and barrier wall at the slide area below the cemetery. Instead , the area of the paved ditch and barrier wall was lined with Cyclopean Stone Rip Rap to stabilize the slide and prevent the bank from c
2005-05-12 | Design | Omission | SURFACE(O) | 1 | CALLOWAY | The item for £Remove Barrier Wall¥ was left off the original proposal. | £Remove Barrier Wall¥ was added by Change Order.
2005-05-12 | Design | Sight Distance | SURFACE(O) | 1 | CALLOWAY | After installation of the 50 inch Concrete Barrier Wall , it was discovered the line of sight for traffic entering US 41 was obstructed. | The decision was made to saw-cut the 50-inch wall to a 32-inch height for a distance of 500 feet in order to provide the required sight distance.
2005-05-12 | Drainage | Drop Box Inlets | SURFACE(O) | 1 | CALLOWAY | There were insufficient items provided in the plans to reduce erosion around the Drop Box Inlets on this project. | Additional quantities of Channel Lining Class II were added through Change Order.
2004-09-16 | Design | Striping | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were no items set up in the original plans for marking the centerline and edge line of US 119 Connector , Ramp A , Ramp B , and Burning Fork Road after construction was complete. | Pavement Striping-Permanent Paint 100MM was added by Change Order.
2004-09-16 | Design | Striping | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were no items set up in the original plans for marking the centerline and edge line of US 119 Connector , Ramp A , Ramp B , and Burning Fork Road after construction was complete. | Pavement Striping-Permanent Paint 100MM was added by Change Order.
2004-09-16 | Maintenance of Traffic | Striping | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Additional items were needed to help traffic safely navigate the US 119 Connector , Ramp A , Burning Fork Road , and various detours during the construction phase. | Pavement Striping-Temporary Paint 100MM was added to temporarily stripe the centerlines of these road segments.
2004-09-16 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were insufficient items set up along existing US 119 to divert traffic to one lane and to protect the traveling public from any fallen rocks or debris. | Four-hundred and seventy-nine additional meters of Concrete Barrier Wall Type 9T had to be established to place barrier wall along existing US 119.
2004-09-16 | Design | Plans | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Some of the match lines on the plans did not provide enough overlap with the next sheet , which made them difficult to read. | Plans should be checked to make sure that match lines provide sufficient overlap with the next sheet of the plans.
2004-09-16 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There was an error on the bar list for the outlet wing walls for the Burning Fork Creek culvert at Sta. 500+842.451. | Additional quantities of steel reinforcement had to be set up for the outlet wing walls.
2004-09-16 | Pavement | Shoulders | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were concerns that the proposed layer of asphalt base on the shoulders of the US 119 Connector would be inadequate. | Six-thousand , five-hundred and forty-eight additional metric tons of Class 3 Asphalt Base 19.0E PG64-22 had to be setup to add an additional layer of asphalt base to the shoulders on the US 119 Connector.
2004-09-16 | Erosion Control Plan | Seeding | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Central Office Construction directed the Contractor to install erosion control mechanisms to all the ditches that were not utilizing channel lining to protect seeding applications. | Erosion control blanket was installed on these ditches to protect seeding applications.
2004-09-16 | Design | Excavation | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Roadway Excavation was set up for the box culvert at Sta. 500+445 , but excavating to remove the culvert would have caused major delays due to high traffic volumes. | It was decided to pneumatically backstow the culvert in order to avoid significant delays. The cost of the excavation was $21 , 418.50 versus $35 , 264.00 for the backstowing process.
2004-09-16 | Pavement | Thickness | BRIDGE REPLACEMENT(P) | 8 | PULASKI | It was felt that the pavement design was not suitable for heavy truck traffic in this area and that the shoulders needed to be designed using thicker pavement and a thicker base. | The changes provided an additional four inches of base to the mainline , full depth asphalt to the shoulders , and a drainage layer connected to perforated pipe and headwalls to divert water from under the mainline to ditches.
2004-09-16 | Drainage | Temporary Drainage | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Additional items not included in the original plans were needed when two way traffic on US 119 was shifted onto the southbound lanes in order for construction to proceed on the existing northbound lane. | Temporary pipe was needed to provide drainage on US 119 while two way traffic was shifted onto the southbound lanes.
2004-09-16 | Design | Grade | BRIDGE REPLACEMENT(P) | 8 | PULASKI | The grade on Burning Fork Approach Road had to be revised. | The grade revision required additional quantities of CL3 Asphalt Base 19.0E PG64-22. Additionally , five S & F Box Outlets were also needed due to the change in the drainage layout for the grade revision.
2004-09-16 | Maintenance of Traffic | Communication | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were concerns that the public was not informed early enough about changes in traffic patterns that would occur due to construction. | The public should be informed earlier about changes in traffic patterns that may occur due to construction. This could have been accomplished by a newspaper article , radio announcement , or public meeting.
2004-09-16 | Structures | Plans | BRIDGE REPLACEMENT(P) | 8 | PULASKI | The rock face that was shown at End Bent #1 on the plans was actually located further back than shown on the plans. | Additional quantities of Retaining Wall had to be set up for the MSE Wall at End Bent #1 because the retaining wall had to be constructed in front of the rock face.
2004-09-16 | Maintenance of Traffic | Safety | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were insufficient measures taken to protect the traveling public from fallen rocks and debris along the existing US 119 towards the new entrance of the Burning Fork detour. | Additional quantities of Concrete Barrier Wall Type 9T were set up to extend the barrier wall.
2004-09-16 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Additional items not included in the original plans were needed when traffic on US 119 was shifted to two ways on the southbound lanes in order for construction to proceed on the existing northbound lane. | Leveling and Wedging was added to accommodate two way traffic being shifted onto the southbound lanes.
2004-09-16 | Maintenance of Traffic | Safety | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were safety concerns regarding construction of the Burning Fork detour during the winter months. | Three-hundred and sixty-six additional meters of Temporary Guardrail had to be setup for the protection of the traveling public.
2004-09-16 | Pavement | Design | BRIDGE REPLACEMENT(P) | 8 | PULASKI | The pavement templates did not match from one section to the other. | The pavement had to be changed from Class 3 Asphalt Base 19.0E PG64-22 to Class 4 Asphalt Base 37.5D PG64-22. Class 3 Asphalt Surface 12.5D PG 64-22 had to be changed to Class 4 Asphalt Surface 12.5D PG 76-22. The DGA was changed to Drainage Blanket Typ
2004-09-16 | Maintenance of Traffic | Safety | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were safety concerns regarding inadequate delineation of temporary barrier wall to the traveling public. | Two-hundred White Delineators for Barrier were added to ensure the safety of the traveling public.
2004-09-16 | Design | Slopes | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Additional drainage was needed to drain water from a redesigned ditch due to a slope change located right of centerline from Sta. 500+800 to Sta. 501+000. | A Drop Box Inlet Type 7 Mod. was added to achieve proper drainage from the redesigned ditch.
2004-09-16 | Erosion Control Plan | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were insufficient erosion control items established in the Best Management Practices Erosion Control Plans. | Ten Silt Traps Type A and Clean Silt Trap Type A had to be added through Change Order.
2004-09-16 | Design | Plans | BRIDGE REPLACEMENT(P) | 8 | PULASKI | It was the opinion of the Post Construction Review Team that the plans should have been delivered to the Contractor earlier so they could have had time to develop accurate estimates. | If the plans were prepared two to three months earlier , it would have given the Contractor adequate time to investigate items such as waste sites , etc.
2004-09-16 | Geotechnical | Elevations | BRIDGE REPLACEMENT(P) | 8 | PULASKI | Solid rock was encountered earlier than anticipated between stations 1645+09.54 and 1642+25. | Eight-hundred and thirty-four additional cubic meters of Structure Excavation ô Solid Rock had to be set up via Change Order.
2004-09-16 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 8 | PULASKI | There were insufficient items set up to divert traffic from the northbound lane to the southbound lane , thus dividing the southbound lanes from one way traffic to two way traffic. | Tubular posts were added to safely divert traffic from the northbound lane to the southbound lane.
2004-05-21 | Utilities | Conflicting Information | MAJOR WIDENING(O) | 9 | BOYD | The plans called for a water meter relocation at Sta. 4+220. It was assumed that this was a standard residential meter , but it was discovered that the water meter was a 6 inch master meter. | A Change Order was established to compensate the Contractor for the extra price to relocate the master meter.
2004-05-21 | Geotechnical | Embankment Stabilization | MAJOR WIDENING(O) | 9 | BOYD | Additional work at various locations throughout an existing cut was needed to repair the existing roadway embankment as well as prevent further erosion and roadway failures after the project was completed. | A Change Order established Special Roadway Excavation to repair the existing roadway embankment.
2004-05-21 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 9 | BOYD | Additional safety items were needed to protect against drop off conditions on the detour at the Buffalo Creek culvert located at Sta. 3+732. | Special Temporary Guardrail was added for placement on the detour at the Buffalo Creek culvert. This is different from normal temporary guardrail because the posts for the temporary guardrail did not have to be drilled.
2004-05-21 | Utilities | Omission | MAJOR WIDENING(O) | 9 | BOYD | A sanitary sewer force main line including gate valves was not shown on the plans. | A Change Order was approved to construct the sanitary sewer force main line and gate valves within the project limits.
2004-05-21 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 9 | BOYD | Central Office Construction directed the Contractor to install erosion control mechanisms to all the ditches that were not utilizing channel lining to protect seeding applications. | Erosion control blanket was installed on these ditches to protect seeding applications.
2004-05-21 | Pavement | Omission | MAJOR WIDENING(O) | 9 | BOYD | The existing base required work not included in the plans before the application of the final riding surface could occur. | A Change Order added leveling and wedging of the existing base before the application of the final riding surface.
2004-05-21 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 9 | BOYD | During excavation for the final mainline grade from Sta. 2+860-Sta. to 3+050 , a coal seam was discovered. | The coal seam was undercut and then removed from the final mainline grade.
2004-05-21 | Environmental | Wells | MAJOR WIDENING(O) | 9 | BOYD | A water well that was not shown on the plans was discovered at Sta. 3+860 Lt. during construction. | The water well was plugged in accordance with specifications.
2004-05-21 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 9 | BOYD | After excavation of the proposed culvert , it was determined that the foundation material was unsuitable. | An additional 0.305 meters of excavation along with Type III filter fabric and placement of Number 2 stone was utilized to correct the problem.
2004-05-21 | Geotechnical | Unsuitable Material | ROCKFALL MITIGTN(P) | 9 | BOYD | Unsuitable material was encountered at subgrade elevation from Rt. Sta. 10+520 to Sta. 10+660. | Quarry-run or shot rock was placed below the subgrade and wrapped in Geotextile Fabric Type III to achieve stabilization of these areas.
2004-05-21 | Maintenance of Traffic | Detours | MAJOR WIDENING(O) | 9 | BOYD | The existing road was very close to a rock cut with a river on the other side. The original detour plan was going to delay traffic considerably through the project. | Upon a field review , it was determined that a cut bench in the rock provided an excellent area for the detour. This worked extremely well because it allowed traffic to flow around the job site with minimal delays. This is something that needs to be co
2004-05-21 | Structures | Piling/Drilled Shaft | ROCKFALL MITIGTN(P) | 9 | BOYD | Due to fractures and crevices in the rock socket during the installation of Drilled Shaft number 2 , the temporary steel casing became imbedded in concrete and fell through the top of the rock socket. | Removal of the casing required an underwater salvage operation.
2004-05-21 | Geotechnical | Piling/Drilled Shaft | ROCKFALL MITIGTN(P) | 9 | BOYD | After the initial pour of a substantial quantity of concrete on Drilled Shaft #1 , it was determined that concrete was being lost through karst fractures and cracks in the rock socket. The concrete level was about 3 meters above the rock socket but belo | Subsequently , it was decided that concrete placement should be ceased which resulted in a construction joint. The remaining drilled shaft construction was completed after the concrete had set up and included de-watering of the casing , underwater clea
2004-05-21 | Utilities | Relocation | MAJOR WIDENING(O) | 9 | BOYD | A service pole for an existing sewage pump station at Sta. 4+000 conflicted with the location of the proposed roadway. | The service pole had to be relocated. A Change Order was approved for the cost of relocating the pole and installation of conduit and wiring under the proposed roadway to the pump station.
2004-05-21 | Design | Adjacent Projects | ROCKFALL MITIGTN(P) | 9 | BOYD | An adjacent project was under construction by the same Contractor. Both projects involved a bridge and four-lane sections of US 27 but their contract working days schedules were different. | A Change Order was approved to extend the contract working days on this project by 84 days , while the same number of working days were subtracted from the adjacent project. This revision was made so that these projects could be constructed concurrently
2004-05-21 | Maintenance of Traffic | Communication | MAJOR WIDENING(O) | 9 | BOYD | There were concerns that the public was not informed early enough about changes in traffic patterns that would occur due to construction. | The public should be informed earlier about changes in traffic patterns that may occur due to construction. This could have been accomplished by a newspaper article , radio announcement , or public meeting.
2004-05-21 | Drainage | Elevation | MAJOR WIDENING(O) | 9 | BOYD | After a field investigation , it was determined that the inlet end of the proposed culvert was approximately 0.9 meters higher than the existing channel. This area consisted of an abundance of silt buildup due to the backwater of the river. At the time | Periodic field visits may help alleviate this problem in this type of situation. As it turned out , there was not enough Right-of-Way area to re-grade the inlet of the channel , thus the culvert had to be lowered to match the existing inlet channel. T
2004-05-21 | Geotechnical | Subsurface | ROCKFALL MITIGTN(P) | 9 | BOYD | Several narrow soil-filled (solutioned) crevices and voids were discovered during excavation from approximately Sta. 10+740 to Sta. 10+820. | The crevices and voids were cleaned of soil then refilled with suitable size aggregates. High strength Geotextile fabric Type III was placed over the entire area of the roadway , from shoulder edge to paved shoulder edge , where cavities were found. T
2004-05-21 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 9 | BOYD | An existing water line was encountered near the entrance to Woodland Estates at Sta. 3+700 which had to be addressed before utility relocation could be completed in this area. | The existing water line was cut and capped by Change Order.
2004-05-21 | Design | Special Note | ROCKFALL MITIGTN(P) | 9 | BOYD | The vertical offset tolerance indicated in the £Special Note for Drilled Shafts¥ was ╝-inch per foot , whereas the total maximum allowable offset over the length of the shaft was indicated in the bridge design as 6¥ inches. Consequently , the shaft was | Most of the resulting Change Order cost could have been avoided if the £Special Note for Drilled Shafts¥ clearly defined the £length¥ of the shaft and/or the Rock Socket. To prevent misinterpretations , the £Special Note for Drilled Shafts¥ should specif
2004-05-21 | Drainage | Temporary Drainage | MAJOR WIDENING(O) | 9 | BOYD | The was inadequate drainage established for the construction of a detour. | Approximately 20 meters of 1200mm storm sewer pipe had to be installed and attached to the outlet end of an existing box culvert at Sta. 4+050 for the construction of the detour.
2004-05-21 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 9 | BOYD | On the original plans , it was specified that 20 meters of sheeting was required to properly construct the diversion. However , it was determined that this was insufficient to obtain the desired safety factor. | A Change Order was approved for an additional 17 meters of sheet piling.
2004-05-21 | Design | Plans | MAJOR WIDENING(O) | 9 | BOYD | It was the opinion of the Post Construction Review Team that the plans should have been delivered to the Contractor earlier so they could have had time to develop accurate estimates. | If the plans were prepared two to three months earlier , it would have given the Contractor adequate time to investigate items such as waste sites , etc.
2004-05-21 | Utilities | New Utilities | MAJOR WIDENING(O) | 9 | BOYD | The open trench method was proposed on the plans for the sanitary sewer line installation , but that approach would require closing the road to traffic. | The open trench method was changed to bore and jack in order to keep the road open to traffic.
2004-05-21 | Design | Plans | MAJOR WIDENING(O) | 9 | BOYD | Some of the match lines on the plans did not provide enough overlap with the next sheet , which made them difficult to read. | Plans should be checked to make sure that match lines provide sufficient overlap with the next sheet of the plans.
2004-05-21 | Design | Guardrail | MAJOR WIDENING(O) | 9 | BOYD | The original plans did not include an item for removing and relocating the existing guardrail in connection with the Davis Branch relocation. | Cost Plus Work was used to compensate the Subcontractor for removing and relocating the existing guardrail during the Davis Branch relocation.
2004-05-21 | Environmental | Stream Mitigation | MAJOR WIDENING(O) | 9 | BOYD | An existing channel along the Davis Branch section of KY 1107 was too close to the roadway. | The Contractor was compensated using Cost Plus Work for revising the existing channel to relocate the channel further away from the roadway.
2004-05-21 | Design | Guardrail | MAJOR WIDENING(O) | 9 | BOYD | The original plans did not include an item for removing and relocating the existing guardrail in connection with the Davis Branch relocation. | Cost Plus Work was used to compensate the Subcontractor for removing and relocating the existing guardrail during the Davis Branch relocation.
2004-05-21 | Geotechnical | Mine | MAJOR WIDENING(O) | 9 | BOYD | Upon excavating the proposed cut , it was discovered that a mine opening existed at Sta. 3+560 , Right of centerline. Later , additional smaller mine openings were discovered in the area. | After consulting with the Geotechnical Branch of the Division of Materials , it was decided to place a concrete wall face on the opening and backfill the cavity of the wall with Class A concrete. It was decided to backstow the smaller openings and cap t
2004-05-21 | Structures | Piling/Drilled Shaft | ROCKFALL MITIGTN(P) | 9 | BOYD | When projects involve wet construction of Drilled Shafts , it is crucial to determine plumbness and detect other anomalies such as cavities in the shaft. | Sonar Calipering should be a bid item when a project involves wet construction of Drilled Shafts.
2004-05-21 | Design | Guardrail | MAJOR WIDENING(O) | 9 | BOYD | Guardrail End Treatment Type 7 for the guardrail extension along KY 1107 adjacent to the local golf course could not be constructed with concrete anchors due to space restraints. | The Guardrail End Treatments Type 7 were constructed with metal base plates in lieu of concrete anchors.
2004-05-21 | Design | Guardrail | MAJOR WIDENING(O) | 9 | BOYD | Guardrail End Treatment Type 7 for the guardrail extension along KY 1107 adjacent to the local golf course could not be constructed with concrete anchors due to space restraints. | The Guardrail End Treatments Type 7 were constructed with metal base plates in lieu of concrete anchors.
2004-05-21 | Drainage | Temporary Drainage | MAJOR WIDENING(O) | 9 | BOYD | The plans did not adequately address how to connect existing drainage structures for the Davis Branch Diversion Detour. | Additional quantities of pipe were added via Changer Order to connect the existing drainage structures for the detour.
2004-05-21 | Design | Entrance | MAJOR WIDENING(O) | 9 | BOYD | An entrance was omitted from the plans while others needed revisions. | Cost Plus Work compensated the Contractor for constructing an entrance and parking area at Parcel #15 and revised entrances for Parcels #23 and #26.
2004-05-21 | Traffic | Omission | MAJOR WIDENING(O) | 9 | BOYD | There were insufficient markings setup at both KY 1107 intersections. | Pavement Marker Type V-MW had to be added at both KY 1107 intersections.
2004-05-21 | Design | Guardrail | ROCKFALL MITIGTN(P) | 9 | BOYD | The guardrail design for the inside shoulder right of Station 11+120 was inadequate. | Guardrail End Treatment Type 7 was added via Change Order.
2004-05-21 | Design | Guardrail | ROCKFALL MITIGTN(P) | 9 | BOYD | The guardrail design for the inside shoulder right of Station 11+120 was inadequate. | Guardrail End Treatment Type 7 was added via Change Order.
2004-03-19 | Pavement | Design | NEW ROUTE(O) | 6 | GALLATIN | The pavement design was determined to be inadequate by the District Office with regard to the long term stability of the driving lanes in areas where no rock was encountered or the roadbed material was soft. The original design called for approximately 4 | A decision to change the pavement design was made in consultation with the Division of Construction , the Division of Design , and the Geotechnical Branch. The change involved cement treatment of the top 8¥ of the sub-grade in all areas were no rock wa
2004-03-18 | Construction | Striping Removal | I-CHANGE RECONST(O) | 6 | KENTON | Traffic shifts prior to full depth construction required line removals that caused damage to the surface. | The final surface course was extended beyond that intended in the plans because line removals had damaged the surface to the point where an overlay was needed. Additional quantities of Class 3 Asphalt Surface 12.5 D PG64-22 and Class 4 Asphalt Surface 12
2004-03-18 | Erosion Control Plan | Channel Lining | I-CHANGE RECONST(O) | 6 | KENTON | Class IV Channel Lining (shot rock) was set up on this project. However , no suitable project materials were uncovered for this item. | Therefore quarry rock was necessary to line ditches so Channel Lining Class III was added.
2004-03-18 | Design | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | No quantity for milled rumble strips was established for Laurel County. | Additional length of 1 , 500 meters of milled rumble strips were added.
2004-03-18 | Drainage | Coordination | I-CHANGE RECONST(O) | 6 | KENTON | Perforated Pipe 150-MM quantities were not set up to include the entire length of the project in which the median widening was constructed , which would have required installation of this material on later contracts by sawing through the asphalt placed o | An additional 384 meters of Perforated Pipe 150-MM were added through Change Order. Also , drainage blanket was placed in the median widening areas which needed the appropriate pipe and outlet system installed to ensure no water would be trapped.
2004-03-18 | Drainage | Temporary Drainage | I-CHANGE RECONST(O) | 6 | KENTON | During traffic phases II and III , traffic was shifted across the centerline and across a valley in the pavement which collected water. This situation was not addressed in the original traffic phasing or plans. | Drop Box Inlet Type 12A was added to construct a traffic worthy temporary box top for the median barrier boxes to remove water from the valley in the pavement for traffic safety during these phases. It should be noted that this solution is far from ideal
2004-03-18 | Maintenance of Traffic | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | No quantity for Relocating Temporary Concrete Median Barrier was established for Rockcastle County. | A quantity for Relocating Temporary Concrete Median Barrier in Rockcastle County was added by Change Order.
2004-03-18 | Pavement | Shoulders | I-CHANGE RECONST(O) | 6 | KENTON | Items needed for wedging the outside shoulders were omitted from the pavement summary. | One-thousand , five-hundred and ninety-four tons of DGA Base were added by Change Order for wedging.
2004-03-18 | Pavement | Repair | I-CHANGE RECONST(O) | 6 | KENTON | KY 1329 in Rockcastle County was damaged severely in the vicinity of the project by legal loads hauling project materials to the bridge. | An additional 2 , 295 tons of Mass Concrete was needed to repair base failures while 1 , 515 tons of CL3 Asphalt Surf 12.5 D PG64-22 was added to resurface KY 1329 in the project vicinity because.
2004-03-18 | Design | Adjacent Projects | I-CHANGE RECONST(O) | 6 | KENTON | Based upon the original plans , permanent barrier wall would be placed in a super-elevated section thus complicating the tie-in to a future adjoining project. There were also safety concerns about placing temporary crash cushions in the superelevated se | The beginning of the project was shifted 117 meters south. A Change Order was established that included all items necessary and incidental to extending the full depth pavement. This prevented the permanent barrier wall from ending in a super-elevated se
2004-03-18 | Design | Shelved Plans | I-CHANGE RECONST(O) | 6 | KENTON | The most recent standard drawing for Bridge End Connector A depicts a length of Island Curb which is mandatory at all bridge ends. However , the Standard for this project was an older version which did not depict curb. It is District policy as well as | A supplemental item for Island Curb and Gutter was added through Change Order.
2004-03-18 | Design | Median | I-CHANGE RECONST(O) | 6 | KENTON | Field calculations indicated that 23 , 900 tons of DGA would be needed to complete the median widening for Rockcastle County as depicted in the typical section , but only 13 , 543 tons were set up for Rockcastle. What was originally intended to be const | Much of the asphalt that had been placed in the Rockcastle Median was removed because it wasn't constructed to the ultimate full depth as well as much of the DGA. Realizing that there was going to be a huge over run in Rockcastle , the subgrade elevatio
2004-03-18 | Geotechnical | Top of Rock | I-CHANGE RECONST(O) | 6 | KENTON | The top of rock elevation at Abutment No. 2 was below the bottom of the footer elevation on one side and higher on the other side of the footer. | The existing rock above the bottom of the footer was removed to create a level surface upon which Mass Concrete was placed to bring the solid surface to bottom of footer elevation. This item was paid for per the specifications.
2004-03-18 | Pavement | Median Crossover | I-CHANGE RECONST(O) | 6 | KENTON | Phase II and Phase III temporary pavement installation and removal was required to shift traffic across the superelevated median , but was not included in the paving summary. | An additional 2 , 536 tons of Asphalt Pavement Milling and Texturing were needed for temporary pavement installation and removal.
2004-03-18 | Design | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | Several items used both in Laurel and Rockcastle counties were only shown in Laurel County. | The necessary accounting adjustment to separate and show bid item quantities under their respective county was made via Change Order.
2004-03-18 | Maintenance of Traffic | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | The original contract amount for Pavement Striping-Temporary Paint-150MM was 44 , 614 meters , but based upon field calculations at least 54 , 600 meters were needed. At least one instance was noted in which the lines had been in place for several month | Additional temporary pavement striping paint quantities were added via Change Order.
2004-03-18 | Pavement | Coordination | I-CHANGE RECONST(O) | 6 | KENTON | Station 24+189.73 to 24+273.205 depicted a 25:1 taper of asphalt pavement. Construction of the taper as depicted , would have wasted the previously installed temporary pavement and would require additional work and materials when the next future projec | Instead of installing the taper as depicted , the District constructed full median widening to eliminate wasting the temporary pavement and to provide a squared off boxed out section to begin the next project.
2004-03-18 | Geotechnical | Top of Rock | I-CHANGE RECONST(O) | 6 | KENTON | Rock was encountered higher than anticipated in the plans. | Field measurements of Structure Excavation Solid Rock yielded a higher than original plan quantity of this item.
2004-03-18 | Maintenance of Traffic | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | No quantity for Relocating Crash Cushion was established for Rockcastle County. | A quantity for Relocating Crash Cushion in Rockcastle County was added by Change Order.
2004-03-18 | Erosion Control Plan | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | The Rockcastle River was identified as an outstanding water resource. Consequently , the Department had to work closely with the Division of Water and make commitments above the norm in order to obtain the necessary permits. | Prior to letting , the Department committed to covering all disturbed areas not expecting equipment travel on the river banks with Erosion Control Blanket and all areas expecting equipment travel with stone base within 24 hours of disturbance. As a resu
2004-03-18 | Maintenance of Traffic | Shoulders | I-CHANGE RECONST(O) | 6 | KENTON | During Phase II and III traffic was required to be shifted onto the inside shoulder but the striping and rumble strips were not addressed in the traffic control notes. | The inside shoulder striping and rumble strips were milled up because it was not desirable for traffic to drive on them. An additional 151 tons of CL3 Asphalt Surf 12.5 D PG64-22 were needed to replace the rumble strips.
2004-03-18 | Pavement | Thickness | I-CHANGE RECONST(O) | 6 | KENTON | There were some areas where the depth of asphalt required to establish the plan vertical alignment was more than anticipated. Also there were other areas where additional items were needed to correct cross slopes. | C14 Asphalt Base 25D PG76-22 was added to achieve the plan vertical alignments in these areas and was also used in lieu of leveling and wedging to correct cross slopes.
2004-03-18 | Geotechnical | Piling/Drilled Shaft | I-CHANGE RECONST(O) | 6 | KENTON | Rock was encountered higher than anticipated during drilled shaft excavation. | This resulted in a reduced quantity of Drilled Shaft 1520MM-Common and increased Drilled Shaft 1520MM-Rock.
2004-03-18 | Pavement | Repair | I-CHANGE RECONST(O) | 6 | KENTON | The shoulders needed to be repaired during Phase IA prior to the first traffic shift and barrier wall placement , but this repair work was not included in the paving summary. | An additional 724 tons of Asphalt Pavement Milling and Texturing and 1 , 415 tons of CL3 Asphalt Surf 12.5 D PG64-22 were needed for these repairs.
2004-03-18 | Geotechnical | Elevations | I-CHANGE RECONST(O) | 6 | KENTON | Suitable rock was not encountered on pier 2 at the plan elevation. This was both a fast track job and was in a cofferdam situation adjacent to the River so redesigning and reordering steel to increase the stem length was not a viable option. | Additional excavation was needed and that material was used to refill the undercut from the bottom of footing to the plan footing elevation. Then Mass Concrete was added to create the proper elevation for pier 2. This was the most desirable solution to
2004-03-18 | Pavement | Coordination | I-CHANGE RECONST(O) | 6 | KENTON | Median widening from Station 24+273 to 24+900 was designed to utilize Class 3 Base material. However , this project was an ultimate three lane construction where the median would be subject to mainline traffic in the future. | Class 4 Base was used instead since the ultimate was 3 lane construction and the median would be subject to mainline traffic.
2004-03-18 | Structures | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | Field measurements of Structure Excavation Common yielded a higher than original plan quantity of this item. | An additional quantity of Structure Excavation Common was established via Change Order.
2004-03-18 | Erosion Control Plan | Quantities | I-CHANGE RECONST(O) | 6 | KENTON | There were insufficient quantities of Special Seeding Crown Vetch set up on the plans. Rough calculations based on the proposed disturbed limits throughout the cuts indicate that 54 , 600 square meters would be needed , but only 750 square meters were s | An additional 58 , 104 square meters were added via Change Order 3.
2003-10-24 | Drainage | Omission | RELOCATION(O) | 10 | MORGAN | Geotextile Fabric Type IV was required for backfilling a pipe in accordance with Section 701.03 of the 2000 Edition of the Kentucky Standard Specifications for Road and Bridge Construction. | Geotextile Fabric Type IV was added via Change Order.
2003-10-24 | Design | Quantities | RELOCATION(O) | 10 | MORGAN | A saw dust pile was shown on the plans , but no quantity was set up for its use on the project. | A more thorough review of the plans may have identified this oversight.
2003-10-24 | Design | Evaluations | RELOCATION(O) | 10 | MORGAN | The project plans indicated removal of the existing guardrail in the area of the ramps. However , the existing guardrail was in relatively new condition. | The existing guardrail was reset resulting in a savings for the Cabinet.
2003-10-24 | Drainage | Temporary Drainage | RELOCATION(O) | 10 | MORGAN | The phasing to construct the northbound lane of KY 1006 did not provide drainage for the BillÖs Lane area. | Additional pipe had to be set up to provide drainage while the construction of KY 1006 was being performed. Safeloading was also setup for an existing pipe in the area.
2003-10-24 | Drainage | Sheet Flow | RELOCATION(O) | 10 | MORGAN | A drainage problem occurred during construction. A drainage area of 0.7 acres was added to the existing ditch producing sheet flow. This resulted in an excessive amount of water being directed along Royal Road. | A portion of the drainage was rerouted via standard curb and gutter to the existing drainage ditch at Ramp D-1 Rt. Sta. 6+100. Additional drainage was rerouted , via storm sewer pipe with a drop box and junction box system to the existing drain at KY 19
2003-10-24 | Maintenance of Traffic | Omission | RELOCATION(O) | 10 | MORGAN | There were insufficient items setup on the bridge to delineate the shift in traffic lanes during various phases of construction. | Temporary Striping was added on the bridge to delineate the shift in traffic lanes during various phases of construction. This work was performed in a manner as to not score the concrete riding surface on the bridge.
2003-10-24 | Design | Entrance | RELOCATION(O) | 10 | MORGAN | An entrance to the Heart Center Clinic was omitted from the plans. | Additional items had to be established via Change Order to construct the entrance at the clinic.
2003-10-24 | Utilities | Conflicting Information | RELOCATION(O) | 10 | MORGAN | As built utility plans were not correct causing a conflict between an existing gas line and the proposed water line. | The water line had to be relocated and was rerouted east of the new Esquire Lane and extended approximately 190 meters along the existing Esquire Lane to tie in to the existing water line at Sybille Lane.
2003-10-24 | Traffic | Signals | RELOCATION(O) | 10 | MORGAN | The 8.54 meter strain poles , as specified on the plans , were too short to provide the minimum clearance above KY 1006. | The bases had to be reconstructed for the 9.144 meter strain poles which were furnished by the Department.
2003-10-24 | Traffic | Signals | RELOCATION(O) | 10 | MORGAN | Strain pole bases need to be reconstructed to accommodate different height poles because the bolt pattern is different for different bases. | It was recommended that the bolt pattern be the same for all bases , which would eliminate the need for reconstruction of bases to accommodate different height poles.
2003-10-23 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 10 | POWELL | The original contract did not include a bid item for signs. | The Contractor was reimbursed for signs installed on the project area through Change Order.
2003-10-23 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 10 | POWELL | Unsuitable material was uncovered in cuts at Rt. Sta. 317+00 , Rt. Sta. 327+75 , and Rt. Sta. 335+50. | Due to the rough terrain of the project area and extensive logging , additional geotechnical investigation would have been beneficial. The cut slopes were revised to a 1:1 slope in order to ensure slope stability.
2003-10-23 | Design | Survey | RECONSTRUCTION(O) | 10 | POWELL | Due to dense vegetation obscuring the contours , flown survey data provided incorrect ground elevations at Lt. Sta. 332+50 and the soil hollow at Lt. Sta. 326+50. | Consequently , the mapping and layout of the project area had to be redone. It was recommended that flown survey data from densely vegetated areas be field checked at critical locations or else be performed entirely in field. The incorrect elevations c
2003-10-23 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 10 | POWELL | Large rock crevices at Rt. Sta. 332+00 and a layer of sandstone overlaying shale at Rt. Sta. 329+00 were encountered. | Due to the rough terrain of the project area and extensive logging , additional geotechnical investigation would have been beneficial. These areas required complete removal per the advice of the Geotechnical Branch.
2003-10-23 | Drainage | Ponding | RECONSTRUCTION(O) | 10 | POWELL | It was suspected that standing water on the pavement between Sta. 308+00 to Sta. 321+00 was caused by excessive pore pressure. | A Change Order added additional striping and traffic control to ensure a safe detour during the installation of Fin Drain implemented to address standing water on the pavement. Additional supplemental items used to eliminate the standing water included c
2003-10-23 | Erosion Control Plan | Quantities | RECONSTRUCTION(O) | 10 | POWELL | The quantity of Wire Mesh Slope Protection had been correctly specified on the cross-section sheets , but was listed incorrectly on the Plan Summary Sheet. | It was suggested that bid quantities for Wire Mesh Slope Protection should include a recommended additional 10% to cover the outcrops and depressions. A Change Order was issued to correct the quantity of Wire Mesh Slope Protection.
2003-10-23 | Design | Waste Areas | RECONSTRUCTION(O) | 10 | POWELL | The Contractor requested to use the Cabinet's Right-of-Way from Rt. Sta. 304+00 to Rt. Sta. 315+50 and Lt. Sta. 306+00 to Lt. Sta. 315+00 for waste areas. | A Change Order was needed to accommodate the proposed location of the waste areas. Items were added for Removal and Resetting of Guardrail within the specified zones. All guardrail and ancillary parts: end treatments , posts , offsets , hardware , e
2003-09-18 | Utilities | Pipe Sizes | I-CHANGE RECONST(O) | 11 | LAUREL | The proposed Tapping Sleeve and Valve at Sta. 6+274 were the wrong size. | A Change Order was approved to replace the 150-mm Tapping Sleeve & Valve at Sta. 6+274 with the correct 200 mm unit.
2003-09-18 | Design | Omission | I-CHANGE RECONST(O) | 11 | LAUREL | An existing ditch at the toe of the existing embankment preventing widening of KY 281 had not been shown on the plans. | Quantities of Embankment-In-Place were added to backfill the existing ditch at the toe of the embankment. The ContractorÖs personnel performed the engineering work.
2003-09-18 | Utilities | Quantities | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient quantities of Trenching and Backfilling on the plans to complete the utility work. | Additional Trenching and Backfilling were established by a Change Order.
2003-09-18 | Geotechnical | Unsuitable Material | I-CHANGE RECONST(O) | 11 | LAUREL | Unsuitable material was encountered in the subgrade. | Additional Granular fill Embankment-In-Place was needed to stabilize the subgrade.
2003-09-18 | Maintenance of Traffic | Quantities | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient quantities of items needed to open all 5 lanes to traffic on the asphalt base for a temporary period. | Additional quantities of Temporary Pavement Striping Paint 100-mm were needed.
2003-09-18 | Traffic | Markings | I-CHANGE RECONST(O) | 11 | LAUREL | A bid item for the Pavement Markings for a crosswalk were not included in the plans. | Additional Pavement Marking was provided by a Change Order.
2003-09-18 | Erosion Control Plan | Slope Protection | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient items established for slope protection on the 2 to 1 slopes. | Additional Erosion Control Blanket was needed.
2003-09-18 | Erosion Control Plan | Quantities | I-CHANGE RECONST(O) | 11 | LAUREL | The original plans did not include sufficient erosion control measure to protect the ditches and areas around a box culvert. | Additional quantities of Channel Lining Class II were needed to protect the ditches and areas around the box culvert.
2003-09-18 | Design | Intersection | I-CHANGE RECONST(O) | 11 | LAUREL | During construction the Department decided to reduce the double left-turn lanes at an intersection to a single left turn. | Additional quantities of Standard Barrier Median Type 1 and Type 4 were needed to increase the size of the Barrier Median to reduce the double left-turn lanes to a single left turn.
2003-09-18 | Right-of-Way | Private Utilities | I-CHANGE RECONST(O) | 11 | LAUREL | A sprinkler system had not been located on the plans and was damaged during cutting a ditch. | A Change Order was needed to repair the damaged sprinkler system.
2003-09-18 | Erosion Control Plan | Sodding | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient quantities for Sodding included in the plans. | Additional Sodding was established via Change Order.
2003-09-18 | Design | Grade | I-CHANGE RECONST(O) | 11 | LAUREL | The grades in the plans did not match field conditions. Also , the plans did not address how to tie the new pavement into existing parking lots. | As a result , additional quantities of Class 3 Asphalt Base 19.0E PG 64-22 , Class 3 Asphalt Surface 12.5A PG 70-22 , and DGA Base were used to correct the errors in the plans. Also , Asphalt Pavement Milling & Texturing was utilized to match the cor
2003-09-18 | Drainage | Pipe Sizing | I-CHANGE RECONST(O) | 11 | LAUREL | The culvert pipe at Sta. 5+125.57 had been incorrectly listed in the contract bid items. | The culvert pipe at Sta. 5+125.57 was changed from 900 mm to 1050 mm.
2003-09-18 | Utilities | Quantities | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient items established in the plans to keep the high mast lighting in service. | Additional cable links of various gauges set up via Change Order.
2003-09-18 | Drainage | Existing Pipe | I-CHANGE RECONST(O) | 11 | LAUREL | An existing pipe needed to be extended but no items were included in the plans for this purpose. | An additional Culvert Pipe had to be established to extend the existing pipe.
2003-09-18 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 11 | LAUREL | There was no item established in the original plans for Relocation of Concrete Barrier Wall during various phasing. | An item for Relocation of Concrete Barrier Wall was introduced through Change Order.
2003-09-18 | Structures | Approaches | I-CHANGE RECONST(O) | 11 | LAUREL | The 2-inch PVC pipe through the sidewalk ended at the approach slab. | The PVC pipe through the sidewalk on the approach slab was extended to allow future access to cross the bridges. This was done on all 4 corners of both bridges on the project.
2003-09-18 | Traffic | Omission | I-CHANGE RECONST(O) | 11 | LAUREL | There were insufficient items established for the roadway lighting and a traffic signal. | Additional Wire No.4 for providing Temporary Service to the existing traffic signals during construction and an additional junction box were set up by Change Order.
2003-09-18 | Traffic | Lighting | I-CHANGE RECONST(O) | 11 | LAUREL | Ten Stain Pole Bases were installed in the wrong locations due to errors in the plans. | The ten Stain Pole Bases had to be removed and relocated.
2003-09-18 | Drainage | Ditches | I-CHANGE RECONST(O) | 11 | LAUREL | An existing paved ditch had been undermined causing drainage problems on Ramp A. | The existing paved ditch was removed and the ditch was relined with channel lining.
2003-09-18 | Geotechnical | Unsuitable Material | I-CHANGE RECONST(O) | 11 | LAUREL | Unsuitable subgrade material was encountered during construction. The material included old pavement , which had not been identified during the geotechnical investigation of the project area. | A Change Order was issued to add Granular Embankment and Geotextile Fabric to stabilize the unsuitable subgrade material. The old pavement was removed prior to stabilizing the subgrade with Granular Embankment Fill and Geotextile Fabric Type III.
2003-09-18 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 11 | LAUREL | Several traffic control items were left off the plans. | Crash Cushion Type VI-T , Flashing Arrow , and Lane Closures were added via Change Order.
2003-09-18 | Maintenance of Traffic | Omission | I-CHANGE RECONST(O) | 11 | LAUREL | There were no items established to properly delineate the Temporary Concrete Barrier Walls. | Delineators were established through Change Order.
2003-09-18 | Maintenance of Traffic | Quantities | I-CHANGE RECONST(O) | 11 | LAUREL | Additional quantities were needed for traffic control on the project. | Additional Barricades were provided by a Change Order.
2003-09-18 | Structures | Piling/Drilled Shaft | I-CHANGE RECONST(O) | 11 | LAUREL | The Pennyrile Overpass Bridge had to be redesigned as solid rock was encountered 3 feet below the surface. The bridge was originally designed with steel H-piling. | The pile points were removed and the piles were spliced together to be used on the CSX bridge. The Contractor was reimbursed for the redesign of the piles and the delay.
2003-09-18 | Maintenance of Traffic | Safety | I-CHANGE RECONST(O) | 11 | LAUREL | The Ridgewood community requested additional measures at the Ridgewood Drive entrance to allow safer access. | A Change Order added a third lane and the associated traffic items at the Ridgewood Drive entrance.
2003-09-18 | Maintenance of Traffic | Changes | I-CHANGE RECONST(O) | 11 | LAUREL | There was an impetus to expedite the project. | The time to remove the bridge over Pennyrile Parkway was reduced to three evenings. As a result , traffic had to be maintained by utilizing the ramps , which required additional traffic control measures including lane closures and assistance from local
2003-09-18 | Design | Radius | I-CHANGE RECONST(O) | 11 | LAUREL | Motorists , particularly ones driving larger vehicles , were striking the guardrail during their execution of the turn at Whittington Drive. | A Change Order was approved to modify the radius at Whittington Drive. An additional Drop Box Inlet Type II was also needed to ensure proper drainage due to the redesign of the intersection.
2003-04-24 | Utilities | Delays | CONGESTION MITIGTN(O) | 2 | DAVIESS | Contrary to what the City of Leitchfield had informed the Department , required utility easements for waterline and sewer line relocations had not been obtained when the project was let. | The Contractor had to suspend operations , remobilize to another location , and/or wait for the redesigned material to arrive. A Change Order was needed to compensate the Contractor for the undue delays.
2003-04-24 | Utilities | Relocation | CONGESTION MITIGTN(O) | 2 | DAVIESS | During utility relocations , a power pole that contained timers and provided service to three business signs adjacent to the Right-of-Way was moved by Warren Rural Electrical Cooperative Corporation. | The Contractor had to restore the service , reset poles , and reconnect the signs. A Change Order was issued to compensate the Contractor for the work to restore electrical service to these businesses.
2003-04-24 | Erosion Control Plan | Sodding | CONGESTION MITIGTN(O) | 2 | DAVIESS | Omission of sodding for urban areas often becomes the basis of a Change Order due to citizen complaints and/or inconsistencies between grassy areas. | Sodding of urban areas should be included in the plans initially.
2003-04-24 | Design | Slopes | CONGESTION MITIGTN(O) | 2 | DAVIESS | The slopes should be designed to minimize injuries to pedestrians in case of falls. A steep 2:1 slope or inconsistently varying slopes between sidewalks and parking lots without safety measures in place can be the basis for lawsuits by the property owne | The slopes between sidewalks and parking lots should be designed to minimize injuries to pedestrians in case of falls.
2003-04-24 | Drainage | Pipe Sizing | CONGESTION MITIGTN(O) | 2 | DAVIESS | A culvert pipe extension at Rt. Sta. 2+933.6 on KY 259 was shown as an 1800 MM culvert pipe on the plans but found to be 1500 MM culvert pipe in the field after the material had been ordered by the Contractor. | As a result , the Contractor was paid invoice cost of the material and a unit price was established for 1500 MM Culvert Pipe. The unused pipe was subsequently delivered to Grayson County Maintenance lot.
2003-04-24 | Maintenance of Traffic | Omission | CONGESTION MITIGTN(O) | 2 | DAVIESS | There was no item set up on the plans to delineate the centerline of detours during the project traffic phasing. | A Change Order was issued to establish a pay item for Pavement Markers Type IV A ô BY Temporary.
2003-04-24 | Design | Entrance | CONGESTION MITIGTN(O) | 2 | DAVIESS | The entrance at Sta. 5+738.30 near the Grayson County Hospital (AKA Twin Lakes Regional Medical Center) had been built per the designs. The entrance was constructed on a 12% upgrade and located on the lower side of a superelevated curve , which created | A Change Order was approved to alter the geometry of the entrance at Sta. 5+738.30.
2003-04-24 | Drainage | Omission | CONGESTION MITIGTN(O) | 2 | DAVIESS | A temporary pipe at Sta. 2+900 was supposed to remain in place but not be used for permanent drainage after Phase 1 completion. However , the plans did not address any additional measures that would need to be taken regarding the temporary pipe. | A unit bid price for safeloading the pipe was established , which was determined to be necessary.
2003-04-24 | Maintenance of Traffic | Quantities | CONGESTION MITIGTN(O) | 2 | DAVIESS | Insufficient quantities of Pavement Striping Temporary Paint-100 MM were set up in the contract to properly stripe the detours during the different phases in accordance with Section 112 of the Standard Specifications. | A Change Order added additional quantities , which were used to stripe the detours during the different phases.
2003-04-24 | Design | Borrow/Waste | CONGESTION MITIGTN(O) | 2 | DAVIESS | Due to mathematical errors in the plan earthwork calculations , an additional 12 , 500 cubic meters of borrow material was hauled to the project from a borrow site when it was actually available on-site. | A Change Order was established to compensate the Contractor for additional expenses incurred due to the earthwork miscalculations.
2003-04-24 | Maintenance of Traffic | Quantities | CONGESTION MITIGTN(O) | 2 | DAVIESS | There were insufficient quantities set up in the contract to cover the numerous detours and maintenance traffic phases. | Additional quantities of Pavement Striping-Temporary Removable Tape White & Yellow and Temporary Paint were established via Change Order.
2003-04-24 | Utilities | Stacked Utilities | CONGESTION MITIGTN(O) | 2 | DAVIESS | There was insufficient room to work around an existing sewer main being intersected by a 48-inch steel casing at Sta. 1+184. Additionally , PVC spacers considered incidental to the Steel encasement were unobtainable. | A bid item was established for Modify 1200 MM Steel Encasement. The Contractor cut out a notch in the new encasement , installed the new main , and welded the notched out plate back in place. The more expensive stainless steel spacers for the Steel en
2003-04-24 | Design | Plans | CONGESTION MITIGTN(O) | 2 | DAVIESS | There was a plan error in the cross-sections from Sta. 2+800 to 3+000. | A Change Order was approved to Establish a unit bid price for additional quantities of Embankment-In-Place.
2002-12-12 | Geotechnical | Subsurface | SAFETY-HAZARD ELIM(P) | 3 | WARREN | The subgrade for the majority of the proposed roundabout was saturated and composed of poor soil. Additionally , the extended utility relocation work caused rutting and exacerbated the already poor soil conditions. | The subgrade beneath the pavement area for the entire project was undercut and replaced with fabric wrapped number 2 stone. In addition , the temporary diversion pavement had to be strengthened in order to support traffic due to the saturated subgrade.
2002-12-12 | Design | Radius | SAFETY-HAZARD ELIM(P) | 3 | WARREN | It is difficult for vehicles pulling trailers to remain on the pavement within the roundabout and occasionally their wheels go off the outside edge. | Future roundabout designs should include a curb on the outside edge to provide a barrier for vehicles to avoid.
2002-12-12 | Utilities | Delays | SAFETY-HAZARD ELIM(P) | 3 | WARREN | Utility relocation was unfinished when the Contractor was scheduled to begin work. | Thirty-five days were added to the contract due to utility delays.
2002-12-12 | Design | Intersection | SAFETY-HAZARD ELIM(P) | 3 | WARREN | There were some problems with drivers understanding how to navigate the roundabout. | An extension of the median islands between two-way traffic entering and exiting the roundabout might have increased the traveling public's understanding by more clearly delineating lanes and creating additional separation.
2002-12-12 | Right-of-Way | CAP | SAFETY-HAZARD ELIM(P) | 3 | WARREN | A land owner was promised an entrance pipe during Right-of-Way acquisition , but a CAP note was not included in the plans. | An Entrance Pipe was added at no cost because there were unused quantities of Temporary Ditch and Temporary Pipe that were subtracted to offset the cost of the entrance pipe. All promises made to property owners need to be documented in the plans as per
2002-06-28 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 5 | JEFFERSON | There was insufficient signage at KY 237 and Temporary Ramp C to adequately direct traffic volumes. | A supplemental item , Cost -Plus 3 was set-up on the contract in order to install a left arrow signal head at KY 237 and Temporary Ramp C to better control the flow of traffic.
2002-06-28 | Design | Median | RECONSTRUCTION(O) | 5 | JEFFERSON | Despite the median being raised 1 foot and a crossover being constructed , the plans did not address how to handle the existing median reference markers. | The Contractor was instructed to remove , store , and reinstall the median reference markers and a pay item was established to compensate the Contractor.
2002-06-28 | Construction | Coordination | RECONSTRUCTION(O) | 5 | JEFFERSON | Central Office Division of Construction requested a kick off meeting for this project. | A Change Order was necessary to set up a pay item for a Partnering Workshop in the contract.
2002-06-28 | Maintenance of Traffic | Lighting | RECONSTRUCTION(O) | 5 | JEFFERSON | The plans did not address the need for temporary lighting on the crossovers and slip ramps. | The Contractor was allowed to install No. 2 ASCR Triplex wire for the temporary lighting on the crossovers and slip ramps. The 18 ft. clearance for the wire required by the National Electric Code was unobtainable in some areas due to sag and topographic
2002-06-28 | Geotechnical | Slides | RECONSTRUCTION(O) | 5 | JEFFERSON | A slide occurred on Ramp 3 at Mineola Pike. | Supplemental item , Cost-Plus -2 was added to the contract in order to compensate the Contractor for repairing the slide.
2002-06-28 | Maintenance of Traffic | Safety | RECONSTRUCTION(O) | 5 | JEFFERSON | There were safety concerns regarding traffic being shifted onto the shoulders. | Type 3 Rumble Strips were cut into the overlaid shoulders. This work occurred after the shoulders had be reconstructed and traffic was shifted due to the phasing of the project.
2002-06-28 | Geotechnical | Subsurface | RECONSTRUCTION(O) | 5 | JEFFERSON | Slip ramps and crossovers were already being constructed when a design change was made due to the poor sub-grade conditions encountered. | Cost-plus work was performed because the underdrain pipes had to be re-laid , DGA had to be removed , and the sub-grade had to be re-cut due to the new design.
2002-06-28 | Structures | Omission | RECONSTRUCTION(O) | 5 | JEFFERSON | Epoxy Coated Reinforcement Steel was inadvertently omitted from the contract for the bridges over the Erlanger Service Road on I-275. | Central Office Construction personnel instructed the Contractor to utilize epoxy steel in the superstructure of these bridges , therefore an item was established to accomplish this work.
2002-06-28 | Pavement | Repair | RECONSTRUCTION(O) | 5 | JEFFERSON | There were potholes in the east and west bound lanes of I-275. | Asphalt Patching was added to the project to repair the potholes.
2002-06-28 | Structures | Plans | RECONSTRUCTION(O) | 5 | JEFFERSON | There were concerns regarding the proposed cost of placing Class A concrete on solid rock in the abutments of the northbound and southbound bridges over the Erlanger Service Road on I-275. | A Value Engineering proposal was approved to eliminate using Class A concrete on the solid rock in the bridge abutments. Instead , the Contractor drove steel piles HP 12x53 , which resulted in savings of $40 , 074.65.
2002-06-28 | Structures | Flowable Fill | RECONSTRUCTION(O) | 5 | JEFFERSON | The Contractor had concerns about using Structure Granular Backfill at the bridge end bents as was originally proposed. | An item for Flowable Fill was added to the contract to allow the Contractor to use flowable fill material at the bridge end bents in lieu of Structure Granular Backfill at the Elijah Creek bridges and the bridges over the Erlanger Service Road.
2002-06-28 | Right-of-Way | Fencing | RECONSTRUCTION(O) | 5 | JEFFERSON | The Right-of-Way fence at the Elijah Creek Bridges and the Erlanger Service Road Bridges needed to be removed during construction of the bridges , but the original contract did not address this situation. | After completion of the bridges , the Contractor was instructed to replace the Right-of-Way fence. Supplemental items were added to the contract to remove , store and replace Right-of-Way fence.
2002-06-28 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 5 | JEFFERSON | District personnel suggested that load transfer assemblies are needed on shoulders , but not typically included in design plans , when there are high truck traffic volumes and shoulders are utilized for detours. | A Change Order was necessary to establish items to overlay and replace the shoulders with Load Transfer Assemblies.
2002-06-28 | Design | Omission | RECONSTRUCTION(O) | 5 | JEFFERSON | The original plans did not address the removal and reinstallation of the existing Panel Signs within the gore areas where slip ramps were being constructed. | The Contractor was instructed to remove the panel signs and to reinstall them after the slip ramps were no longer necessary. Supplemental pay items were established to accomplish this work.
2002-06-28 | Erosion Control Plan | Seeding | RECONSTRUCTION(O) | 5 | JEFFERSON | There were concerns about inadequate erosion control to protect the seeding in the immediate area of the median boxes. | Erosion control blanket was added to the project.
2002-06-28 | Structures | Plans | RECONSTRUCTION(O) | 5 | JEFFERSON | There were issues regarding the bridge design specifically the proposed overlay of the existing approach slab , problems associated with the cellular abutments , and the removal and replacement of the wing walls. | A Change Order reduced the quantities of Removing Concrete Masonry , Concrete-Class AAA , Steel Reinforcement-Epoxy Coated , Electrical Conduit , and Machine Prep of Existing Slab while adding pay items for Flowable Fill and Raise Back wall to Grade.
2002-06-28 | Maintenance of Traffic | Shoulders | RECONSTRUCTION(O) | 5 | JEFFERSON | When traffic was shifted onto the blacktop shoulders , the shoulders failed within 36 hours. Upon testing by the University of Kentucky Research team , the sub-base of the shoulders was determined to be inadequate. | The Contractor was instructed by Central Office to remove the existing shoulders and sub-base from station 366+54 to station 578+92 and replace them with rock sub-base and geotextile fabric type IV.
2002-06-28 | Design | Evaluations | RECONSTRUCTION(O) | 5 | JEFFERSON | After inspection by Transportation Cabinet Bridge personnel , it was determined that three bridges needed repairs. | A Change Order established items for overlays on the KY 20 bridge over I-275 and the two I-275 bridges over the Erlanger Service Road. Construction phasing allowed for latex concrete overlays to be constructed with no additional traffic impacts. FHWA co
2002-06-27 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 5 | JEFFERSON | Very small amounts of Traffic Bound Base were setup in the contract for maintenance of traffic. However , it was realized that proper maintenance of entrances would require several applications during the construction process. | Once it was realized that maintenance of entrances would require large quantities of TBB , the Contractor agreed to modify their unit bid price to a lower amount and a supplemental unit price was established for Traffic Bound Base Revised.
2002-06-27 | Design | Quantities | NEW ROUTE(O) | 5 | JEFFERSON | Thee were insufficient quantities of DGA mat and Asphalt Binder. The thickness of the DGA mat and Asphalt Binder were monitored to ensure the required thickness was constructed. | A Change Order established unit prices for additional quantities of these items.
2002-06-27 | Design | Quantities | NEW ROUTE(O) | 5 | JEFFERSON | The plans specified an insufficient quantity of Geotextile Fabric Type III to cover the undercut areas. | The quantity for Geotextile Fabric Type III was increased via Change Order.
2002-06-27 | Environmental | Asbestos | NEW ROUTE(O) | 5 | JEFFERSON | A new 15 inch high-pressure gas main was to be installed and the old gas main removed. At the advice of Louisville Gas & Electric , the Contractor had samples of the coating on the gas main tested for asbestos , which came back positive. | The Contractor hired a qualified third party specialized in removal and disposal of hazardous material to handle removal of the old main. The removal required a seven day buffer before work resumed , which added to the contract days.
2002-06-27 | Utilities | Relocation | NEW ROUTE(O) | 5 | JEFFERSON | The water facility relocation sheets in the plans did not indicate that the existing services to 2950 7th Street at Sta. 105+50 were to be relocated. However , Louisville Water Company (LWC) indicated that these services , which included a 1.5 inch dom | These services were relocated as requested as part of a Change Order.
2002-06-27 | Design | Drainage | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns regarding the functionality , constructability , and cost of the 4 inch perforated pipe underdrain system proposed to provide drainage to the No. 3 Stone. | The 4 inch perforated pipe underdrain system was replaced by Drop Box Inlets Type 13 , which were modified to position the 4 inch core hole level with the bottom of the No. 3 Stone. This method provided adequate drainage of the No. 3 Stone , simplifica
2002-06-27 | Design | Access | NEW ROUTE(O) | 5 | JEFFERSON | Ownership of the property at Sta. 84+00 Lt. changed before the project was let. Prior access to the property was originally from behind the parcel through the previous owner's manufacturing facility. However , this imposed an undo hardship to the new o | It was agreed to provide a 24 foot entrance at the this location , since ownership had changed well in advance of the project letting. Construction of the entrance required removal of the newly constructed curb , gutter , and sidewalk.
2002-06-27 | Construction | Revisions | NEW ROUTE(O) | 5 | JEFFERSON | The project plans required that a lift of Asphalt Base be placed beneath the curb and gutter sections. However , there were concerns regarding the impact upon the project schedule and the cost of multiple mobilizations and demobilizations. | A decision was made to pour the concrete curb and gutter sections at full depth.
2002-06-27 | Drainage | Omission | MAJOR WIDENING(O) | 5 | JEFFERSON | An existing inlet left at station 20+105 that was not shown on the plans had to be reconstructed. | A Change Order was necessary to add pay items for Reconstruct Existing Inlet.
2002-06-27 | Pavement | Quantities | MAJOR WIDENING(O) | 5 | JEFFERSON | Insufficient quantities of Asphalt Curing Seal , Lime , and Blotter Sand were established on the original contract to complete work according to the typical sections. | Additional quantities of Asphalt Curing Seal , Lime , and Blotter Sand were added via Change Order.
2002-06-27 | Utilities | Relocation | NEW ROUTE(O) | 5 | JEFFERSON | Another existing fiber optic line was connected to a pole , which had to be removed as part of the widening of 7th Street. | A Change Order established payment to relocate the fiber optic line to the new utility poles within the right-of-way.
2002-06-27 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 5 | JEFFERSON | After all the temporary stationary signs were installed per contract , it was determined that additional signs were necessary to ensure proper maintenance of traffic and safety of motorists. | A Change Order was approved to establish a unit bid price for an overrun quantity of signs.
2002-06-27 | Traffic | Omission | MAJOR WIDENING(O) | 5 | JEFFERSON | All pavement-marking items were inadvertently omitted from the contract bid items. | A Change Order was necessary to establish unit prices for pavement striping , pavement markers , and thermoplastic pavement markings.
2002-06-27 | Construction | Revisions | MAJOR WIDENING(O) | 5 | JEFFERSON | The catch basin at the Econolodge entrance left at station 0+690 had to be adjusted to the new grade of the frontage road created by the construction revision. | A Change Order was necessary to add pay items for Adjusting Catch Basin.
2002-06-27 | Design | Entrance | NEW ROUTE(O) | 5 | JEFFERSON | The entrance at Sta. 103+45 Lt could not be relocated as proposed in the plans. It contained a massive concrete slab that was not shown on the plans. The slab was approximately 1 foot thick and heavily reinforced. | The entrance at Sta. 103+45 Lt had to be modified instead of relocated. In order to reconstruct the entrance the slab had to be removed.
2002-06-27 | Maintenance of Traffic | Omission | NEW ROUTE(O) | 5 | JEFFERSON | Additional MOT items were needed because water line construction that was to be accomplished during Phase 1 , encroached into the existing northbound driving lane from Sta. 48+00 to 50+00. | A Change Order established the unit bid price and quantities for removal of existing lanes and temporary striping in order to use the existing southbound lanes to accommodate traffic.
2002-06-27 | Utilities | Plans | NEW ROUTE(O) | 5 | JEFFERSON | There were safety and constructability concerns regarding the design of the Manhole Type C Modified at Rt. Sta. 79+84. The original design indicated an excavation depth of approximately 50 feet to the bottom of the existing inverted egg sewer , which wo | The Contractor proposed an alternative design to the MSD that would allow safer and more feasible construction of the manhole. The alternative did not require excavation to the bottom of the sewer and required less sheeting length that was easier to driv
2002-06-27 | Construction | Revisions | MAJOR WIDENING(O) | 5 | JEFFERSON | An approved construction revision on the project involved widening and rehabilitating a frontage road necessary for truck access to a connector road from a Pilot truck stop. A right turn lane from KY 338 to frontage road was constructed for direct access | A Change Order was necessary to add additional quantities of Roadway Excavation , Remove and Replace Right-of-Way Fence , Seeding & Protection , Fabric-Geotextile Type III , and Erosion Control Blanket. Also , items for Overhaul , Standard Curb & G
2002-06-27 | Maintenance of Traffic | Part Width | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns about the steep grades needed to maintain access to entrances after traffic would be shifted to the other side of the road. | The existing roadway was widened 8 feet to the west so traffic could be shifted. This created approximately 14 feet between traffic and new pavement , which provided a smoother transition for maintaining entrances.
2002-06-27 | Design | Phasing | NEW ROUTE(O) | 5 | JEFFERSON | Phasing changes at the intersections of Wathen and Arcade Streets required that signal heads be installed in a temporary configuration before being moved to their permanent location at the conclusion of the project. | A Change Order established a supplemental item to install the signals in a temporary configuration.
2002-06-27 | Traffic | Signals | NEW ROUTE(O) | 5 | JEFFERSON | The plans for this project specified new signals and signal controllers be installed at all three signalized intersections on this project , however no provision was provided for connecting the fiber optics to the controllers. | A Change Order established payment to connect the signals to the fiber optic cables and the fiber optic cables to the fiber optic system at City Hall.
2002-06-27 | Construction | Revisions | MAJOR WIDENING(O) | 5 | JEFFERSON | In order to match the new grade on the frontage road created by the construction revision , the Waffle House entrance (Left station 0+550) and trench drain had to be raised. | Cost plus work was authorized to complete work at Waffle House entrance on the frontage road.
2002-06-27 | Drainage | Elevation | MAJOR WIDENING(O) | 5 | JEFFERSON | The elevations on the pipe sheets did not match the elevations on the cross-sections. | The Contractor was reimbursed for adjusting drainage boxes.
2002-06-27 | Traffic | Signals | NEW ROUTE(O) | 5 | JEFFERSON | Due to a plan error , the location of an existing Steel Strain Pole for the signals at Arcade Street was shown remaining at Sta. 106+90 Lt. However , the same plans showed a commercial entrance for two businesses being constructed between Sta. 106+60 L | It was necessary to construct an island for the pole , move it to the new location , and reconnect all the wiring.
2002-06-27 | Traffic | Signals | NEW ROUTE(O) | 5 | JEFFERSON | The existing electrical services at Berry Boulevard , Arcade Avenue , and Wathen Lane were supposed to be used with new signal system at each intersection. However , an inspection found the existing services to be in very poor condition. | Therefore , a decision was made to rebuild the services at these intersections.
2002-06-27 | Design | Entrance | NEW ROUTE(O) | 5 | JEFFERSON | The final grade for Homeview Drive was lower than the original grade , which caused an entrance at approximate Sta. 10+75 Rt. to be too steep. | The existing entrance was removed and replaced at a safer grade.
2002-06-27 | Utilities | Communication | NEW ROUTE(O) | 5 | JEFFERSON | The plans were designed for Corrugated Metal Pipe (CMP) to be installed for the storm sewer on this project , which drained into a combination sewer maintained by the Metropolitan Sewer District (MSD). After work had begun on the storm sewer , the MSD | The Contractor was delayed for seven days until it was agreed that all storm sewer pipes would be changed to reinforced concrete. Previously laid pipes were removed and the pipes that were already onsite were hauled to the maintenance facility in Middlet
2002-06-27 | Design | Entrance | NEW ROUTE(O) | 5 | JEFFERSON | Due to a plan error involving parcel 14 , the entrance did not align with the existing structures and gated entrance on the property. After the entrance was constructed , the property owner submitted a request to relocate the entrance closer to the loc | The request to relocate the entrance was accommodated via Change Order. The Division of Construction approved the change.
2002-06-27 | Design | Radius | MAJOR WIDENING(O) | 5 | JEFFERSON | Truck traffic was dragging the # 2 Stone from the frontage road right turn lane shoulder onto westbound KY 338 , which caused a traffic hazard. | The # 2 Stone was removed from the right turn lane shoulder at westbound KY 338 and soil was used in it's place.
2002-06-27 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 5 | JEFFERSON | Unsuitable material was encountered on the project during excavation operations. | A Change Order was necessary to add additional quantities of Roadway Excavation and the Contractor was compensated Overhaul for hauling unsuitable material from the project to the waste area.
2002-06-27 | Design | Shelved Plans | NEW ROUTE(O) | 5 | JEFFERSON | Field measurements of entrance pavement confirmed that plan quantities of Cement Concrete Entrance Pavement did not reflect the most recent Standard Drawing. Earlier versions of Standard Drawing No. RPM-150-03 did not include the sidewalk ramps or the ra | A Change Order established an updated unit price for Cement Concrete Entrance Pavement.
2002-06-27 | Maintenance of Traffic | Part Width | NEW ROUTE(O) | 5 | JEFFERSON | Safety concerns existed regarding grade differences between existing roadway and the final grade. Phase I construction included all work from centerline to northbound pavement edge while traffic utilized the remaining portion of 7th Street. However , f | In order to mitigate these problems , the centerline grade profile was raised 6 inches along the length of the project.
2002-06-27 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 5 | JEFFERSON | A pay item for relocating crash cushion for phase II construction was omitted from the proposal. | The pay item for relocating crash cushion for phase II construction was added through Change Order.
2002-06-27 | Drainage | Ponding | NEW ROUTE(O) | 5 | JEFFERSON | The proposed grades where Oleanda and Phyllis Avenue tied into 7th Street were flat creating standing water issues. | Slotted drains were constructed across both intersections and encased in 5 foot concrete aprons. Then , the slotted drains were connected to the proposed slotted drain on the south side of the entrance and tied into the proposed DBI Type 13 on the north
2002-06-27 | Maintenance of Traffic | Phasing | MAJOR WIDENING(O) | 5 | JEFFERSON | The pavement block-out at center lanes adjacent to KY 338 could not be completed according to the traffic phases included in the plans. | The Contractor was reimbursed for additional costs related to pavement block-out at center lanes adjacent to KY 338.
2002-06-27 | Utilities | New Utilities | NEW ROUTE(O) | 5 | JEFFERSON | After all the project paving was complete , it was discovered that several fittings on the water main , which were installed during the project construction , were leaking. The fittings were determined to be defective by a qualified third party hired | To repair the leaks , the newly placed pavement had to be cut in several locations. Seven separate cuts were made between Sta. 112+00 to 117+00.
2002-06-27 | Drainage | Omission | NEW ROUTE(O) | 5 | JEFFERSON | Right of entry to Parcel 10 , a car lot , was obtained prior to the letting. However , the need for effective drainage control had been inadvertently overlooked. | As a result of the settlement agreement with the property owner , the Cabinet agreed to construct a Drop Box Inlet Type 11 at the approximate location of Sta. 62+70.46 Rt. The structure was tied into the 30 inch storm sewer with a 12 inch pipe by cuttin
2002-06-27 | Design | Drainage | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns regarding the potential loss of fines and DGA into the No. 3 Stone during construction. | A decision was made to place a layer of Geotextile Fabric Type IV on top of the No. 3 Stone.
2002-06-27 | Design | Entrance | NEW ROUTE(O) | 5 | JEFFERSON | As a result of an error in the plans , the entrance that was to be constructed at Sta. 82+00 Lt. was incorrectly constructed across a property line and into a fence line. | To correct the error a portion of the existing entrance was removed and the centerline of the entrance was relocated to Sta. 82+00 , which was the original intent of the project.
2002-06-27 | Design | Drainage | MAJOR WIDENING(O) | 5 | JEFFERSON | The original drainage design from station 20+410 to station 22+015 , left and right , was not feasible due to the earth shoulders. The original design utilized asphalt drainage blanket shoulders , but drainage was not set-up underneath the drainage bl | A Change Order was necessary to eliminate the drainage blanket beyond the shoulders and provide pavement drainage by adding perforated pipe. Additional quantities of perforated pipe 100 MM , Non-perforated pipe 100 MM , Drainage Blanket , and Type II-
2002-04-11 | Right-of-Way | CAP | NEW ROUTE(O) | 6 | BOONE | There were several entrances in a row , and according to the design plans the same size entrance pipe would provide sufficient drainage at all these locations. However , the existing pipe at one of the entrances (24) was larger than the proposed pipe ( | The Cabinet could develop a policy requiring privately owned entrance pipes to be replaced in kind with equivalent size pipe. However , if a product that was perceived to be better or more expensive was installed on one property and not the others , th
2002-04-11 | Geotechnical | Subsurface | NEW ROUTE(O) | 6 | BOONE | The existing soil throughout the entire project area was very saturated due to poor drainage. Geotechnical testing was performed during the middle of summer and the report recommended undercutting existing material , but did not mention any need for sta | Based upon a request by District 3 Construction , a Geotechnical Roadway Report addendum recommending a 1-foot granular embankment was issued two weeks prior to letting in November , 2009. However , during construction it became apparent that the 1-fo
2002-04-11 | Drainage | Ponding | NEW ROUTE(O) | 6 | BOONE | Drainage constructed for KYTC projects is often adequate to the Right-of-Way line , but not beyond. This same issue also impacts maintenance efforts. On interstate projects , for example , silt covered ditches are encountered , but they cannot be pr | The Cabinet is doing a better job of obtaining permanent drainage easements. Another possible solution is to construct retention basins. Sometimes , however , designers just need to investigate more thoroughly where water will drain from the Right-of-
2002-02-27 | Geotechnical | Investigation | RELOCATION(O) | 1 | MCCRACKEN | Sufficient geotechnical data and geotechnical notes for the west end of the project area were not included with the plans when this project was let. This was due to property disputes and wetland designations , which prohibited access to the project area | Upon completion of the geotechnical investigation of these areas , the Geotechnical Branch recommended placement of non-erodible Roadway Fill-Granular Embankment wherever these areas were encountered in order to provide a working platform for embankment
2002-02-27 | Structures | Piling/Drilled Shaft | RELOCATION(O) | 1 | MCCRACKEN | The proposed piling method on the Gene Snyder Freeway bridges over Dixie Highway involved use of Pile Points. However , upon review of the functionality of previously installed pile points , it was decided that they were not warranted and a subsequent | The piling method for these bridges was revised to use Steel Piles in lieu of Pile Points. This change was implemented per the recommendation of Division of Construction and resulted in an overall savings , despite the Restocking Fee for the quantities
2002-02-27 | Construction | Public Relations | RELOCATION(O) | 1 | MCCRACKEN | After the sound barrier wall was designed and erected on the north side of the Greenbelt Highway the Cabinet began to receive complaints by affected residents on the south side of the project. | Having no barrier wall on the south side , a Change Order was issued to construct a privacy fence on the south side of Greenbelt Highway from approximate Lt. Sta. 40+30 to 53+44. The decision to construct a 10 foot tall wooden privacy fence required rem
2002-02-27 | Design | Special Note | RELOCATION(O) | 1 | MCCRACKEN | There was an error in the rate for flagging services of Paducah and Louisville Railway Company. The rate was incorrectly listed at $26.30 per hour in the Special Notes in the contract proposal whereas the correct rate was $43.00 per hour. | A Change Order was approved to correct the error and compensate the Contractor for the difference in the cost for P & L flagging services.
2002-02-27 | Traffic | Lighting | RELOCATION(O) | 1 | MCCRACKEN | A High Mast light was installed per the project plans , but due to unforeseen clear distance issues its location was determined by the Division of Traffic to be unsafe. | Consequently , the light was relocated to 61.6 feet right of Ramp 3 Sta. 37+61 and upgraded from 100 feet high to 120 feet.
2002-02-27 | Maintenance of Traffic | Detours | RELOCATION(O) | 1 | MCCRACKEN | Addition traffic control items were needed to ensure the safety of the travelling public as well as to make approved changes to detours and crossovers. | A Change Order was issued to pay for Temporary Pavement Striping and Pavement Markers.
2002-02-27 | Construction | Revisions | RELOCATION(O) | 1 | MCCRACKEN | The plans called for cement stabilization , but the Contractor had access to quantities of Bottom Ash. | The Contractor submitted a Value Engineering proposal to use Bottom Ash in lieu of cement stabilization. The proposal was approved by Central Office contingent upon acceptable values of CBR both for Bottom Ash and the embankment material where Bottom Ash
2002-02-27 | Environmental | Pollution | RELOCATION(O) | 1 | MCCRACKEN | According to the Division of Environmental Analysis , it was warranted to construct a sound barrier wall along Greenbelt Highway at Frenchrone Drive based upon the noise abatement policy. | A Change Order was approved to construct the sound barrier wall at Frenchrone Drive. The sound barrier was constructed using the same design as the wall built along Ramp7 from Sta. 34+30 to 38+70 Lt. Concrete Median Barrier Type 9 , two additional feet
2002-02-27 | Design | Omission | RELOCATION(O) | 1 | MCCRACKEN | Plans for this project indicated two retaining walls be constructed between Ramp 5 and Ramp 9. However , no quantities or design plans were provided for these structures. | A Change Order was written to establish all items necessary to construct these retaining walls.
2002-02-27 | Maintenance of Traffic | Signage | RELOCATION(O) | 1 | MCCRACKEN | Due to the high traffic volumes on Dixie Highway , there were concerns about needing to provide additional warning about ongoing construction to better ensure the safety of motorists and workers. | A Change Order was issued to install two Variable Message Boards.
2002-02-27 | Drainage | Ditches | RELOCATION(O) | 1 | MCCRACKEN | Right and left roadway ditches from Sta.38+00 Greenbelt highway to the end of the project extending towards Mill Creek were wet and needed additional means of drainage control. | Channel Lining Class II was placed in the roadway ditches as an additional means of drainage control.
2002-02-27 | Pavement | Shoulders | RELOCATION(O) | 1 | MCCRACKEN | There were concerns that the shoulder pavement depth as proposed in the plans was inadequate to accommodate future maintenance of traffic and withstand typical expected wear on access controlled highways. | Quantities of PCC Pavement Non-Reinforced were increased so the shoulder depth could be revised from 6 inches to the full depth of 10 inches.
2002-02-27 | Structures | Erosion Control | RELOCATION(O) | 1 | MCCRACKEN | There were concerns about excessive erosion occurring at the bridge end embankment. | Channel Lining Class II was added to seal in the embankment at bridge ends to prevent possible erosion.
2002-01-28 | Geotechnical | Sinkhole | RECONSTRUCTION(O) | 3 | WARREN | One of the sinkholes being addressed with this project was much larger than what was shown on the plans. The sinkhole was further enlarged upon the initial disturbance. Due to the unexpected size of the sinkhole , additional work was necessary to treat | The contract working days were increased due to the additional work necessary for the sinkhole. The sinkhole was stabilized with good results by placing Channel Lining Class III wrapped in Geotextile Fabric Type IV inside it.
2002-01-28 | Maintenance of Traffic | Quantities | MAJOR WIDENING(O) | 3 | WARREN | Two flashing arrows were needed , one at each end of the project , but only one was set up under the original contract. | A Change Order added one additional flashing arrow.
2002-01-28 | Drainage | Omission | RECONSTRUCTION(O) | 3 | WARREN | Geotextile Fabric Type needed to separate coarse aggregate pipes from adjacent soil embankment while backfilling pipes was inadvertently left off the plans. | Geotextile Fabric Type IV was added by Change Order.
2002-01-28 | Geotechnical | Soils | MAJOR WIDENING(O) | 3 | WARREN | A more than expected amount of soft , wet areas were encountered , which is typical of the geologic/soil conditions in Western Kentucky. | A Change Order established additional roadway excavation quantities to undercut these areas.
2002-01-28 | Geotechnical | Soils | MAJOR WIDENING(O) | 3 | WARREN | There were insufficient MOT quantities in the original contract to maintain access to numerous businesses during all phases of construction. MOT quantity overruns are common in densely populated commercial areas. | The quantities of Traffic Bound Base were increased through Change Order.
2002-01-28 | Geotechnical | Sinkhole | RECONSTRUCTION(O) | 3 | WARREN | A section of the road on near the other sinkhole needed additional stabilization. | This section of the road was stabilized using Geotextile Fabric Type III overlain with 2 feet of Crushed Aggregate Size 23 down to the subgrade level.
2002-01-28 | Design | Quantities | MAJOR WIDENING(O) | 3 | WARREN | There were insufficient quantities of Curb & Gutter removal included on the plans. | A Change Order established the additional quantity not included in the original plans.
2002-01-28 | Environmental | Vegetation | RECONSTRUCTION(O) | 3 | WARREN | There were concerns regarding the extremely sensitive environmental nature of the project. | Due to extremely sensitive environmental nature of the project area , a decision was made to use CF4 Erosion Control Blanket to ensure optimal erosion control and promote establishment of vegetative cover on the shoulders.
2002-01-28 | Design | Elevations | MAJOR WIDENING(O) | 3 | WARREN | Numerous elevation errors were encountered at various locations on this project. The elevations indicated on the plans were not representative of actual field elevations. Elevations of the proposed storm sewer pipes varied from 0.15 to 0.36 meters from | As a result , the Contractor had to remove and relay the storm sewer pipe at Lt. Sta. 28+615 - Lt. Sta. 28+681. The drainage boxes , which had been prefabricated , no longer matched the field conditions and had to be replaced. Additional pipe was req
2001-11-30 | Pavement | Type | MINOR WIDENING(O) | 11 | HARLAN | Crushed stone base was preferred by contractor. | Crushed stone base was permitted instead of DGA.
2001-11-30 | Geotechnical | Slides | MINOR WIDENING(O) | 11 | HARLAN | A large slide occurred on this site. | Roadway excavation , horizontal drains , and a fall bench was constructed to remedy the slide.
2001-11-30 | Utilities | Pipe Sizes | MINOR WIDENING(O) | 11 | HARLAN | The 3 inch and 8 inch steel encasements were too small for the 2 inch and 6 inch water lines because of the couplings and other connectors. | The encasements were increased to 4 and 10 inch.
2001-11-30 | Geotechnical | Cut-Slope | MINOR WIDENING(O) | 11 | HARLAN | Several cut slopes had unstable and failed material. | Slopes were revised to remove unstable and failed material back to stable slopes. Additional excavation was also added to remove loose material from adjoining hollow drains.
2001-11-30 | Geotechnical | Cut-Slope | MINOR WIDENING(O) | 11 | HARLAN | Construction on adjacent cut slopes showed that the 1:20 slopes were breaking up and becoming unstable. | The cut slopes were changed to 1/4:1 slopes.
2001-11-30 | Geotechnical | Slides | MINOR WIDENING(O) | 11 | HARLAN | A slide occurred at the stockpile site blocking the Cumberland river. | The contractor was paid cost plus to clear the river , unload other potential slide areas , and repair the river bank. Since suitable areas were no longer available for stockpiling material , the roadway had to be shut down so that all the earthwork c
2001-11-30 | Construction | Contracts | MINOR WIDENING(O) | 11 | HARLAN | Removal of coal by the contractor may lead to liability problems for the department. | A policy concerning coal extraction by the contractors should be established.
2001-11-30 | Construction | Contracts | MINOR WIDENING(O) | 11 | HARLAN | No one was sure how to set up quantities in the contract documents for backstowing of mine openings , as it was a new idea. | Unavoidable.
2001-11-30 | Utilities | Relocation | MINOR WIDENING(O) | 11 | HARLAN | Utilities on the project were relocated about a year late. | There needs to be ways for holding utility companies accountable for relocating their services on schedule.
2001-11-30 | Maintenance of Traffic | Diversions | MINOR WIDENING(O) | 11 | HARLAN | This section of road probably could have been built easier and cheaper if the roadway could have been shut down for construction. However no acceptable detour route was available at the design stage of this project. | When construction started there was an acceptable detour that could have been used to allow road closure.
2001-11-30 | Drainage | Ditches | MINOR WIDENING(O) | 11 | HARLAN | A drainage problem occurred. | Curb and gutter were used to correct this problem.
2001-11-30 | Structures | Phasing | MINOR WIDENING(O) | 11 | HARLAN | Original design called for phased construction of a culvert which would have been complicated and taken a long time to complete. | A temporary detour was constructed to facilitate construction of a box culvert , eliminating phased construction.
2001-11-30 | Design | Relocation | MINOR WIDENING(O) | 11 | HARLAN | Construction would have caused excess delays and inconvenience to KY 2014 and KY 92. | KY 2014 access to US 25E was relocated in conjunction with the contractor's waste area proposal. This shortened KY 2014 approximately 0.4 Mile and provided better access for traffic avoiding construction delays.
2001-11-30 | Geotechnical | Cut-Slope | MINOR WIDENING(O) | 11 | HARLAN | Some slopes had already been constructed at 1:20 and were breaking up. | These slopes were revised to 1/4:1 slopes.
2001-11-30 | Utilities | Existing Utilities | MINOR WIDENING(O) | 11 | HARLAN | Water lines would have been damaged by construction activities. | The waterlines were replaced in areas where waste excavation was being placed on the right of way.
2001-11-30 | Structures | RCBC | MINOR WIDENING(O) | 11 | HARLAN | Unsuitable foundation materials were encountered during excavation for a double barrel culvert. | The material was undercut and replaced with quarry run stone.
2001-11-30 | Maintenance of Traffic | Signage | MINOR WIDENING(O) | 11 | HARLAN | Project construction caused delays and adverse road conditions. | Two variable message signs were added to provide the traveling public with information concerning delays and road conditions.
2001-11-30 | Design | Omission | MINOR WIDENING(O) | 11 | HARLAN | The cost for a partnering facilitator for the initial workshop was not in the bid items. | The cost for a partnering facilitator for the initial workshop was added.
2001-11-29 | Pavement | Design | MAJOR WIDENING(O) | 11 | LAUREL | The asphalt surface course that was called for in the Maintenance of Traffic plans differed from that used on other I-75 widening projects and was more expensive. | A Change Order was approved to change the specification of the course for Maintenance of Traffic from a Class 4 Asphalt Surface 9.5A PG76-22 to a Class 4 Asphalt Surface 9.5C PG76-22. This surface course was confirmed by the Division of Materials to prov
2001-11-29 | Pavement | Design | WEIGH STA REHAB(P) | 11 | LAUREL | The asphalt surface course that was called for in the Maintenance of Traffic plans differed from that used on other I-75 widening projects and was more expensive. | A Change Order was approved to change the specification of the course for Maintenance of Traffic from a Class 4 Asphalt Surface 9.5A PG76-22 to a Class 4 Asphalt Surface 9.5C PG76-22. This surface course was confirmed by the Division of Materials to prov
2001-11-29 | Maintenance of Traffic | Changes | WEIGH STA REHAB(P) | 11 | LAUREL | The location of a Barrier Wall as established by the Traffic Control Plan impeded the construction of a section of the roadway where the tangent sections were short and Concrete Barrier Median was to be poured. | A Change Order for Relocation of Barrier Wall expedited construction of this section of roadway by allowing the entire quantity of Concrete Barrier Median Type 230 to be poured during Phase I Construction. This revision eliminated the need for a Change O
2001-11-29 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 11 | LAUREL | The location of a Barrier Wall as established by the Traffic Control Plan impeded the construction of a section of the roadway where the tangent sections were short and Concrete Barrier Median was to be poured. | A Change Order for Relocation of Barrier Wall expedited construction of this section of roadway by allowing the entire quantity of Concrete Barrier Median Type 230 to be poured during Phase I Construction. This revision eliminated the need for a Change O
2001-09-25 | Design | Guardrail | RECONSTRUCTION(O) | 4 | MARION | The existing guardrail was supposed to remain in place as a part of the original plans. However , due to changes in the road grade subsequent to the application of overlay , the existing guardrail was rendered too low. | As a result , the guardrail had to be removed and hauled away. The guardrail , including appropriate end treatments and connectors to the shoulder bridge piers , was replaced.
2001-09-25 | Construction | Safety | RECONSTRUCTION(O) | 4 | MARION | There were concerns regarding how to safely remove excavated material near the outside driving lane. It was determined that measures needed to be taken to prevent shot rock from entering the roadway as much as possible. | A Temporary Concrete Barrier Wall Type 9M was placed one foot from the outside of the driving lane.
2001-09-25 | Design | Guardrail | RECONSTRUCTION(O) | 4 | MARION | The existing guardrail was supposed to remain in place as a part of the original plans. However , due to changes in the road grade subsequent to the application of overlay , the existing guardrail was rendered too low. | As a result , the guardrail had to be removed and hauled away. The guardrail , including appropriate end treatments and connectors to the shoulder bridge piers , was replaced.
2001-09-25 | Maintenance of Traffic | Quantities | RECONSTRUCTION(O) | 4 | MARION | There was insufficient striping set up to maintain traffic during the various phases of the project. | A Change Order was established for the additional striping needed to maintain traffic both during the application of asphalt courses and until the adjoining projects could be completed.
2001-09-25 | Design | Guardrail | RECONSTRUCTION(O) | 4 | MARION | After a line of guardrail was placed at northbound lane Sta. 130+00 , it was discovered that it did not meet the current standards. The line of guardrail was within a cut area and was supposed to have a Type 3 End Treatment. | The guardrail was extended 150 feet and End Treatment Type 1 was installed to provide for a recovery zone and protection from the roadside hazard.
2001-09-25 | Geotechnical | Cut-Slope | RECONSTRUCTION(O) | 4 | MARION | A rock cut slope between southbound Sta. 64+90 and 69+60 , right of the centerline , was deteriorating due to the high friability of shale. | The cut was stabilized by placing it on a 2:1 slope.
2001-09-25 | Design | Guardrail | RECONSTRUCTION(O) | 4 | MARION | After a line of guardrail was placed at northbound lane Sta. 130+00 , it was discovered that it did not meet the current standards. The line of guardrail was within a cut area and was supposed to have a Type 3 End Treatment. | The guardrail was extended 150 feet and End Treatment Type 1 was installed to provide for a recovery zone and protection from the roadside hazard.
2001-09-25 | Construction | Striping Removal | RECONSTRUCTION(O) | 4 | MARION | Centerline striping on existing open graded surface was removed using a pavement marking eraser instead of the traditional milling machine in an attempt to minimize cost. However , this approach resulted in the deterioration of the open graded surface l | Subsequently , a lane closure was necessary to repair the existing roadway.
2001-09-25 | Construction | Safety | RECONSTRUCTION(O) | 4 | MARION | During construction of the exterior phase , the travelling public would be exposed to drop-offs greater than 4. | The Temporary Concrete Median Barrier Wall Type 9M was relocated to the new pavement in order to protect traffic.
2001-09-25 | Drainage | Elevation | RECONSTRUCTION(O) | 4 | MARION | A Drop Box Inlet Type 1 at Sta. 92+05 was too low due to an oversight during the field inspection. | The Drop Box Inlet was raised to achieve a 4:1 shoulder slope at the box.
2001-09-25 | Pavement | Type | RECONSTRUCTION(O) | 4 | MARION | There was an increase in the Average Daily Traffic (ADT) with regard to the number of heavy trucks. | Asphalt Concrete Base Class CK was used in lieu of Class K. This change was agreed upon by the Division of Design.
2001-09-25 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 4 | MARION | There was insufficient erosion control set up on this project. The erosion control requirements of Design Memo 8-98 were not in effect at the time the plans were made. | Channel Lining Class II and III were added in ditches and around drainage structures at various locations as appropriate. Silt fence was also utilized in strategic areas.
2001-09-25 | Design | Special Note | RECONSTRUCTION(O) | 4 | MARION | The special note for Pavement Subsurface Drainage Outlet had not been included in the project proposal. | Crushed Aggregate Size No. 2 was added to control erosion at the Pavement Subsurface Drainage Outlet.
2001-09-25 | Structures | Elevation Difference | RECONSTRUCTION(O) | 4 | MARION | Temporary Concrete Median Barrier Wall could not be used permanently due to elevation differences in the roadway surface on the northbound and southbound lanes , particularly in the superelevated and transition areas. | Consequently , permanent asymmetrical barrier walls had to be poured in place.
2001-09-25 | Design | Plans | RECONSTRUCTION(O) | 4 | MARION | The typical sections showed removal of the 3 foot inside shoulder on both lanes , which had not been shown on the cross-sections. | A Change Order was approved to correct errors in the cross-sections.
2001-09-25 | Traffic | Omission | RECONSTRUCTION(O) | 4 | MARION | The original project plans were not in accordance with M.U.T.C.D. standards as required by F.H.W.A. | Delineators were added to this project in accordance with M.U.T.C.D. standards.
2001-09-25 | Pavement | Omission | RECONSTRUCTION(O) | 4 | MARION | An item had been left out of the pavement design. | Rut Lessening Modifier was added via Change Order.
2001-09-24 | Erosion Control Plan | Slope Protection | MAJOR WIDENING(O) | 4 | NELSON | There were concerns regarding potential erosion in areas where the slopes were steeper than 1:3. | A unit price for Special Seeding Crown Vetch was established so it could be utilized in areas designated by the Resident Engineer. Crown Vetch is known to spread strong roots , which tend to hold the soil in place.
2001-09-24 | Design | Safety | MAJOR WIDENING(O) | 4 | NELSON | The Crash Cushions Type IX-A , which were originally set up in the plans were not the correct type to be utilized at the median piers for the KY 458 and Murphy Lane overpasses. | Crash Cushions Type IX were added and the Crash Cushions Type IX-A were eliminated.
2001-09-24 | Maintenance of Traffic | Phasing | MAJOR WIDENING(O) | 4 | NELSON | Originally , the eastbound lanes were to be completed through the final surface and the lanes striped using Temporary Removable Tape before the westbound lanes were finished. | The revised plan called for the eastbound lanes to be constructed through the last lift of base and the striping to be done using £Temporary Striping-150 mm Paint¥ while the final surfacing was completed using lane closures after westbound lanes were comp
2001-09-24 | Drainage | Headwalls | MAJOR WIDENING(O) | 4 | NELSON | A decision was made to flatten a slope Lt. Sta. 63+860 instead of constructing a headwall. | A Drop Box Inlet Type 5D was utilized to flatten the slope.
2001-09-24 | Geotechnical | Slides | MAJOR WIDENING(O) | 4 | NELSON | There were five slides with heights between 40Ö to 50Ö that were originally being repaired in a separate project. Due to a lack of sufficient geotechnical information at the time , there were concerns regarding the timeliness of the repairs. | The slide repair work was added to this project in order to speed up the process. All repair work was performed within the Right-of-Way limits of this project. The slides were effectively stabilized with the installation of horizontal and vertical rock
2001-09-24 | Design | Omission | PAVEMENT REHAB-PRK(P) | 4 | NELSON | There were 11 entrances on the project that were not shown on the plans. | Each entrance required entrance pipe , which caused an overrun of this item.
2001-09-24 | Structures | Elevation Difference | MAJOR WIDENING(O) | 4 | NELSON | There were concerns about the overhang on the eastbound and westbound structures not having a consistent depth of approximately 200 mm throughout. In fact , the depth could have been as much as 305 mm if the overhang was constructed per the plans. The | A Change Order was issued to compensate the Contractor for £Overhang Revision¥. The overhang was reworked to have a consistent depth of approximately 200 mm throughout.
2001-09-24 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | Additional quantities were needed to remove all conflicting striping at the crossovers. Also , Pavement Marker Type IV-A were called for in the plans but left out of the bid items. | Additional pavement striping removal and Pavement Marker Type IV-A were added.
2001-09-24 | Pavement | Thickness | PAVEMENT REHAB-PRK(P) | 4 | NELSON | This project was originally set up as an Embankment-in-Place job. The contract plans showed the concrete pavement was 6.5 inches thick and the excavation being to the bottom of this pavement. However , there were overlays added by maintenance in this a | Quantities of embankment in place were deducted from the contract and quantities of roadway excavation were added. The contractor agreed to the same price for each of these bid items.
2001-09-24 | Drainage | Bridge Ends | MAJOR WIDENING(O) | 4 | NELSON | There were insufficient drainage measures established to drain the median due to the installation of the Crash Cushion Type IX-A at the Chaplin River Bridge on the Washington County side of the river. | A 375-mm culvert pipe and a Drop Box Inlet Type 5D were added to drain the median.
2001-09-24 | Structures | Fencing | MAJOR WIDENING(O) | 4 | NELSON | The existing Right-of-Way fence had to be removed to allow the widening of the twin structures over the Chaplin River. While the overall length of the fence was short , eight connections to the structures were required. | A Change Order was issued to establish a price for Right-of-Way Fence Type 2.
2001-09-24 | Pavement | Quantities | PAVEMENT REHAB-PRK(P) | 4 | NELSON | There was an overrun in Crushed Stone Base due to the pavement being 12 inches thick instead of 6.5 inches. | Crushed Stone Base was used in lieu of DGA Base due to availability.
2001-09-24 | Design | Guardrail | MAJOR WIDENING(O) | 4 | NELSON | The guardrail systems on the median side of the bifurcated section were altered as called for by the TCP , but would have been substandard if left in service upon completion of the project. | A Change Order was approved to partially upgrade the guardrail systems on the median side of the bifurcated section with additional guardrail and end treatments.
2001-09-24 | Design | Guardrail | MAJOR WIDENING(O) | 4 | NELSON | The guardrail systems on the median side of the bifurcated section were altered as called for by the TCP , but would have been substandard if left in service upon completion of the project. | A Change Order was approved to partially upgrade the guardrail systems on the median side of the bifurcated section with additional guardrail and end treatments.
2001-09-24 | Structures | Omission | PAVEMENT REHAB-PRK(P) | 4 | NELSON | Deck drains were omitted from the contract bid items. | Deck drains were added to provide proper drainage for the bridge and to enhance safety.
2001-09-24 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 4 | NELSON | Two culvert pipes needed metal end sections in order to meet current safety requirements. | These culvert pipes were extended to 600 MM pipe instead of 475 MM as shown on the contract plans.
2001-09-24 | Drainage | Quantities | MAJOR WIDENING(O) | 4 | NELSON | There were insufficient quantities of Non-perforated Pipe 100-mm to ensure the perforated pipe headwalls could be installed at the correct locations. | A Change Order was approved to increase the quantities of Non-perforated Pipe 100-mm.
2001-09-24 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 4 | NELSON | The depth of Base for the crossover was set up at 3¥ , which was deemed inadequate for the conditions. Also , the design approach angle of the crossovers was 10 degrees , which was too sharp and presented a safety hazard for the motorists having to ne | The depth of Base in the crossover was subsequently raised to 5¥. Additionally , the approach angle was reduced to 3 degrees , which created much safer conditions and allowed the speed limit to be increased to 55 MPH. These changes resulted in more th
2001-09-24 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 4 | NELSON | A Concrete Barrier Wall omission was caused by an oversight. | Concrete Barrier Wall was added via Change Order.
2001-09-24 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 4 | NELSON | The crossover designs were not in compliance with Standard Drawing TSC-248-08 for median crossover case II. | Items for Temporary Crash Cushion and Relocate Crash Cushion were added to construct the crossovers.
2001-09-24 | Construction | Evaluations | MAJOR WIDENING(O) | 4 | NELSON | The bridge decks over Chaplin River were to be removed using hydrodemolition. However , after hydrodemolition had begun , much of the existing concrete deck on the eastbound bridge was found to be in a very poor condition. Many cracks had rapidly deve | A construction cost analysis for a new bridge deck including the Engineering Cost for the redesign of the structures was commissioned and showed only a 13% increase over the original cost taking into account the potential overrun of full depth patching as
2001-07-27 | Maintenance of Traffic | Shoulders | SAFETY-RR SEPARATN(P) | 7 | JESSAMINE | There was insufficient roadway capacity to accommodate the traffic volumes experienced during construction. | The existing unpaved shoulder area was paved to create three lanes of traffic.
2001-07-27 | Traffic | Signals | SAFETY-RR SEPARATN(P) | 7 | JESSAMINE | Traffic jams were occurring due to high volumes of off-ramp and on-ramp traffic coming from I-64. | A Change Order was approved for the installation of five bulb signal heads , trip loops , and all other ancillary items needed to allow protected and permitted left-turn movements.
2001-07-27 | Design | Guardrail | SAFETY-RR SEPARATN(P) | 7 | JESSAMINE | There was insufficient room in the safety zones under the bridge along I-64 to flare out and terminate the guardrail sections. | Four units of Crash Cushion Type VI-T were added.
2001-07-27 | Design | Guardrail | SAFETY-RR SEPARATN(P) | 7 | JESSAMINE | There was insufficient room in the safety zones under the bridge along I-64 to flare out and terminate the guardrail sections. | Four units of Crash Cushion Type VI-T were added.
2001-06-19 | Structures | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | An armored edge was needed at End Bent No. 1 of the C&O Railroad bridge. | A supplemental item was added to install armored edge at End Bent No. 1 of the C&O Railroad bridge.
2001-06-19 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Unsuitable material was uncovered behind the C&O Railroad bridge end bents. | The unsuitable material was removed and replacement backfill was used with Geotextile Fabric Type IV.
2001-06-19 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The plans did not address how to handle the 4 and 6 thermo plastic striping at the proposed median crossovers. | A Change Order was added for Removal of 4 and 6 thermo plastic striping at the median crossovers.
2001-06-19 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The structure granular backfill was not sufficient to replace the unsuitable material that was removed at the C&O Railroad bridge end bents. Additional materials were needed to solve the pavement settlement problem adjacent to the bridge ends. | Supplemental Items for Flowable Fill and Channel Lining Class III were necessary to replace the unsuitable material. The combination of these items were placed together as a backfill in lieu of structure granular backfill and this method worked well to p
2001-06-19 | Structures | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Due to an oversight , dowel bars were needed at the bearing locations of the Ecton Road Bridge. | The dowel bars were added via Change Order and installed at Pier #1. A supplemental item was also added to install epoxy coated steel reinforcement for the dowel bars , which were doweled into the existing concrete to create a fixed connection as shown
2001-06-19 | Erosion Control Plan | Seeding | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | There were concerns that the Seeding and Protection proposed in the plans would not properly ensure vegetation growth in the median because poor soils were encountered. | It was necessary to eliminate quantities of Seeding and Protection and add a supplemental item for Erosion Control Blanket.
2001-06-19 | Structures | Patching | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | There were concerns that the Epoxy Inject Cracks method of repairing damaged concrete on the piers as prescribed in the plans would not work due to the spalling of the concrete face that was encountered during reconstruction of the pier caps. | It was necessary to eliminate all quantities of Epoxy Inject Cracks and add a supplemental item for Concrete Patching-Latex Grout.
2001-06-19 | Maintenance of Traffic | Shoulders | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | There were safety concerns regarding the width of a shoulder to be used for a temporary lane during the temporary detour Phase III of Construction. | Additional CL5 Asphalt Base 1.5E PG64-22 quantities were necessary to widen the shoulder for the temporary detour from the planned width of six feet to a width of seven and a half feet.
2001-06-19 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The original locations of some Guardrail Type A Bridge Connectors and Guardrail End Treatments Type I were to be temporary during Phase III of the Traffic Control Plan. However , the plans did not address how they were to be placed in their permanent lo | Supplemental Items for Remove and Reset Guardrail Type A Bridge Connector and Remove and Reset Guardrail End Treatment Type I were necessary to place these guardrail items in their permanent locations.
2001-06-19 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The contract plans indicated the wrong guardrail termini , Type 1 , for a median situation as per Kentucky Department of Highway Standard Drawing Number RBB-002-07. | Supplemental items for Crash Cushion Type IX-A and Guardrail-Steel W Beam D Face were necessary to place the appropriate guardrail termini for the median situation as per the Standard Drawing.
2001-06-19 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The contract plans indicated the wrong guardrail termini , Type 1 , for a median situation as per Kentucky Department of Highway Standard Drawing Number RBB-002-07. | Supplemental items for Crash Cushion Type IX-A and Guardrail-Steel W Beam D Face were necessary to place the appropriate guardrail termini for the median situation as per the Standard Drawing.
2001-06-19 | Drainage | Ditches | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | A Right-of-Way fence was damaged by sediment due to erosion that occurred along paved ditches that failed to properly transport runoff. | It was necessary to replace the Right-of-Way fence that was damaged.
2001-06-19 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The Traffic Control Plan failed to address how permanent 6 skip lines and edge lines were to be covered during Phases II , III and IV of the TCP. | Supplemental items for Pavement Striping Durable Type I-6 inch Black and Type I-8 inch Black were necessary to temporarily cover the permanent 6 skip lines and edge lines.
2001-06-19 | Design | Omission | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | The plans specified removing material along the westbound shoulder where the pavement had to be widened for a temporary detour. However , there was not a contract bid item set up for this , it had been overlooked. | The unit price of $2.65 per linear foot was established for the item of Trenching , which included the labor , equipment , and materials required to remove the material to create a trench depth of one-half foot and a width of eight feet.
2001-06-19 | Structures | Approaches | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Concrete pavement had broken and settled on the eastbound bridge approaches at Morris Road. Consequently , the replacement of these approaches required additional unanticipated work. | A supplemental item for removal of PCC Pavement was necessary to remove the concrete pavement that had broken and settled. Although the contract did not intend to include dig outs at the bridge approaches , this work was necessary.
2001-06-19 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Type A1 Guardrail Connectors to Bridge were setup in the plans to connect guardrail to the existing type of barrier walls located on the Ecton Road Bridge at Station 82+00 but they were inadequate due to field conditions. | A supplemental item for Guardrail Connector to Bridge Type C was necessary.
2001-06-19 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Type A1 Guardrail Connectors to Bridge were setup in the plans to connect guardrail to the existing type of barrier walls located on the Ecton Road Bridge at Station 82+00 but they were inadequate due to field conditions. | A supplemental item for Guardrail Connector to Bridge Type C was necessary.
2001-06-19 | Maintenance of Traffic | Safety | PAVEMENT REHAB-PRK(P) | 2 | MUHLENBERG | Original quantities of Temporary Concrete Median Barrier Wall Type 9M were insufficient to create an overlap necessary to protect traffic from the blunt end of the barrier wall at the median crossovers. | Additional quantities of Temporary Concrete Median Barrier Wall Type 9M and Relocate Temporary Concrete Barrier Wall were added.
2001-06-18 | Pavement | Thickness | MAJOR WIDENING(O) | 2 | DAVIESS | There were concerns regarding potential pavement damage at the entrance right of Sta. 10+910 due to heavy truck traffic. The original plans called for this entrance to be constructed using PCC Pavement-150 mm Non-Reinforced. | The entrance was constructed with PCC Pavement-250 mm Non-Reinforced in lieu of PCC Pavement-150 mm Non-Reinforced.
2001-06-18 | Structures | Phasing | MAJOR WIDENING(O) | 2 | DAVIESS | The temporary railroad bridge at Sta. 10+300.708 needed repairs as requested by Norfolk Southern. Additionally , there were concerns about the temporary bridge causing conflicts with the construction phasing. | Additional pile bents were constructed to repair the temporary railroad bridge. A containment wall was constructed to accommodate the construction phasing.
2001-06-18 | Design | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | The plans did not address how to tie into the existing curb and gutter at entrance Lt. Sta. 10+418. | A Change Order was established for constructing standard curb and gutter to tie into the existing curb and gutter at entrance Lt. Sta. 10+418.
2001-06-18 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 2 | DAVIESS | Unsuitable rock and mud seams were encountered at Abutments #1 and #2. | Additional concrete and steel reinforcement was needed to lower these Abutments. Consequently , additional quantities of masonry coating were needed to cover the exposed surfaces on the Abutments to 150 mm below the ground line. Geotextile Fabric Type
2001-06-18 | Structures | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | Northfolk Railroad and the Division of Construction requested changes be made to the railroad bridge design. | A Change Order was set up for installation of ╛-inch auxiliary plates between the connection plates and tension flange at various locations.
2001-06-18 | Erosion Control Plan | Seeding | MAJOR WIDENING(O) | 2 | OHIO | The plans called for a Seed Mix containing Bluegrass. However , it was pointed out that Bluegrass does not grow well in this area while KY 31 Fescue does very well. | The grass species in the Seed Mix was changed from Bluegrass (Mix 2) to KY 31 Fescue (Mix 1).
2001-06-18 | Drainage | Coordination | MAJOR WIDENING(O) | 2 | DAVIESS | The plans called for a Temporary Culvert Extension on the Railroad Runaround , Sta. 10+450 RT. However , the Plan Notes designated that the runaround embankment remain in place. | A Change Order was approved to compensate the Contractor for constructing a Permanent Pipe Extension.
2001-06-18 | Structures | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | There were concerns about drainage on the railroad bridge. | Eight additional stainless steel plates were installed from the deck to the barrier wall to ensure proper drainage.
2001-06-18 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 2 | DAVIESS | Various soft locations containing materials unsuitable for presplitting were encountered at Left and Right of Sta. 10+000 to Sta. 10+070. | The various soft locations were undercut and 2:1 back slopes were constructed in lieu of presplitting.
2001-06-18 | Structures | Guardrail | MAJOR WIDENING(O) | 2 | DAVIESS | There were concerns regarding the proposed guardrail at the railroad bridge. The original plans called for Single Face , Double Strength Guardrail installed along the front of the pier. | A Change Order revised the guardrail type to Guardrail Connector to Bridge End Type A , which instead connected directly to the pier. This change resulted in savings and was authorized by the Division of Construction.
2001-06-18 | Design | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | An item for the final Pavement Striping was not included in the original plans. | Pavement Striping was added to the project via Change Order.
2001-06-18 | Geotechnical | Investigation | MAJOR WIDENING(O) | 2 | OHIO | Based upon the outcomes of test excavations and recommendations made by the Geotechnical Branch , the decision was made to undercut the entire project. | As directed by the Geotechnical Branch , undercutting was performed and 18¥ of Coarse Aggregate underlain with Geotextile Fabric Type III and overlain with Geotextile Fabric Type IV , was added to the length of the project.
2001-06-18 | Structures | Beams | MAJOR WIDENING(O) | 2 | DAVIESS | The top and bottom flange of ten beams on Span 1 did not match the skew of the bridge. | The top and bottom flange of these beams were coped to match skew of bridge. Consequently , it was necessary to repaint the beam ends to prevent rust.
2001-06-18 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | There were no items set up to direct traffic from the new roadway through the tunnel during an approved control change. | A Change Order was established to install temporary guardrail to direct traffic from the new roadway through the tunnel.
2001-06-18 | Drainage | Temporary Drainage | MAJOR WIDENING(O) | 2 | DAVIESS | There were inadequate mechanisms in the plans to provide drainage at Sta. 10+834 during phase construction. | A Change Order allowed the pipe at Sta. 10+834 to be extended in order to provide sufficient drainage during construction.
2001-06-18 | Geotechnical | Top of Rock | MAJOR WIDENING(O) | 2 | DAVIESS | The elevation of the existing rock line at the bottom of the footing on Abutment 1 was lower than what the plans indicated. | A Change Order was approved to add Mass Concrete in order to raise the elevation of the bottom of footing on Abutment 1 to plan grade.
2001-06-18 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 2 | OHIO | An 8-inch utility water main located Lt. Sta. 189+80 had not been shown on the plans. The thrust block of the existing line was in the area of two proposed 48-inch equivalent pipes leaving inadequate room to do the work. | A Change Order was issued to relocate an 8-inch utility water main.
2001-06-18 | Pavement | Approaches | MAJOR WIDENING(O) | 2 | DAVIESS | Cracks had precipitously developed under heavy truck traffic at the north and south sections of the concrete inlay on Nicholasville Road. | A Change Order was approved to resurface the north and south sections of the concrete inlay on Nicholasville Road. The repair required two lane closures and mobilization.
2001-06-18 | Design | Shoulders | MAJOR WIDENING(O) | 2 | DAVIESS | There were concerns about the considerable truck traffic from the quarry , concrete , and asphalt plants as well as stores in the area damaging the shoulder pavement. | Due to the heavy truck traffic the decision was made to pave the shoulders at full depth to minimize the future damage caused by truckloads on the shoulder pavement.
2001-06-18 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 2 | DAVIESS | There were discrepancies between the plans and the bid items in the size and reinforcement of timber needed for the bridge. | A Change Order was issued to correct the discrepancies based on the specifications in the plans.
2001-06-18 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 2 | OHIO | The Contractor performed all work involving the relocation of utility lines owned by Bell South as per the plans. However , the elevations provided by Bell South were incorrect causing the Contractor to damage the lines. | A Change Order was approved to compensate the Contractor for the relocation and subsequent repair of the utility lines.
2001-06-18 | Design | Quantities | MAJOR WIDENING(O) | 2 | DAVIESS | The quantity of Railroad Ballast set up in the plans was sufficient for the Detour but not for the Railroad Detour tie-ins and the Permanent Structure. | A Change Order was issued to increase the quantity of Railroad Ballast to cover the Railroad Detour tie-ins and the Permanent Structure.
2001-06-18 | Erosion Control Plan | Slope Protection | MAJOR WIDENING(O) | 2 | DAVIESS | There were concerns regarding potential erosion at the outlet end of a box culvert Right of Sta. 10+536 to Right of Sta. 10+600 due to the steep slope of the embankment. | A gabion retaining wall was constructed at the outlet end of the box culvert to alleviate any impending erosion.
2001-05-03 | Geotechnical | Embankment Stabilization | PAVEMENT REHAB-INT(P) | 9 | BATH | The geotechnical notes specified one foot of Roadway Fill-Granular Embankment to be used to stabilize the areas referenced in the previous issue. These areas were within designated wetland areas and were very swampy. | A decision was made to use an additional two feet of select granular embankment material to stabilize the area. This issue and solution need to be considered for future projects in this type of area.
2001-05-03 | Geotechnical | Omission | PAVEMENT REHAB-INT(P) | 9 | BATH | Geotextile Fabric Type III was specified beneath the Roadway Fill-Granular Embankment from Sta. 635+00 to Sta. 669+00 and from Sta. 677+00 to Sta. 683+00 per the geotechnical notes. However , a contract bid had been inadvertently left out from the plans | A Change Order was issued to establish a unit price for Geotextile Fabric Type III.
2001-05-03 | Drainage | Quantities | PAVEMENT REHAB-INT(P) | 9 | BATH | There was a deficiency in the quantity of C3 bar needed in the sidewalls of a 5'X5' RCBC at Sta. 678+70. Only half the required quantity was set up in the plans. | A Change Order was approved to add the necessary quantities of C3 bar.
2001-05-03 | Structures | Piling/Drilled Shaft | PAVEMENT REHAB-INT(P) | 9 | BATH | There were concerns about achieving minimum penetration without overstressing the 14-inch concrete piles in the structure at Sta. 650+82. | Steel H-piles were substituted for the 14-inch concrete piles. The Design Consultant , the Geotechnical Branch , and the Division of Bridge Design concurred that HP 14X73 steel piles as shown on Standard Drawing No. BPS-009.05 could be substituted for
2001-05-03 | Structures | Piling/Drilled Shaft | PAVEMENT REHAB-INT(P) | 9 | BATH | Extremely unpredictable soil conditions on this project caused great variation in lengths of steel piling required to obtain acceptable bearing values for the structures. | A Change Order was established to reimburse the Contractor for the additional lengths of steel piling required and the increased costs for splices.
2001-05-03 | Design | Safety | PAVEMENT REHAB-INT(P) | 9 | BATH | There were safety concerns regarding the culvert on KY 996 at Sta. 42+15. | A Change Order was approved to establish quantities and unit bid prices for Guardrail and Terminal Section Type 1 to be used at the culvert. These were items not included in the plans but were required by this project.
2001-04-05 | Pavement | Approaches | MAJOR WIDENING(O) | 12 | FLOYD | There was an uneven transition between the new pavement on US 62 and the old pavement at Sta. 47+00. | Additional Asphalt Pavement Milling was needed.
2001-04-05 | Design | Special Note | BRIDGE REPLACEMENT(P) | 12 | MARTIN | A note about clearing and grubbing was misinterpreted by the Contractor. The note was meant to supersede the spec for clearing from Right-of-Way line to Right-of-Way line. In this case , only the disturbed limits were supposed to be cleared. | The Contractor should have known that special notes supersede specs. Additionally , the note itself would have been clearer if it had began with the phrase , £Contrary to the specs¥.
2001-04-05 | Design | Quantities | MAJOR WIDENING(O) | 12 | FLOYD | The original plan quantity of DGA Base was insufficient to provide an adequate base for asphalt quantities needed to construct safe detours and paved entrances during construction. Additional quantities of Traffic Bound Base were also needed to provide s | Additional quantities of DGA Base and Traffic Bound Base were added.
2001-04-05 | Utilities | Omission | MAJOR WIDENING(O) | 12 | FLOYD | There was a conflict with a force main that was not shown on the plans. | A Change Order was approved to reimburse the contractor for downtime caused by the conflict. One additional working day was added by this Change Order.
2001-04-05 | Design | Entrance | BRIDGE REPLACEMENT(P) | 12 | MARTIN | An existing county road that tied into the project ran directly into a creek , but instead of correcting this situation the plans left the approach unchanged. | This situation should have been addressed as part of this project. It's typically Cabinet policy to try to minimize possible environmental issues such as this.
2001-04-05 | Design | Shelved Plans | MAJOR WIDENING(O) | 12 | FLOYD | A proposed Guardrail End Treatment Type 4 did not conform to the revised safety standards. | The proposed Guardrail End Treatment was replaced with a Type 1 Crash Cushion.
2001-04-05 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | MARTIN | Soft material was encountered at or near the finished grade elevation at Singleton Road sta. 40+94 to 42+55. | The material was undercut and excavated in order to stabilize this area.
2001-04-05 | Construction | Subsurface | MAJOR WIDENING(O) | 12 | FLOYD | The old subgrade was not capable of withstanding the load imposed by construction equipment. | The old subgrade was undercut and backfilled with suitable Embankment-in-place material to stabilize to the ground.
2001-04-05 | Design | Specifications | BRIDGE REPLACEMENT(P) | 12 | MARTIN | A bid item for removing guardrail was omitted due to a lack of knowledge regarding the specs. It was assumed that a bid item for removal of a structure included the guardrail. However , guardrail removal requires a separate pay item. | Designers should have a better general knowledge of KYTC specifications and the Cabinet staff should help educate them while performing QA/QC reviews of consultant designs.
2001-04-05 | Geotechnical | Soils | BRIDGE REPLACEMENT(P) | 12 | MARTIN | The original base material included in the plans was crushed stone base. However , due to the presence of New Albany Shale , which has acidic runoff , there were concerns regarding potential drainage into the subgrade material. | The base material was switched to dense grade aggregate at same cost to better seal off the New Albany shale and prevent drainage into the subgrade material.
2001-04-05 | Pavement | Repair | MAJOR WIDENING(O) | 12 | FLOYD | The old US 231 had poor pavement material. The pavement was comprised of conflicting courses of concrete and asphalt. Due to excessive undercutting of the existing roadway at several locations , additional measures were needed to achieve the design thi | Additional quantities of Embankment-In-Place and Asphalt Concrete Base Class K were added.
2001-04-05 | Drainage | Ditches | MAJOR WIDENING(O) | 12 | FLOYD | The old US 231 had poor drainage control. | Additional quantities of Channel Lining Class II and Geotextile Type IV were added for ditch and channel protection.
2001-04-05 | Traffic | Safety | MAJOR WIDENING(O) | 12 | FLOYD | The Division of Traffic required safety enhancements at the intersection of KY 69 and US 231 before the road was opened to traffic. | A Change Order was approved to install a traffic signal system at the intersection.
2001-04-05 | Construction | Delays | MAJOR WIDENING(O) | 12 | FLOYD | There were concerns about protecting the K Base from weather and traffic during the winter months , until the surface course could be completed. | Additional quantities of Seal Coarse were added to protect the K Base during the winter months.
2001-04-05 | Erosion Control Plan | Omission | BRIDGE REPLACEMENT(P) | 12 | MARTIN | There was no erosion control item in the plans to help minimize stream disturbance during construction of structures on project. The Contractor needed a means to temporarily divert the stream away from the work area. | A 4 millimeter plastic liner was used to create a temporary diversion ditch channel. This method worked really well in this instance and was recommended for use elsewhere. However , the Division of Construction or Design needs to address if this should
2001-04-05 | Drainage | Omission | MAJOR WIDENING(O) | 12 | FLOYD | Additional items were needed to provide proper drainage at the 12th Street approach due to the planned elimination of the existing drainage ditch. Also an existing Drop Box Inlet had deteriorated and needed replacement. | Two Drop Box Inlets Type 7 were added to address these issues.
2001-04-05 | Structures | Quantities | MAJOR WIDENING(O) | 12 | FLOYD | Quantities of £Steel Reinforced-Epoxy Coated¥ were not estimated appropriately for the structure at Sta. 153+57. Consequently , the provided quantity was not sufficient. | Additional quantities of £Steel Reinforced-Epoxy Coated¥ were added.
2001-04-05 | Structures | Erosion Control | MAJOR WIDENING(O) | 12 | FLOYD | There was insufficient erosion and silt control set up for the bridge construction at Muddy Creek. | Channel Lining Class II was added for erosion and silt control at Sta. 128+00.
2001-04-05 | Structures | Erosion Control | BRIDGE REPLACEMENT(P) | 12 | MARTIN | There were no erosion control mechanisms set up in the original plans to minimize potential scour around the bridge piers at sta. 167+50 and 269+68. | Cyclopean stone rip rap was added via Change Order to prevent scour around the piers.
2001-04-05 | Structures | Omission | MAJOR WIDENING(O) | 12 | FLOYD | Concrete and granular backfill for an Approach Slab and Structure Granular Backfill for the abutment type structure at the North Fork of Muddy Creek located at Sta. 171+73.80 were not included in the plans. | Additional quantities of concrete and granular backfill and Structure Granular Backfill were added.
2001-04-05 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 12 | FLOYD | Unstable foundation was encountered during construction of pipe trenches from Sta. 180+98 to 200+33. The available backfill material on site was unstable and could not be used. | Undercutting and backfill material were used to stabilize the pipe trenches.
2001-04-05 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | MARTIN | Material at the bottom of the pipe trench at stations 75+80 , 339+20 , and 343+05 was not stable. | The unstable material was removed and replaced with suitable material. Undercutting that was less than two feet was setup per Standard Specifications Section 701.05 , while a price for undercuts deeper than two feet was negotiated with the Contractor.
2001-04-05 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | MARTIN | Soft material was encountered at or near finished grade elevation from sta. 305+00 to sta. 314+50. | The soft material had to be removed and additional undercutting was needed to stabilize the roadbed with suitable fill material. The wet areas encountered were unforeseeable.
2001-04-05 | Environmental | Underground Tank | MAJOR WIDENING(O) | 12 | FLOYD | The quantity of sludge that needed to be removed and disposed from underground storage tanks was in excess of the quantities set up in the plans. | Additional quantities for this work were established. After the tank removal , additional £Progressive Soil Analysis of Tank Pit¥ was performed to ensure removal of all contaminated earth material prior to backfilling of the tank pit in accordance with
2001-04-05 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 12 | MARTIN | The plans did not address a necessary waterline relocation at King Cemetery Road. | A lump sum price for full compensation of all labor , equipment , materials , and incidentals necessary to perform the extra work including excavation , relaying pipe , and mobilization was agreed upon.
2001-04-05 | Structures | Piling/Drilled Shaft | MAJOR WIDENING(O) | 12 | FLOYD | There were three proposed structures on this project. Two of the three structures called for pre-stressed concrete piles in the bid proposal plans whereas the award plans specified steel piles. | The decision was made to change the piles in all three structures to steel piles , which resulted in substantial savings.
2001-04-05 | Drainage | Elevation | MAJOR WIDENING(O) | 12 | FLOYD | A Drop Box Inlet was installed in the superelevation section of the road causing drainage problems to a property owner. | The solution involved raising the grade and installing a sidewalk on a cost plus basis.
2001-04-05 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | MARTIN | Soft material was encountered near the finished grade elevation from sta. 389+80 to sta. 392+30. | A Change Order was established to remove the soft material and stabilize the roadbed with suitable material.
2001-04-05 | Erosion Control Plan | Quantities | MAJOR WIDENING(O) | 12 | FLOYD | There was insufficient control of silt runoff throughout the project. | Additional quantities of silt fence were needed at various locations.
2001-04-05 | Maintenance of Traffic | Timing | MAJOR WIDENING(O) | 12 | FLOYD | Additional items were needed for Maintenance of Traffic on US 231 where cross-drains were installed across the mainline. It would have been difficult to quantify this need during the design phase because it only became necessary in order to complete the | Leveling & Wedging were added for Maintenance of Traffic on US 231.
2001-04-05 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 12 | MARTIN | A waterline at Left Station 48+00 along a frontage road was shown on plans but did not include any relocation information. | The roadway Contractor supplied an estimate to relocate the existing waterline providing service to properties along frontage road that was approved by the Department.
2001-04-05 | Drainage | Drop Box Inlets | MAJOR WIDENING(O) | 12 | FLOYD | Two existing drop boxes on mainline US 231 at Sta. 51+50 and Sta. 52+25 were found to be deteriorated once exposed. | These two drop boxes were replaced via Change Order.
2001-04-05 | Structures | Approaches | BRIDGE REPLACEMENT(P) | 12 | MARTIN | There were concerns about approach settlement issues with the bridges on this project. | The first bridge on the project at STA. 167+50.00 included approach slabs and there has been no settlement at this location. The Contractor and some district staff advised that a good formula for avoiding the settlement bump is to use buried approach sla
2001-04-05 | Geotechnical | Top of Rock | BRIDGE REPLACEMENT(P) | 12 | MARTIN | The Contractor encountered mud seams during footer excavation of bridge piers at sta. 167+50. | The Contractor excavated the mud seams to reach solid rock and then drilled test holes to verify the mud seams had been completely removed from footer area. Mass concrete was added to fill the excavated areas to the footer elevation.
2001-04-05 | Geotechnical | Unsuitable Material | BRIDGE REPLACEMENT(P) | 12 | MARTIN | The area from sta. 43+00 to sta. 78+00 was marshy and wet. | Type IV fabric was needed to stabilize the area for rock fill material.
2001-04-05 | Construction | Safety | MAJOR WIDENING(O) | 12 | FLOYD | There was nothing to prevent children from entering the job site from an adjacent baseball field and swimming pool while a retaining wall was being constructed along US 231 from Sta. 190+31.79 to 195+69.57. | A Security Fence was installed to protect and prevent children from entering the job site.
2001-04-05 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 12 | MARTIN | A waterline was shown on the plans but it was not addressed how to reroute it to install a proposed culvert. The utilities were supposed to be relocated before construction began but either this line was missed or there might have been a change to the cu | Three hundred feet of pipe and a tie in valve were added to reroute the existing line to avoid the culvert location. If there were changes to the culvert design the plans should have been checked for utility impacts. A Constructability review might have
2001-04-05 | Utilities | Inaccurate Location | MAJOR WIDENING(O) | 12 | FLOYD | There were additional conflicts with utility locations. The invert elevation of the storm sewer cross-drain was shown lower than the force main , which was not shown on the plans. Also , several other pipes were shown at higher elevations in the plans | Three additional working days were added to correct these issues.
2001-04-05 | Design | Sight Distance | MAJOR WIDENING(O) | 12 | FLOYD | A retaining wall located along US 231 from Sta. 192+50 to 196+50 was too close to the roadway , thereby imposing sight distance limitations. | A Change Order was authorized for the modification of the retaining wall on a cost plus basis.
2001-04-05 | Design | Grade | MAJOR WIDENING(O) | 12 | FLOYD | There were difficulties achieving the proposed grades from the plans. | Additional Asphalt Pavement Milling was performed as directed by the Cabinet , starting from the gutter line in order to establish the grades set up in the plans.
2001-03-29 | Design | Safety | MAJOR WIDENING(O) | 8 | ROCKCASTLE | If the entrance culvert at approximate station 52+60 Right had been installed as per plan , there would have been a large ditch which would have been a safety hazard to the traveling public and pedestrian residents of the La Hacienda Apartment complex. | Additional quantities of entrance pipe were established for extending the culvert to the edge of the river bank.
2001-03-29 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 8 | ROCKCASTLE | Seeding and Protection quantities for slopes were left off the original contract plans. | Quantities for Seeding and Protection were added via Change Order. This issue likely could have been prevented by a more thorough review of the plans , possibly a Constructability Review.
2001-03-29 | Traffic | Safety | MAJOR WIDENING(O) | 8 | ROCKCASTLE | There were safety concerns regarding the approach at the west end of the project. The proposed design did not sufficiently accommodate the increasing traffic from the ongoing development in the areas adjacent to the approach and that of heavy trucks from | A Change Order was approved to improve the approach by relocating the beginning point of construction from Sta. 4+420 to 4+249 and extending the westbound truck lane from Sta. 4+525 to 4+340. This Change Order included all quantities of materials for asp
2001-03-29 | Traffic | Safety | MAJOR WIDENING(O) | 8 | ROCKCASTLE | There were safety concerns regarding the approach at the west end of the project. The proposed design did not sufficiently accommodate the increasing traffic from the ongoing development in the areas adjacent to the approach and that of heavy trucks from | A Change Order was approved to improve the approach by relocating the beginning point of construction from Sta. 4+420 to 4+249 and extending the westbound truck lane from Sta. 4+525 to 4+340. This Change Order included all quantities of materials for asp
2001-03-29 | Design | Excavation | MAJOR WIDENING(O) | 8 | ROCKCASTLE | The plans proposed sodding an area that served as an existing parking lot. However , there were insufficient quantities of topsoil and excavation to remove the old parking lot surface. | The Cabinet decided to simply repave the parking lot because it was less expensive than completing the work per plan , which would have required the use of Change Orders. This issue may have been identified by a Constructability Review.
2001-03-29 | Utilities | Plans | MAJOR WIDENING(O) | 8 | ROCKCASTLE | There were concerns regarding the quality of the sewer line plans on the subject project. The proposed pipe bursting would have left the sewer line at the same existing elevation approximately 25 feet below grade , which would make future maintenance by | The Prime Contractor presented KYTC personnel , City of Hazard officials , and the consulting sewer line engineer with a suggestion to replace the proposed pipe bursting with a directional bore and some additional sanitary sewer manholes. This method p
2001-03-29 | Structures | Handrail | MAJOR WIDENING(O) | 8 | ROCKCASTLE | Upon installation of the bridge railing systems , it was realized that the height of the railing was did not meet pedestrian safety standards. | A top rail was added to the originally designed rail system , which added approximately 10 inches of height and greatly increased pedestrian safety. Also , additional quantities of epoxy coated steel reinforcement were added in order to raise the plint
2001-03-29 | Utilities | Plans | MAJOR WIDENING(O) | 8 | ROCKCASTLE | During utility relocations , sidewalks and patios that were not spotted on the utility plans we damaged. | The sidewalks and patios were repaired. There should have been a note in the utility plans for repairing the disturbed area. It is important to make sure whatever is impacted by utility work is accounted for in the plan quantities.
2001-03-29 | Materials | Asphalt Mixtures | MAJOR WIDENING(O) | 8 | ROCKCASTLE | The Superpave Mixtures for the Asphalt Base and Surface courses of the mainline did not meet the requirements of Special Note for Fiber Reinforced Superpave Mixtures dated 9/13/99. | A Change Order was established per the direction of the State Highway Engineer to revise the Superpave Mixtures to include polyester reinforcement fibers.
2001-03-29 | Materials | Asphalt Mixtures | MAJOR WIDENING(O) | 8 | ROCKCASTLE | The Superpave Mixtures for the Asphalt Base and Surface courses of the mainline did not meet the requirements of Special Note for Fiber Reinforced Superpave Mixtures dated 9/13/99. | A Change Order was established per the direction of the State Highway Engineer to revise the Superpave Mixtures to include polyester reinforcement fibers.
2001-02-23 | Structures | Quantities | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Fabric Geotextile Type III and Backfilling Undercut , items integral to the proposed Bridge End Stabilization , were left out of the contract. | Bid prices for these items were established via Change Order.
2001-02-23 | Pavement | Thickness | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Difficulties arose while trying to pave the roadway and shoulders to the profile grades specified in the plans because the depth of asphalt in certain areas was as high as 26. | A Change Order was approved to provide additional leveling and wedging in order to obtain the profile grades as specified in the plans.
2001-02-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 7 | CLARK | The originally planned guardrail Type 4A end treatments did not meet current specifications. | The Type 4A end treatments were changed to Type 3. As a result , Drop Box Inlet Type 5f , which is used in conjunction with Type 3 end treatments , was also established.
2001-02-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 7 | CLARK | The originally planned guardrail Type 4A end treatments did not meet current specifications. | The Type 4A end treatments were changed to Type 3. As a result , Drop Box Inlet Type 5f , which is used in conjunction with Type 3 end treatments , was also established.
2001-02-23 | Design | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Guardrail bridge end connectors Type A-1 and guardrail terminal section No. 1 were indicated in Standard Drawings RBC-001-07 and RBB-002-07 but left out from the plans. | These items were added via Change Order.
2001-02-23 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Additional items were needed for the proposed traffic phasing which involved single-lane traffic through the four sets of bridges located on this project. | Temporary pavement markers Type IV were added via Change Order.
2001-02-23 | Construction | Delays | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Due to numerous Change Orders , this project was prolonged through the entire construction season and had to be opened to traffic prior to completion. A solid white stripe used to delineate traffic during a lane closure had to be dealt with in order to | The solid white stripe was removed by means of a milling machine and a Change Order was approved to reimburse the Contractor for pavement striping removal.
2001-02-23 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Temporary Barrier Wall was proposed as part of the Traffic Control Plan (TCP). However , delineators , which are typically used in conjunction with Temporary Barrier Wall , were left out from the contract. | A Change Order established the bid prices for Delineators for Barrier Wall.
2001-02-23 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | A Lane Closure was proposed in this project. However , Temporary Removable Striping Tape which is used as an integral part of lane closures , was not included in the plans. | A Change Order established bid items for Temporary Removable Striping Tape.
2001-02-23 | Structures | Bearing Pad | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Upon field review of the substructure of the bridge over Slate Creek and Kendall Springs Road , it was determined that additional bearings needed replacement. | A Change Order established the pay item for additional bearing replacement.
2001-02-23 | Erosion Control Plan | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Special Seeding Crown Vetch had been set up in the plans on slopes steeper than 3:1 without corresponding pay items. | A Change Order added Special Seeding Crown Vetch on slopes steeper than 3:1.
2001-02-23 | Structures | Phasing | PAVEMENT REHAB-PRK(P) | 7 | CLARK | The Contractor worked on eight bridges involved with the project concurrently. | Four additional crash cushions and four additional crash cushion relocations were required.
2001-02-23 | Geotechnical | Safety | PAVEMENT REHAB-PRK(P) | 7 | CLARK | There was a major safety concern due to the precarious nature of slope material in the project area predominately consisting of highly weathered shales and limestone. | A Change Order was submitted to implement cut slope revisions located at eastbound Sta. 26+000 to 26+360 and westbound Sta. 26+080 to 26+280. The Change Order included all items necessary to perform the work including maintenance and control of traffic ,
2001-02-23 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRK(P) | 7 | CLARK | There were areas of cut slopes where the earth material , consisting of shales and limestone , was highly unstable and presented a significant safety concern to the travelling traffic involving potential rock falls. | A Change Order added additional excavation (104 , 000 cubic meters) of several cut slopes. This Change Order included all items necessary to stair-step and lay the unstable areas back in stable slopes away from the highway including Clearing and Grabbing
2001-02-23 | Pavement | Omission | PAVEMENT REHAB-PRK(P) | 7 | CLARK | As per the project phasing , the existing outside shoulder of I-64 was to be used to divert traffic. The existing shoulder was to be removed and replaced with full depth asphalt material to provide added stability. However , the pay item for Asphalt P | A Change Order was issued to set up the pay item for Asphalt Pavement Milling of the shoulder area.
2001-02-23 | Drainage | Existing Pipe | PAVEMENT REHAB-PRK(P) | 7 | CLARK | There were safety concerns regarding the drainage system within the safety zone. | A Change Order was approved for reconstruction of the existing Drainage Box Inlets within the safety zone. Additionally , a 1050-mm pipe was extended and a Sloped & Flared Box Inlet/Outlet was constructed. The aforementioned drainage work alleviated th
2001-02-23 | Design | Drainage | PAVEMENT REHAB-PRK(P) | 7 | CLARK | Upon field review of the proposed 100-mm drainage system , the decision was made to use the existing median boxes for drainage. | A Change Order established the pay items for this work.
2001-02-22 | Design | Omission | NEW ROUTE(O) | 10 | ESTILL | The contract plans called for a pipe located at Station 4+560 to be safeloaded. However no pay item was set up in the contract. | The item , Safeloading was added to the contract in order to compensate the Contractor for this item of work.
2001-02-22 | Drainage | Error | NEW ROUTE(O) | 10 | ESTILL | Culvert Pipe 600mm was listed in the pipe summary and pipe sections , but the pay item was for the incorrect size , 450mm. | All plan quantity of Culvert Pipe 450mm was deleted from the contract and a new item , Culvert Pipe 600mm was established.
2001-02-22 | Design | Borrow/Waste | BYPASS(O) | 10 | ESTILL | The project was designed as an Embankment in Place project , but after most of the earthwork was completed it became obvious that there would be excess material on the project. There was approximately 70 , 716 cubic meters of waste material. | Additional quantities of Embankment place were needed on the project.
2001-02-22 | Drainage | Ponding | RELOCATION(O) | 10 | MENIFEE | There was insufficient existing drainage within the limits of the existing depressed median from Sta. 83+000 to Sta. 84+000 to prevent water from migrating onto the pavement surface. | Additional quantities of roadway excavation were needed to undercut and stabilize the subgrade. Remedial action also included use of Geotextile Fabric Type IV , Crushed Aggregate Size No. 23 , and extending the existing 200-mm perforated pipe 132.00 me
2001-02-22 | Pavement | Quantities | BYPASS(O) | 10 | ESTILL | An insufficient quantity of Traffic Bound Base was set up in the contract since both ends of the project were constructed under traffic. | An additional quantity of Traffic Bound Base was added to the contract.
2001-02-22 | Design | Slopes | NEW ROUTE(O) | 10 | ESTILL | The Contractor was instructed to waste material in the Right-of-Way in order to flatten the slope from 2:1 to 4:1. Due to this work , an existing manhole located Rt. KY 89 Station 5+247 had to be raised. | The Contractor installed precast concrete risers on this manhole and an item Adjusting Manhole was added to the contract to compensate the Contractor for this item of work.
2001-02-22 | Maintenance of Traffic | Safety | NEW ROUTE(O) | 10 | ESTILL | Motorists were using the uncompleted bypass. | Four additional barricades were needed to completely block traffic. These barricades were placed on the Stump Connector and KY 89.
2001-02-22 | Materials | Asphalt Mixtures | NEW ROUTE(O) | 10 | ESTILL | Due to the 4.522% slope on the mainline hill , there were concerns about potential rutting if the top course of base and the surface course remained PG64-22 as indicated in the plans. | After consultation with the Division of Materials , the top course of base and the surface course were changed from PG64-22 to PG76-22. This change was made because it was felt that an upgrade to a stiffer asphalt mix was needed.
2001-02-22 | Pavement | Quantities | NEW ROUTE(O) | 10 | ESTILL | The detours on this project needed patching and three entrances were added after the plans were made. Also , in order to eliminate future maintenance on the shoulders , it was decided to pave the shoulders a full 2.4 meters. The original plans called | Asphalt Base Class I quantities were increased in order to compensate the Contractor for extra tonnage needed to complete the project.
2001-02-22 | Geotechnical | Slides | NEW ROUTE(O) | 10 | ESTILL | A slip occurred on the Stump Road Connector. | An additional quantity of Roadway Excavation was needed to compensate the Contractor for undercutting this area.
2001-02-22 | Drainage | Omission | BYPASS(O) | 10 | ESTILL | There were some drainage concerns on the project. | A 1200mm and a 750mm pipe were added to the contract. Additional quantities of Concrete Class A and Steel Reinforcement needed to place standard headwalls on both the inlet and outlet ends of these pipes were also added.
2001-02-22 | Erosion Control Plan | Channel Lining | NEW ROUTE(O) | 10 | ESTILL | Severe erosion was observed around and under the wire baskets after installing some of the Type IA gabion baskets. | It was decided to use Class III channel lining in lieu of Type IA. Class III channel was established for the substitution , for use in other areas as determined by the Engineer , as well as for small slide corrections.
2001-02-22 | Pavement | Repair | NEW ROUTE(O) | 10 | ESTILL | Over the course of the winter , a paved area between Station 3+110 and 3+170 on the mainline warped severely. This area was previously stabilized and paved and there were some discussions as to whether the stabilization had failed. | It was decided to remove the pavement and undercut 300 mm below the subgrade. Geotextile Fabric Type III was put down and #4 stone was used as a backfill and was covered with fabric. This area was then paved according to the typical section.
2001-02-22 | Erosion Control Plan | Channel Lining | NEW ROUTE(O) | 10 | ESTILL | Severe erosion was observed around and under the wire baskets after installing some of the Type IA gabion baskets. | It was decided to use Class III channel lining in lieu of Type IA. Class III channel was established for the substitution , for use in other areas as determined by the Engineer , as well as for small slide corrections.
2001-02-22 | Construction | Revisions | RELOCATION(O) | 10 | MENIFEE | The guardrail strings were located within the limits of the truck lane typical section , which had a planned shoulder wedge constructed of crushed stone base. This scheme was implemented on the southbound lanes. However , the open graded asphalt cours | Consequently , due to the difficulty encountered in driving guardrail posts through asphalt drainage blanket , some guardrail posts were installed in predrilled holes.
2001-02-22 | Design | Granular Embankment | NEW ROUTE(O) | 10 | ESTILL | Roadway Fill-Granular Embankment was originally set up on the project with a majority of this material to come directly from rock cuts on the job site. However , when this material was shot there were mud seams , which prohibited the material from bein | After consulting with the Central Office Division of Construction and Materials , Geotechnical Branch , it was decided that the fill would be stable enough using this material. Due to the special circumstance of handling the material , it was agreed t
2001-02-22 | Drainage | Elevation | BYPASS(O) | 10 | ESTILL | The proposed pipe elevation at mainline station 2+300 was too high and the pipe would not fit in the ditch. Consequently , there was a need to alleviate water from the roadway ditch. | A pay item Flume Inlet Type II' was added to the contract.
2001-02-22 | Drainage | Omission | BYPASS(O) | 10 | ESTILL | Headwalls for entrance pipes were not included on the pipe sheets. There were concerns regarding potential accidental damage occurring during ditching operations and unsafe traveling conditions for the general public. | Pay items for headwalls were added.
2001-02-22 | Structures | Phasing | RELOCATION(O) | 10 | MENIFEE | There were concerns that the proposed phase construction of the new Sand Hill Road Bridge over I-75 would delay the project. The proposed location of the new bridge was at the same location as the existing bridge. | A Change Order was approved to implement a Value Engineering proposal to move the location of the new Sand Hill Road Bridge four meters north from the planned location at Sta. 87+707.079 to Sta. 87+711.079. By obtaining additional Right-of-Way and revisi
2001-02-22 | Maintenance of Traffic | Safety | RELOCATION(O) | 10 | MENIFEE | There were concerns about the ability to adequately advise the travelling public of road conditions within the construction areas. | Remote Capability and Cellular Phone Service was required for the Variable Sign Message (VMS) boards. Remote Capability to VMS was provided per the Special Note for Variable Message Signs. The Contractor was reimbursed for the cost of cellular phone ser
2001-02-22 | Design | Omission | NEW ROUTE(O) | 10 | ESTILL | The quantity for undercutting 300 mm in rock cuts was omitted from the original contract plans. | Additional quantities were added for the undercutting and refilling needed for lime/concrete stabilization.
2001-02-22 | Geotechnical | Embankment Stabilization | NEW ROUTE(O) | 10 | ESTILL | After lime stabilization was used as set up in the original plans , the Geotechnical Branch and the Central Office , Division of Construction decided that cement would work better for the remaining portion of roadway. | The remaining quantity of Lime Modified Roadbed and Lime were deleted from the contract and items were established for Cement Modified Roadbed and Cement to reflect the change in materials used.
2001-02-22 | Maintenance of Traffic | Safety | RELOCATION(O) | 10 | MENIFEE | The 100 mm temporary paint pavement striping established in the contract was not consistent with the proposed permanent pavement striping which had been specified at 150 mm and there were concerns regarding it's visibility within the construction work zon | The 100 mm temporary paint pavement striping was replaced with 150 mm type.
2001-02-22 | Design | Drainage | NEW ROUTE(O) | 10 | ESTILL | The Resident Engineer decided not to use wire baskets with the Type 1A Channel Lining after the Contractor had already ordered enough for plan quantity and installed approximately 200m. The decision was made not to use the wire baskets after it was disco | The Contractor was reimbursed for a restocking fee paid to his supplier for returning the wire baskets.
2001-02-22 | Drainage | Existing Pipe | BYPASS(O) | 10 | ESTILL | A 100mm steel encasement pipe was going to be laid through an existing pipe Left of mainline Station 3+442. | Flowable Fill was added to the contract and was used to plug the existing pipe.
2001-02-22 | Maintenance of Traffic | Omission | RELOCATION(O) | 10 | MENIFEE | The plans did not address how to handle striping for the traffic transitions during phase construction. | A Change Order was established to remove the painted pavement striping of lane lines and edge lines for the traffic transitions in phase construction. Temporary pavement striping was added through the transition areas.
2001-02-22 | Design | Quantities | BYPASS(O) | 10 | ESTILL | There was insufficient quantities of excavation set up on this project. | An additional quantity of 64 , 663 cubic meters of Excavation was added via Change Order.
2001-02-22 | Design | Omission | NEW ROUTE(O) | 10 | ESTILL | The item for Pavement Striping Removal was omitted from the original contract. | A pay item for Pavement Striping Removal-100mm was added to the contract.
2001-02-22 | Design | Entrance | BYPASS(O) | 10 | ESTILL | The Menifee County Board of Education requested that something be done at Bott's Elementary School in order to alleviate some congestion problems. | A turning lane was added to help relieve the pre-school and post-school congestion problems. The addition of this turning lane necessitated a redesign of the Bott's School entrance and an adjacent church entrance. This redesign required and additional 1
2001-02-22 | Erosion Control Plan | Seeding | NEW ROUTE(O) | 10 | ESTILL | Due to poor soil conditions there were concerns regarding the use of Crown Vetch seeding. | Division of Construction , Central Office , decided to use Sericea-Lespedeza in lieu of Crown Vetch on the remaining portions of the project that were to be seeded.
2001-02-22 | Design | Guardrail | NEW ROUTE(O) | 10 | ESTILL | The plans called for new guardrail tying into the old rail on both ends of KY 89. However , the old guardrail was severely out of alignment due to slips. | State maintenance forces removed the old guardrail and repaired the shoulders in the slip areas. A pay item for Guardrail End Treatment Type 1 and additional quantities of Guardrail-Steel W Beam-S Face were added to the contract and the new rail was then
2001-02-22 | Design | Guardrail | NEW ROUTE(O) | 10 | ESTILL | The plans called for new guardrail tying into the old rail on both ends of KY 89. However , the old guardrail was severely out of alignment due to slips. | State maintenance forces removed the old guardrail and repaired the shoulders in the slip areas. A pay item for Guardrail End Treatment Type 1 and additional quantities of Guardrail-Steel W Beam-S Face were added to the contract and the new rail was then
2001-02-22 | Design | Entrance | NEW ROUTE(O) | 10 | ESTILL | A metal end section Type I and 55.4 meters of Culvert Pipe-375mm were to be placed in a fill area next to an end treatment located Rt. Station 2+495. However , an entrance was added at this location. | These items were deleted from the contract. Guardrail was used to create the radius into the entrance.
2001-02-22 | Drainage | Elevation | BYPASS(O) | 10 | ESTILL | There was an insufficient difference in elevation from the pipe outlet at mainline station 4+209 and the creek elevation to provide proper drainage. | A modified box was needed to fix the situation. As a result , the pay item Slope Box Outlet was added to the contract.
2001-02-22 | Geotechnical | Slides | NEW ROUTE(O) | 10 | ESTILL | A slide occurred at Lt. Station 3+160. The slide developed on top of the slope Rt. KY 89 Station 4+944.5. Originally a 2:1 slope was designed , but a double drop box inlet was located between stations and the distance from the centerline would only all | The material was excavated and Type III Geotextile Fabric was placed and backfilled with Class III Channel Lining. Due to the erosive properties of the material , a slope adjustment was necessary , a bench was excavated , and Class III Channel Lining
2001-02-22 | Maintenance of Traffic | Quantities | NEW ROUTE(O) | 10 | ESTILL | Original quantities of Pavement Striping-Temp Paint-100mm and Pavement Marker Type IV A-BY were set up only for the detour. KY 89 was built in phases according to the plans , but no additional quantities of striping were set up for shifting traffic. | Pavement Striping-Temp Paint-100mm and Pavement Marker Type IV A-BY quantities were increased.
2001-02-22 | Pavement | Approaches | RELOCATION(O) | 10 | MENIFEE | The Division of Operations and FHWA requested the existing roadway surface from the planned beginning of new pavement Sta. 82+919 back to the Laurel County line Sta. 81+753 be resurfaced and milled. | The milling and asphalt resurfacing were added via Change Order and included all mainline pavement , inside shoulder , and 0.9 meter of the outside shoulder. This item covered erosion control as well as ditching for the project extension. Additional M
2001-02-22 | Design | Phasing | RELOCATION(O) | 10 | MENIFEE | Rumble strips in the inside median shoulders could not be installed per the plans due to the construction and traffic control phasing of the final surface course. The normal rolled-in rumble strips could not be installed during the surfacing of the insid | The rumble strips were milled into the shoulder after traffic was switched to the finished mainline driving lanes.
2001-01-19 | Construction | Delays | RELOCATION(O) | 12 | PIKE | The asphalt plant was not producing enough material to keep up with the Motor Transfer Vehicle (MTV) Paver. | A Change Order allowed the use of a Cedar Rapids Remix Paver in lieu of the MTV Paver on the remaining section of the project from MP 56.03 to MP 59.85. This change was recommended by the Resident Engineer and resulted in approximate savings of $800 , 00
2001-01-19 | Construction | Delays | RELOCATION(O) | 12 | PIKE | The asphalt plant was not producing enough material to keep up with the Motor Transfer Vehicle (MTV) Paver. | A Change Order allowed the use of a Cedar Rapids Remix Paver in lieu of the MTV Paver on the remaining section of the project from MP 56.03 to MP 59.85. This change was recommended by the Resident Engineer and resulted in approximate savings of $800 , 00
2001-01-19 | Maintenance of Traffic | Safety | RELOCATION(O) | 12 | PIKE | There were no items included in the plans to protect traffic from the bridge ends during the phase when traffic would be crossed over in the opposing direction. | Temporary Bridge End Connectors Type A and C were added to the project as well as other appropriate ancillary items such as temporary guardrail and end treatments.
2001-01-19 | Maintenance of Traffic | Safety | RELOCATION(O) | 12 | PIKE | There were no items included in the plans to protect traffic from the bridge ends during the phase when traffic would be crossed over in the opposing direction. | Temporary Bridge End Connectors Type A and C were added to the project as well as other appropriate ancillary items such as temporary guardrail and end treatments.
2001-01-19 | Pavement | Repair | RELOCATION(O) | 12 | PIKE | The concrete had deteriorated in the areas where traffic had been shifted during the winter months. | A Change Order added additional quantities of PCC Pavement Repair.
2001-01-19 | Pavement | Repair | RELOCATION(O) | 12 | PIKE | The concrete had deteriorated in the areas where traffic had been shifted during the winter months. | A Change Order added additional quantities of PCC Pavement Repair.
2001-01-19 | Design | Guardrail | RELOCATION(O) | 12 | PIKE | The Guardrail End Treatments in the plans for KY 604 and KY 2697 did not meet the current geometric standards. | Guardrail End Treatment Type 2A were replaced with Type 7.
2001-01-19 | Design | Guardrail | RELOCATION(O) | 12 | PIKE | The Guardrail End Treatments in the plans for KY 604 and KY 2697 did not meet the current geometric standards. | Guardrail End Treatment Type 2A were replaced with Type 7.
2001-01-19 | Design | Guardrail | RELOCATION(O) | 12 | PIKE | The Guardrail End Treatments in the plans for KY 604 and KY 2697 did not meet the current geometric standards. | Guardrail End Treatment Type 2A were replaced with Type 7.
2001-01-19 | Design | Guardrail | RELOCATION(O) | 12 | PIKE | The Guardrail End Treatments in the plans for KY 604 and KY 2697 did not meet the current geometric standards. | Guardrail End Treatment Type 2A were replaced with Type 7.
2001-01-19 | Erosion Control Plan | Seeding | RELOCATION(O) | 12 | PIKE | It was difficult to achieve the desired vegetative cover due to recurring problems with achieving seed germination. | Erosion Control Blanket was added for the entire area of the median.
2001-01-19 | Design | Median | RELOCATION(O) | 12 | PIKE | When replacing raised medians with the depressed type , treating the location of the median pipe and the quantity of flowable fill as incidental can result in insufficient quantities of flowable fill being used by the Contractor. | When replacing raised medians with the depressed type , the location of the median pipe and the quantity of flowable fill should be specified rather than incidental.
2001-01-19 | Drainage | Omission | RELOCATION(O) | 12 | PIKE | Nothing was set up in the plans to connect a cross-drain and a median drain at Sta. 4439+00. | A junction box was added to correct this oversight.
2001-01-19 | Geotechnical | Subsurface | RELOCATION(O) | 12 | PIKE | A cavity was encountered below a wall at the KY 2697 Bridge. | An item to £Remove and Replace Slope Wall¥ was added.
2001-01-19 | Geotechnical | Subsurface | RELOCATION(O) | 12 | PIKE | A cavity was encountered below a wall at the KY 2697 Bridge. | An item to £Remove and Replace Slope Wall¥ was added.
2001-01-19 | Design | Median | RELOCATION(O) | 12 | PIKE | When replacing raised medians with the depressed type , treating the location of the median pipe and the quantity of flowable fill as incidental can result in insufficient quantities of flowable fill being used by the Contractor. | When replacing raised medians with the depressed type , the location of the median pipe and the quantity of flowable fill should be specified rather than incidental.
2001-01-19 | Drainage | Omission | RELOCATION(O) | 12 | PIKE | Nothing was set up in the plans to connect a cross-drain and a median drain at Sta. 4439+00. | A junction box was added to correct this oversight.
2001-01-19 | Erosion Control Plan | Seeding | RELOCATION(O) | 12 | PIKE | It was difficult to achieve the desired vegetative cover due to recurring problems with achieving seed germination. | Erosion Control Blanket was added for the entire area of the median.
2001-01-19 | Maintenance of Traffic | Omission | RELOCATION(O) | 12 | PIKE | Delineators for guardrail and tubular markers needed to safely channelize traffic on US 431 and the Western Kentucky Parkway transitions were called for in the standard drawing but left out from the pay items. | These items were added via Change Order.
2001-01-19 | Structures | Omission | RELOCATION(O) | 12 | PIKE | Backfill for the US 431 , KY 2697 , and KY 604 bridge ends was required by the pertinent Standard Drawings but was not set up on the plans. | £Structure Granular Backfill¥ was added by Change Order.
2001-01-19 | Structures | Omission | RELOCATION(O) | 12 | PIKE | Backfill for the US 431 , KY 2697 , and KY 604 bridge ends was required by the pertinent Standard Drawings but was not set up on the plans. | £Structure Granular Backfill¥ was added by Change Order.
2001-01-19 | Traffic | Signs | RELOCATION(O) | 12 | PIKE | The existing sign support beams were left off the previous Western Kentucky Parkway signing project and had to be removed before the new Sign Bridge Attachment Brackets could be installed. | A Change Order was established to remove the existing sign support beams in order to install the new signs.
2001-01-19 | Traffic | Signs | RELOCATION(O) | 12 | PIKE | The existing sign support beams were left off the previous Western Kentucky Parkway signing project and had to be removed before the new Sign Bridge Attachment Brackets could be installed. | A Change Order was established to remove the existing sign support beams in order to install the new signs.
2001-01-19 | Maintenance of Traffic | Omission | RELOCATION(O) | 12 | PIKE | Delineators for guardrail and tubular markers needed to safely channelize traffic on US 431 and the Western Kentucky Parkway transitions were called for in the standard drawing but left out from the pay items. | These items were added via Change Order.
2001-01-19 | Design | Omission | RELOCATION(O) | 12 | PIKE | Pavement Removal from the shoulder areas was set up in the plans. However , quantities for this item were not included in the plan summary. | A Change Order added additional quantities of Pavement Removal.
2001-01-19 | Design | Omission | RELOCATION(O) | 12 | PIKE | Pavement Removal from the shoulder areas was set up in the plans. However , quantities for this item were not included in the plan summary. | A Change Order added additional quantities of Pavement Removal.
2000-09-20 | Design | Quantities | SIGNING(P) | 6 | KENTON | Actual field measurements determined the quantities for Structure Excavation Solid Rock and Channel Lining Class II and III were underestimated. | The additional quantities of these items that were necessary to complete the project as designed were added via Change Order.
2000-09-20 | Design | Quantities | MAJOR WIDENING(O) | 6 | KENTON | Actual field measurements determined the quantities for Structure Excavation Solid Rock and Channel Lining Class II and III were underestimated. | The additional quantities of these items that were necessary to complete the project as designed were added via Change Order.
2000-09-20 | Design | Quantities | MAJOR WIDENING(O) | 6 | KENTON | Actual field measurements determined the quantities for Structure Excavation Solid Rock and Channel Lining Class II and III were underestimated. | The additional quantities of these items that were necessary to complete the project as designed were added via Change Order.
2000-09-20 | Right-of-Way | CAP | MAJOR WIDENING(O) | 6 | KENTON | According to the negotiations for purchasing Right-of-Way from the owner of Parcel 23 , an agreement was made to remove the concrete walled sand filter at Left Station 526+25. However , the plans did not indicate this work. | Since an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Right-of-Way | CAP | MAJOR WIDENING(O) | 6 | KENTON | According to the negotiations for purchasing Right-of-Way from the owner of Parcel 23 , an agreement was made to remove the concrete walled sand filter at Left Station 526+25. However , the plans did not indicate this work. | Since an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Right-of-Way | CAP | SIGNING(P) | 6 | KENTON | According to the negotiations for purchasing Right-of-Way from the owner of Parcel 23 , an agreement was made to remove the concrete walled sand filter at Left Station 526+25. However , the plans did not indicate this work. | Since an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was insufficient erosion control set up on this project. | In order to provide erosion control , it was necessary to construct Silt Fence in various areas on the project.
2000-09-20 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was insufficient erosion control set up on this project. | In order to provide erosion control , it was necessary to construct Silt Fence in various areas on the project.
2000-09-20 | Erosion Control Plan | Omission | SIGNING(P) | 6 | KENTON | There was insufficient erosion control set up on this project. | In order to provide erosion control , it was necessary to construct Silt Fence in various areas on the project.
2000-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Design | Guardrail | SIGNING(P) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Design | Guardrail | MAJOR WIDENING(O) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Design | Guardrail | SIGNING(P) | 6 | KENTON | The Guardrail End Treatments set up for this project were not in accordance with current design criteria. | Guardrail End Treatments Type 4A were substituted for Guardrail End Treatment Type 4.
2000-09-20 | Drainage | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was an excess land purchase by the Department at Right Station 549+00 to 552+00 , which borders the Right-of-Way. After the removal of a house at this location , the land in this area was not graded for proper drainage. | Since the plans did not indicate this work and because an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Environmental | Asbestos | MAJOR WIDENING(O) | 6 | KENTON | The contract proposal contained the Special Note for Building Inspection , Asbestos Containing Materials (ACM) Removal , and Demolition. Upon inspection of the structures listed in the proposal , asbestos was discovered in the buildings on Parcels 13 | It was necessary to add these items to the contract.
2000-09-20 | Utilities | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was inadequate access to install new gas mains. | In order to provide access to the gas mains , it was necessary to construct 6 Steel Casing Pipe across the roadway at Station 522+86 , Station 540+57 , and Station 571+15.
2000-09-20 | Utilities | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was inadequate access to install new gas mains. | In order to provide access to the gas mains , it was necessary to construct 6 Steel Casing Pipe across the roadway at Station 522+86 , Station 540+57 , and Station 571+15.
2000-09-20 | Utilities | Omission | SIGNING(P) | 6 | KENTON | There was inadequate access to install new gas mains. | In order to provide access to the gas mains , it was necessary to construct 6 Steel Casing Pipe across the roadway at Station 522+86 , Station 540+57 , and Station 571+15.
2000-09-20 | Drainage | Omission | MAJOR WIDENING(O) | 6 | KENTON | There was an excess land purchase by the Department at Right Station 549+00 to 552+00 , which borders the Right-of-Way. After the removal of a house at this location , the land in this area was not graded for proper drainage. | Since the plans did not indicate this work and because an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Drainage | Omission | SIGNING(P) | 6 | KENTON | There was an excess land purchase by the Department at Right Station 549+00 to 552+00 , which borders the Right-of-Way. After the removal of a house at this location , the land in this area was not graded for proper drainage. | Since the plans did not indicate this work and because an agreement could not be made as to the cost of this work , it was agreed to perform the work on a cost-plus basis.
2000-09-20 | Environmental | Asbestos | SIGNING(P) | 6 | KENTON | The contract proposal contained the Special Note for Building Inspection , Asbestos Containing Materials (ACM) Removal , and Demolition. Upon inspection of the structures listed in the proposal , asbestos was discovered in the buildings on Parcels 13 | It was necessary to add these items to the contract.
2000-09-20 | Environmental | Asbestos | MAJOR WIDENING(O) | 6 | KENTON | The contract proposal contained the Special Note for Building Inspection , Asbestos Containing Materials (ACM) Removal , and Demolition. Upon inspection of the structures listed in the proposal , asbestos was discovered in the buildings on Parcels 13 | It was necessary to add these items to the contract.
2000-09-20 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 6 | KENTON | There is a pond situated off the Right-of-Way at approximate station It. 493+00 on US 31E in the Glenmary subdivision. This pond was exposed to deposits of silt from the project area. | It was necessary to drain and dredge the pond. However , since it was deemed that some of the silt had been deposited from the proposed roadway grade before the project started , costs for this work was shared equally by the Department and the Contract
2000-09-20 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 6 | KENTON | The Division of Bridges recommended changing the type of structural steel used for the neoprene expansion dams. | The structural steel for the neoprene expansion dams was changed from steel angles with straps to steel plates with studs. This new design was easier to install but increased the amount of structural steel required for both the northbound and southbound
2000-09-20 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 6 | KENTON | The Division of Bridges recommended changing the type of structural steel used for the neoprene expansion dams. | The structural steel for the neoprene expansion dams was changed from steel angles with straps to steel plates with studs. This new design was easier to install but increased the amount of structural steel required for both the northbound and southbound
2000-09-20 | Structures | Reinforcement Steel | SIGNING(P) | 6 | KENTON | The Division of Bridges recommended changing the type of structural steel used for the neoprene expansion dams. | The structural steel for the neoprene expansion dams was changed from steel angles with straps to steel plates with studs. This new design was easier to install but increased the amount of structural steel required for both the northbound and southbound
2000-09-20 | Erosion Control Plan | Omission | SIGNING(P) | 6 | KENTON | There is a pond situated off the Right-of-Way at approximate station It. 493+00 on US 31E in the Glenmary subdivision. This pond was exposed to deposits of silt from the project area. | It was necessary to drain and dredge the pond. However , since it was deemed that some of the silt had been deposited from the proposed roadway grade before the project started , costs for this work was shared equally by the Department and the Contract
2000-09-20 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 6 | KENTON | There is a pond situated off the Right-of-Way at approximate station It. 493+00 on US 31E in the Glenmary subdivision. This pond was exposed to deposits of silt from the project area. | It was necessary to drain and dredge the pond. However , since it was deemed that some of the silt had been deposited from the proposed roadway grade before the project started , costs for this work was shared equally by the Department and the Contract
2000-09-20 | Utilities | Communication | MAJOR WIDENING(O) | 6 | KENTON | The existing cable line was abandoned in place. | In order to maintain future access for TKR Cable , a 4 Steel Conduit was installed at Station 486+20. The installation was performed according to the specifications of the cable company.
2000-09-20 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | KENTON | A 16 water main was discovered at Old Bardstown Road. | The grade was raised on the relocated Fairmount Road to clear the 16 water main. Since pipes for two entrances had already been constructed at plan grade , it was necessary to remove and relay the pipe.
2000-09-20 | Utilities | Communication | MAJOR WIDENING(O) | 6 | KENTON | The existing cable line was abandoned in place. | In order to maintain future access for TKR Cable , a 4 Steel Conduit was installed at Station 486+20. The installation was performed according to the specifications of the cable company.
2000-09-20 | Utilities | Existing Utilities | SIGNING(P) | 6 | KENTON | A 16 water main was discovered at Old Bardstown Road. | The grade was raised on the relocated Fairmount Road to clear the 16 water main. Since pipes for two entrances had already been constructed at plan grade , it was necessary to remove and relay the pipe.
2000-09-20 | Utilities | Communication | SIGNING(P) | 6 | KENTON | The existing cable line was abandoned in place. | In order to maintain future access for TKR Cable , a 4 Steel Conduit was installed at Station 486+20. The installation was performed according to the specifications of the cable company.
2000-09-20 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | KENTON | A 16 water main was discovered at Old Bardstown Road. | The grade was raised on the relocated Fairmount Road to clear the 16 water main. Since pipes for two entrances had already been constructed at plan grade , it was necessary to remove and relay the pipe.
2000-09-20 | Utilities | Omission | MAJOR WIDENING(O) | 6 | KENTON | Directions for the diversion of existing water service to the water meter vaults located along the new water mains constructed on this project were omitted from the utility plans. | A Change Order was established to divert the existing water service to the new water mains on parcels #10 , #11 , #18 , #33 , #45 , #52 , #59 , and #63.
2000-09-20 | Construction | Wells | SIGNING(P) | 6 | KENTON | A six inch diameter water well was discovered in the roadway section located 37 feet left of Station 638+30. | A bid item for plugging this water well was established in the contract.
2000-09-20 | Utilities | Omission | MAJOR WIDENING(O) | 6 | KENTON | Directions for the diversion of existing water service to the water meter vaults located along the new water mains constructed on this project were omitted from the utility plans. | A Change Order was established to divert the existing water service to the new water mains on parcels #10 , #11 , #18 , #33 , #45 , #52 , #59 , and #63.
2000-09-20 | Utilities | Omission | SIGNING(P) | 6 | KENTON | Directions for the diversion of existing water service to the water meter vaults located along the new water mains constructed on this project were omitted from the utility plans. | A Change Order was established to divert the existing water service to the new water mains on parcels #10 , #11 , #18 , #33 , #45 , #52 , #59 , and #63.
2000-09-20 | Construction | Wells | MAJOR WIDENING(O) | 6 | KENTON | A six inch diameter water well was discovered in the roadway section located 37 feet left of Station 638+30. | A bid item for plugging this water well was established in the contract.
2000-09-20 | Construction | Wells | MAJOR WIDENING(O) | 6 | KENTON | A six inch diameter water well was discovered in the roadway section located 37 feet left of Station 638+30. | A bid item for plugging this water well was established in the contract.
2000-09-20 | Erosion Control Plan | Slope Protection | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated that the berm being constructed on the new US 31E from Lt. Station 478+00 to Station 516+00 would have a varied cross slope along its backside ranging from 1.5:1 to 2:1. | In order to provide effective protection of this slope , it was agreed to install an Excelsior Blanket along the entire length of the berm.
2000-09-20 | Erosion Control Plan | Slope Protection | SIGNING(P) | 6 | KENTON | The plans indicated that the berm being constructed on the new US 31E from Lt. Station 478+00 to Station 516+00 would have a varied cross slope along its backside ranging from 1.5:1 to 2:1. | In order to provide effective protection of this slope , it was agreed to install an Excelsior Blanket along the entire length of the berm.
2000-09-20 | Erosion Control Plan | Slope Protection | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated that the berm being constructed on the new US 31E from Lt. Station 478+00 to Station 516+00 would have a varied cross slope along its backside ranging from 1.5:1 to 2:1. | In order to provide effective protection of this slope , it was agreed to install an Excelsior Blanket along the entire length of the berm.
2000-09-20 | Utilities | Relocation | SIGNING(P) | 6 | KENTON | The plans indicated that the existing 12 water main at Station 503+00 was to be relocated to Station 502+70. However , this would cause a prolonged disruption of service to customers. | In order to avoid a prolonged disruption of service , it was agreed the Contractor would install a Gate Valve on the existing water main before constructing the tie-in with the new water main.
2000-09-20 | Utilities | Relocation | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated that the existing 12 water main at Station 503+00 was to be relocated to Station 502+70. However , this would cause a prolonged disruption of service to customers. | In order to avoid a prolonged disruption of service , it was agreed the Contractor would install a Gate Valve on the existing water main before constructing the tie-in with the new water main.
2000-09-20 | Utilities | Relocation | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated that the existing 12 water main at Station 503+00 was to be relocated to Station 502+70. However , this would cause a prolonged disruption of service to customers. | In order to avoid a prolonged disruption of service , it was agreed the Contractor would install a Gate Valve on the existing water main before constructing the tie-in with the new water main.
2000-09-20 | Traffic | Lighting | MAJOR WIDENING(O) | 6 | KENTON | The new US 31E crosses the entrance roadways connecting the Glenmary subdivision with the existing US 31E. Consequently , the new construction eliminated the lighting , which previously delineated the entrance roadways while the new section of US 31E w | It was agreed that the Cabinet would provide lighting at each of the affected entrances. The supplemental unit price for Lighting was full compensation for the installation , maintenance , and electric consumption of three streetlights over a two year
2000-09-20 | Traffic | Lighting | MAJOR WIDENING(O) | 6 | KENTON | The new US 31E crosses the entrance roadways connecting the Glenmary subdivision with the existing US 31E. Consequently , the new construction eliminated the lighting , which previously delineated the entrance roadways while the new section of US 31E w | It was agreed that the Cabinet would provide lighting at each of the affected entrances. The supplemental unit price for Lighting was full compensation for the installation , maintenance , and electric consumption of three streetlights over a two year
2000-09-20 | Traffic | Omission | MAJOR WIDENING(O) | 6 | KENTON | It was necessary to remove the Pavement Markers in order to resurface existing pavement. However , no bid item was included in the contract for Remove Type V Marker. | A supplemental bid item was established for this work.
2000-09-20 | Traffic | Lighting | SIGNING(P) | 6 | KENTON | The new US 31E crosses the entrance roadways connecting the Glenmary subdivision with the existing US 31E. Consequently , the new construction eliminated the lighting , which previously delineated the entrance roadways while the new section of US 31E w | It was agreed that the Cabinet would provide lighting at each of the affected entrances. The supplemental unit price for Lighting was full compensation for the installation , maintenance , and electric consumption of three streetlights over a two year
2000-09-20 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | KENTON | Project construction displaced gas service for parcels #18 , #28 , and #44. | New service lines had to be installed for these parcels.
2000-09-20 | Utilities | Existing Utilities | MAJOR WIDENING(O) | 6 | KENTON | Project construction displaced gas service for parcels #18 , #28 , and #44. | New service lines had to be installed for these parcels.
2000-09-20 | Utilities | Existing Utilities | SIGNING(P) | 6 | KENTON | Project construction displaced gas service for parcels #18 , #28 , and #44. | New service lines had to be installed for these parcels.
2000-09-20 | Traffic | Omission | MAJOR WIDENING(O) | 6 | KENTON | It was necessary to remove the Pavement Markers in order to resurface existing pavement. However , no bid item was included in the contract for Remove Type V Marker. | A supplemental bid item was established for this work.
2000-09-20 | Traffic | Omission | SIGNING(P) | 6 | KENTON | It was necessary to remove the Pavement Markers in order to resurface existing pavement. However , no bid item was included in the contract for Remove Type V Marker. | A supplemental bid item was established for this work.
2000-09-20 | Structures | Expansion Joints | MAJOR WIDENING(O) | 6 | KENTON | The 1/2 joints on the bridges on US 31E over Floyds Fork had widened due to approach slab settlement and rotation of the joints. | Upon recommendation of the Central Office Division of Construction , the existing Neoprene Joint Seal was removed and the joint was sealed with silicone. The neoprene that was removed from the joints became the property of the Department.
2000-09-20 | Structures | Expansion Joints | SIGNING(P) | 6 | KENTON | The 1/2 joints on the bridges on US 31E over Floyds Fork had widened due to approach slab settlement and rotation of the joints. | Upon recommendation of the Central Office Division of Construction , the existing Neoprene Joint Seal was removed and the joint was sealed with silicone. The neoprene that was removed from the joints became the property of the Department.
2000-09-20 | Construction | Temporary Fencing | SIGNING(P) | 6 | KENTON | The plans indicated a new water main was to cross a fenced parcel at Rt. Station 467+50. | In order to maintain the enclosure and safeguard this area during construction , a temporary fence was erected along the construction easement limits.
2000-09-20 | Drainage | Omission | MAJOR WIDENING(O) | 6 | KENTON | The 6' x 6' x 53' Box Culvert located Left of Station 631+75 and the 6' x 4' x 64' Box Culvert located Left of Station 658+50 both crossed beneath existing US 31E where the new US 31E incorporated the existing roadway within its embankment section. | These culverts had to be removed. However , no unit bid price for this work was established in the contract. Therefore a supplemental item had to be established for Remove Box Culvert.
2000-09-20 | Drainage | Omission | MAJOR WIDENING(O) | 6 | KENTON | The 6' x 6' x 53' Box Culvert located Left of Station 631+75 and the 6' x 4' x 64' Box Culvert located Left of Station 658+50 both crossed beneath existing US 31E where the new US 31E incorporated the existing roadway within its embankment section. | These culverts had to be removed. However , no unit bid price for this work was established in the contract. Therefore a supplemental item had to be established for Remove Box Culvert.
2000-09-20 | Drainage | Omission | SIGNING(P) | 6 | KENTON | The 6' x 6' x 53' Box Culvert located Left of Station 631+75 and the 6' x 4' x 64' Box Culvert located Left of Station 658+50 both crossed beneath existing US 31E where the new US 31E incorporated the existing roadway within its embankment section. | These culverts had to be removed. However , no unit bid price for this work was established in the contract. Therefore a supplemental item had to be established for Remove Box Culvert.
2000-09-20 | Structures | Expansion Joints | MAJOR WIDENING(O) | 6 | KENTON | The 1/2 joints on the bridges on US 31E over Floyds Fork had widened due to approach slab settlement and rotation of the joints. | Upon recommendation of the Central Office Division of Construction , the existing Neoprene Joint Seal was removed and the joint was sealed with silicone. The neoprene that was removed from the joints became the property of the Department.
2000-09-20 | Construction | Temporary Fencing | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated a new water main was to cross a fenced parcel at Rt. Station 467+50. | In order to maintain the enclosure and safeguard this area during construction , a temporary fence was erected along the construction easement limits.
2000-09-20 | Construction | Temporary Fencing | MAJOR WIDENING(O) | 6 | KENTON | The plans indicated a new water main was to cross a fenced parcel at Rt. Station 467+50. | In order to maintain the enclosure and safeguard this area during construction , a temporary fence was erected along the construction easement limits.
2000-09-20 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 6 | KENTON | The construction phasing on this project required changes to the existing traffic patterns and roadway markings. However , the contract did not include a bid item to remove the existing striping. | It was agreed to set up a bid item for Removing Striping.
2000-09-20 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 6 | KENTON | The construction phasing on this project required changes to the existing traffic patterns and roadway markings. However , the contract did not include a bid item to remove the existing striping. | It was agreed to set up a bid item for Removing Striping.
2000-09-20 | Maintenance of Traffic | Omission | SIGNING(P) | 6 | KENTON | The construction phasing on this project required changes to the existing traffic patterns and roadway markings. However , the contract did not include a bid item to remove the existing striping. | It was agreed to set up a bid item for Removing Striping.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The project documents indicated construction of a storm water drainage system between Station 160+00 and 162+00. However , there were unstable soil conditions and a need to drain and monitor ground fluids in this area. | It was agreed to use Crushed Aggregate Size No. 57 as a pipe bedding and backfill material. The material excavated during the construction of the storm sewer was not acceptable for use on this project , nor was it acceptable for use on the proposed Phas
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The project documents indicated construction of a storm water drainage system between Station 160+00 and 162+00. However , there were unstable soil conditions and a need to drain and monitor ground fluids in this area. | It was agreed to use Crushed Aggregate Size No. 57 as a pipe bedding and backfill material. The material excavated during the construction of the storm sewer was not acceptable for use on this project , nor was it acceptable for use on the proposed Phas
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The project documents indicated construction of a storm water drainage system between Station 160+00 and 162+00. However , there were unstable soil conditions and a need to drain and monitor ground fluids in this area. | It was agreed to use Crushed Aggregate Size No. 57 as a pipe bedding and backfill material. The material excavated during the construction of the storm sewer was not acceptable for use on this project , nor was it acceptable for use on the proposed Phas
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The existing soil between Station 160+00 and 162+00 was very unstable. | The soil had to be undercut 12 inches and further reinforced in order to be able to support the proposed road. This unstable material was stripped and moved to an approved facility.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The existing soil between Station 160+00 and 162+00 was very unstable. | The soil had to be undercut 12 inches and further reinforced in order to be able to support the proposed road. This unstable material was stripped and moved to an approved facility.
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The existing soil between Station 160+00 and 162+00 was very unstable. | The soil had to be undercut 12 inches and further reinforced in order to be able to support the proposed road. This unstable material was stripped and moved to an approved facility.
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | Parcel Number 112 located at 2408 Crittenden Drive did not have access to its existing entrance due to the closure of Foster Street. However , the property owner was not paid to provide interim security at the closed entrance as this item was overlooked | It was agreed to construct a six-foot tall , twenty-foot wide double vehicular chain link gate at the entrance to this property.
2000-09-19 | Right-of-Way | Fencing | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Parcel Number 112 located at 2408 Crittenden Drive did not have access to its existing entrance due to the closure of Foster Street. However , the property owner was not paid to provide interim security at the closed entrance as this item was overlooked | It was agreed to construct a six-foot tall , twenty-foot wide double vehicular chain link gate at the entrance to this property.
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | Parcel Number 112 located at 2408 Crittenden Drive did not have access to its existing entrance due to the closure of Foster Street. However , the property owner was not paid to provide interim security at the closed entrance as this item was overlooked | It was agreed to construct a six-foot tall , twenty-foot wide double vehicular chain link gate at the entrance to this property.
2000-09-19 | Utilities | Existing Utilities | RELOCATION(O) | 6 | CAMPBELL | There was an existing 12-inch water main , which runs parallel to Floyd Street. This water line was shown on the plans , however , when the water main was uncovered it was in bad condition. | It was necessary to remove a section of the water line and install a new replacement water main at a lower elevation.
2000-09-19 | Utilities | Existing Utilities | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | There was an existing 12-inch water main , which runs parallel to Floyd Street. This water line was shown on the plans , however , when the water main was uncovered it was in bad condition. | It was necessary to remove a section of the water line and install a new replacement water main at a lower elevation.
2000-09-19 | Utilities | Existing Utilities | RELOCATION(O) | 6 | CAMPBELL | There was an existing 12-inch water main , which runs parallel to Floyd Street. This water line was shown on the plans , however , when the water main was uncovered it was in bad condition. | It was necessary to remove a section of the water line and install a new replacement water main at a lower elevation.
2000-09-19 | Utilities | New Utilities | RELOCATION(O) | 6 | CAMPBELL | There were three additional locations along Central Avenue where electrical crossings were needed for lighting that the City of Louisville planned to install in the future. | Additional conduit and junction boxes were added at these locations.
2000-09-19 | Utilities | New Utilities | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | There were three additional locations along Central Avenue where electrical crossings were needed for lighting that the City of Louisville planned to install in the future. | Additional conduit and junction boxes were added at these locations.
2000-09-19 | Utilities | New Utilities | RELOCATION(O) | 6 | CAMPBELL | There were three additional locations along Central Avenue where electrical crossings were needed for lighting that the City of Louisville planned to install in the future. | Additional conduit and junction boxes were added at these locations.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | Unstable soil was encountered during pipe excavation. The unstable soil consisted of silty brown sand , which saturated to nearly a quick condition. The soil would not support the pipe or pipe bedding material. This area was isolated from the rest of | It was agreed to undercut the pipe trenches as needed by a depth of 12 inches. The bottom and sides of the trenches were lined with Type III Geotextile Fabric and the trench was backfilled to a depth of 12 inches with Crushed Aggregate Size Number 3. Ro
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Unstable soil was encountered during pipe excavation. The unstable soil consisted of silty brown sand , which saturated to nearly a quick condition. The soil would not support the pipe or pipe bedding material. This area was isolated from the rest of | It was agreed to undercut the pipe trenches as needed by a depth of 12 inches. The bottom and sides of the trenches were lined with Type III Geotextile Fabric and the trench was backfilled to a depth of 12 inches with Crushed Aggregate Size Number 3. Ro
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | Unstable soil was encountered during pipe excavation. The unstable soil consisted of silty brown sand , which saturated to nearly a quick condition. The soil would not support the pipe or pipe bedding material. This area was isolated from the rest of | It was agreed to undercut the pipe trenches as needed by a depth of 12 inches. The bottom and sides of the trenches were lined with Type III Geotextile Fabric and the trench was backfilled to a depth of 12 inches with Crushed Aggregate Size Number 3. Ro
2000-09-19 | Environmental | Pollution | RELOCATION(O) | 6 | CAMPBELL | Weep holes could not be installed in the gravity walls on both sides of Central Avenue at Floyd Street from Station 156+91 to Station 159+75. The weep holes were omitted in order to prevent the leakage of potentially contaminated groundwater out onto the | It was agreed to increase the quantities for Crushed Aggregate Size No. 57. This additional material was needed to backfill both of the gravity walls.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The undercutting , geotextile fabric , and aggregate stabilization materials used between Station 160+00 and 162+50 were not sufficient to provide a stable enough subgrade to place Dense Graded Aggregate or pavement. | It was agreed to construct a 4 inch thick course of Cement Treated Base in this area in lieu of the Dense Graded Aggregate.
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The undercutting , geotextile fabric , and aggregate stabilization materials used between Station 160+00 and 162+50 were not sufficient to provide a stable enough subgrade to place Dense Graded Aggregate or pavement. | It was agreed to construct a 4 inch thick course of Cement Treated Base in this area in lieu of the Dense Graded Aggregate.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The undercutting , geotextile fabric , and aggregate stabilization materials used between Station 160+00 and 162+50 were not sufficient to provide a stable enough subgrade to place Dense Graded Aggregate or pavement. | It was agreed to construct a 4 inch thick course of Cement Treated Base in this area in lieu of the Dense Graded Aggregate.
2000-09-19 | Environmental | Pollution | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Weep holes could not be installed in the gravity walls on both sides of Central Avenue at Floyd Street from Station 156+91 to Station 159+75. The weep holes were omitted in order to prevent the leakage of potentially contaminated groundwater out onto the | It was agreed to increase the quantities for Crushed Aggregate Size No. 57. This additional material was needed to backfill both of the gravity walls.
2000-09-19 | Environmental | Pollution | RELOCATION(O) | 6 | CAMPBELL | Weep holes could not be installed in the gravity walls on both sides of Central Avenue at Floyd Street from Station 156+91 to Station 159+75. The weep holes were omitted in order to prevent the leakage of potentially contaminated groundwater out onto the | It was agreed to increase the quantities for Crushed Aggregate Size No. 57. This additional material was needed to backfill both of the gravity walls.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The ground fluids encountered in this area likely contained petroleum-based materials , which needed to be kept out of the storm sewer system in order to prevent deterioration of the pipe joint materials. | It was agreed to use the flexible butyl resin sealant ConSeal CS-440 manufactured by Concrete Sealant , Inc. to seal the reinforced concrete culvert pipes.
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The ground fluids encountered in this area likely contained petroleum-based materials , which needed to be kept out of the storm sewer system in order to prevent deterioration of the pipe joint materials. | It was agreed to use the flexible butyl resin sealant ConSeal CS-440 manufactured by Concrete Sealant , Inc. to seal the reinforced concrete culvert pipes.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | The ground fluids encountered in this area likely contained petroleum-based materials , which needed to be kept out of the storm sewer system in order to prevent deterioration of the pipe joint materials. | It was agreed to use the flexible butyl resin sealant ConSeal CS-440 manufactured by Concrete Sealant , Inc. to seal the reinforced concrete culvert pipes.
2000-09-19 | Right-of-Way | Fencing | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The Right-of-Way negotiations for two properties that adjoined the project were not complete at the time this project began construction. These properties consisted of an employee parking lot and a bus compound. | It became necessary to construct a temporary six-foot tall chain link security fence along these properties as part of a Right-of-Way concession.
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | The Right-of-Way negotiations for two properties that adjoined the project were not complete at the time this project began construction. These properties consisted of an employee parking lot and a bus compound. | It became necessary to construct a temporary six-foot tall chain link security fence along these properties as part of a Right-of-Way concession.
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | The Right-of-Way negotiations for two properties that adjoined the project were not complete at the time this project began construction. These properties consisted of an employee parking lot and a bus compound. | It became necessary to construct a temporary six-foot tall chain link security fence along these properties as part of a Right-of-Way concession.
2000-09-19 | Design | Adjacent Projects | RELOCATION(O) | 6 | CAMPBELL | The City of Louisville requested that the Right-of-Way fence and accessories on the subject project be vinyl coated. This coating was requested in order to match the proposed Right-of-Way fences on future adjacent projects on the roadway and to enhance t | The fence on this project was changed to six-gauge black vinyl fused and bonded fence fabric and black painted posts , rails and fittings.
2000-09-19 | Design | Adjacent Projects | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The City of Louisville requested that the Right-of-Way fence and accessories on the subject project be vinyl coated. This coating was requested in order to match the proposed Right-of-Way fences on future adjacent projects on the roadway and to enhance t | The fence on this project was changed to six-gauge black vinyl fused and bonded fence fabric and black painted posts , rails and fittings.
2000-09-19 | Design | Adjacent Projects | RELOCATION(O) | 6 | CAMPBELL | The City of Louisville requested that the Right-of-Way fence and accessories on the subject project be vinyl coated. This coating was requested in order to match the proposed Right-of-Way fences on future adjacent projects on the roadway and to enhance t | The fence on this project was changed to six-gauge black vinyl fused and bonded fence fabric and black painted posts , rails and fittings.
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | In order to minimize the amount of water , which needed to be excavated and disposed of , it was agreed to limit the undercutting between Station 156+61 and 160+00 and Stations 160+00 and 162+50 to a depth of 12 inches below the original subgrade. As a | It was agreed to use an additional layer of the woven geotextile product CEF 2044 produced by Amoco due to its high strength characteristics. In both areas the high strength geotextile fabric was not pinned. The seams were sewn together in accordance wi
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | In order to minimize the amount of water , which needed to be excavated and disposed of , it was agreed to limit the undercutting between Station 156+61 and 160+00 and Stations 160+00 and 162+50 to a depth of 12 inches below the original subgrade. As a | It was agreed to use an additional layer of the woven geotextile product CEF 2044 produced by Amoco due to its high strength characteristics. In both areas the high strength geotextile fabric was not pinned. The seams were sewn together in accordance wi
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | In order to minimize the amount of water , which needed to be excavated and disposed of , it was agreed to limit the undercutting between Station 156+61 and 160+00 and Stations 160+00 and 162+50 to a depth of 12 inches below the original subgrade. As a | It was agreed to use an additional layer of the woven geotextile product CEF 2044 produced by Amoco due to its high strength characteristics. In both areas the high strength geotextile fabric was not pinned. The seams were sewn together in accordance wi
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | The Right-of-Way fence was to be mounted to the tops of the gravity walls. However , this mounting would result in a hole at the top of the walls , which may have led to cracking at each location where the fence was to be mounted on the wall. | An alternate method was used to mount the fence on the walls (See Attached Detail Sheet). It is recommended that the attached detail be used on walls that have a narrow width.
2000-09-19 | Drainage | Existing Pipe | RELOCATION(O) | 6 | CAMPBELL | Native materials excavated from the pipe trenches could not be used as pipe backfill. | In order to construct a stable drainage system in this area , it was necessary to use Crushed Aggregate Size No. 57 as pipe bedding and as a backfill material for the pipe trenches.
2000-09-19 | Design | Adjacent Projects | RELOCATION(O) | 6 | CAMPBELL | The City of Louisville requested that the exposed side of the gravity walls constructed alongside Central Avenue have uniform texturing via the use of form liners. This work was requested in order to provide a suitable match for other proposed masonry tr | Form liners were added to the front face of the gravity walls to a depth of 12 inches below the proposed finished grade.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | An area of unstable subgrade was encountered between Station 136+00 and Rt. Station 143+53. | In order to maintain roadway base stability , a layer of Geotextile Fabric Type III was installed on the subgrade before the Dense Graded Aggregate was placed.
2000-09-19 | Right-of-Way | Fencing | RELOCATION(O) | 6 | CAMPBELL | The Right-of-Way fence was to be mounted to the tops of the gravity walls. However , this mounting would result in a hole at the top of the walls , which may have led to cracking at each location where the fence was to be mounted on the wall. | An alternate method was used to mount the fence on the walls (See Attached Detail Sheet). It is recommended that the attached detail be used on walls that have a narrow width.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | Unsuitable material was encountered on the subject project between Station 160+20 and Station 161+75. This material consisted of an off-white substance which was friable when wet and resembled clay when moist. This material also had a tendency to swell | The material was hauled off site for disposal at an approved location. It was agreed to compensate the Contractor for the additional hauling costs in excess of what it would have originally cost to haul this material to the designated stockpile site in a
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Unsuitable material was encountered on the subject project between Station 160+20 and Station 161+75. This material consisted of an off-white substance which was friable when wet and resembled clay when moist. This material also had a tendency to swell | The material was hauled off site for disposal at an approved location. It was agreed to compensate the Contractor for the additional hauling costs in excess of what it would have originally cost to haul this material to the designated stockpile site in a
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | Unsuitable material was encountered on the subject project between Station 160+20 and Station 161+75. This material consisted of an off-white substance which was friable when wet and resembled clay when moist. This material also had a tendency to swell | The material was hauled off site for disposal at an approved location. It was agreed to compensate the Contractor for the additional hauling costs in excess of what it would have originally cost to haul this material to the designated stockpile site in a
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | An area of unstable subgrade was encountered between Station 136+00 and Rt. Station 143+53. | In order to maintain roadway base stability , a layer of Geotextile Fabric Type III was installed on the subgrade before the Dense Graded Aggregate was placed.
2000-09-19 | Maintenance of Traffic | Omission | RELOCATION(O) | 6 | CAMPBELL | The contract documents did not address any special traffic control considerations for holidays , local or regional events , festivals , or special event coordination for the Kentucky Fair & Exposition Center for any of the roadways involved with the pr | The Contractor requested to remove a lane closure from Crittenden Drive in order to restore the traffic capacity of this roadway for the volume of traffic expected for the Kentucky Derby. The Contractor was directed to shore up the vertical drop off imme
2000-09-19 | Maintenance of Traffic | Omission | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The contract documents did not address any special traffic control considerations for holidays , local or regional events , festivals , or special event coordination for the Kentucky Fair & Exposition Center for any of the roadways involved with the pr | The Contractor requested to remove a lane closure from Crittenden Drive in order to restore the traffic capacity of this roadway for the volume of traffic expected for the Kentucky Derby. The Contractor was directed to shore up the vertical drop off imme
2000-09-19 | Maintenance of Traffic | Omission | RELOCATION(O) | 6 | CAMPBELL | The contract documents did not address any special traffic control considerations for holidays , local or regional events , festivals , or special event coordination for the Kentucky Fair & Exposition Center for any of the roadways involved with the pr | The Contractor requested to remove a lane closure from Crittenden Drive in order to restore the traffic capacity of this roadway for the volume of traffic expected for the Kentucky Derby. The Contractor was directed to shore up the vertical drop off imme
2000-09-19 | Drainage | Existing Pipe | RELOCATION(O) | 6 | CAMPBELL | Native materials excavated from the pipe trenches could not be used as pipe backfill. | In order to construct a stable drainage system in this area , it was necessary to use Crushed Aggregate Size No. 57 as pipe bedding and as a backfill material for the pipe trenches.
2000-09-19 | Drainage | Existing Pipe | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Native materials excavated from the pipe trenches could not be used as pipe backfill. | In order to construct a stable drainage system in this area , it was necessary to use Crushed Aggregate Size No. 57 as pipe bedding and as a backfill material for the pipe trenches.
2000-09-19 | Environmental | Pollution | RELOCATION(O) | 6 | CAMPBELL | An impermeable barrier needed to be constructed between Stations 160+00 and 162+50 as a result of the work plan that was approved by the Superfund agency. | It was agreed to install an 8-mil polyethylene barrier on the remaining materials in this area after the storm system was completed and after the high strength geotextile fabric was installed. This impermeable barrier extended full width under the roadwa
2000-09-19 | Utilities | Omission | RELOCATION(O) | 6 | CAMPBELL | The existing six-inch sanitary sewer line that served Parcel 104 adjacent to the project was found to tie directly into an existing manhole that was designated to be replaced. The existing manhole was brick lined and in poor condition. | An additional sanitary sewer manhole tie-in was installed at Lt. Station 172+20 even though the project documents did not indicate that this work would be needed.
2000-09-19 | Utilities | Omission | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The existing six-inch sanitary sewer line that served Parcel 104 adjacent to the project was found to tie directly into an existing manhole that was designated to be replaced. The existing manhole was brick lined and in poor condition. | An additional sanitary sewer manhole tie-in was installed at Lt. Station 172+20 even though the project documents did not indicate that this work would be needed.
2000-09-19 | Utilities | Omission | RELOCATION(O) | 6 | CAMPBELL | The existing six-inch sanitary sewer line that served Parcel 104 adjacent to the project was found to tie directly into an existing manhole that was designated to be replaced. The existing manhole was brick lined and in poor condition. | An additional sanitary sewer manhole tie-in was installed at Lt. Station 172+20 even though the project documents did not indicate that this work would be needed.
2000-09-19 | Drainage | Pipe Sizing | RELOCATION(O) | 6 | CAMPBELL | The Louisville Water Company felt that the proposed pipe crossing Central Avenue at Station 179+20 was insufficient to support future development in the area. | Eight-inch Ductile Iron Pipe was installed inside the 18-inch steel encasement pipe that was constructed in lieu of the six-inch Ductile Iron Pipe that was originally required by the contract.
2000-09-19 | Drainage | Pipe Sizing | RELOCATION(O) | 6 | CAMPBELL | The Louisville Water Company felt that the proposed pipe crossing Central Avenue at Station 179+20 was insufficient to support future development in the area. | Eight-inch Ductile Iron Pipe was installed inside the 18-inch steel encasement pipe that was constructed in lieu of the six-inch Ductile Iron Pipe that was originally required by the contract.
2000-09-19 | Environmental | Pollution | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | An impermeable barrier needed to be constructed between Stations 160+00 and 162+50 as a result of the work plan that was approved by the Superfund agency. | It was agreed to install an 8-mil polyethylene barrier on the remaining materials in this area after the storm system was completed and after the high strength geotextile fabric was installed. This impermeable barrier extended full width under the roadwa
2000-09-19 | Drainage | Pipe Sizing | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The Louisville Water Company felt that the proposed pipe crossing Central Avenue at Station 179+20 was insufficient to support future development in the area. | Eight-inch Ductile Iron Pipe was installed inside the 18-inch steel encasement pipe that was constructed in lieu of the six-inch Ductile Iron Pipe that was originally required by the contract.
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | Oil drums and other possible contaminants were discovered while performing geotechnical investigations on site between Station 160+00 and Station 162+00. The soil in this area was extremely unstable. | A series of special temporary access roads had to be constructed in order to allow the Environmental Consultant access to this area to perform required testing and sampling. This work required the use of a large quantity of shot rock.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | An area of unstable subgrade was encountered between Station 136+00 and Rt. Station 143+53. | In order to maintain roadway base stability , a layer of Geotextile Fabric Type III was installed on the subgrade before the Dense Graded Aggregate was placed.
2000-09-19 | Construction | Delays | RELOCATION(O) | 6 | CAMPBELL | There were concerns regarding whether the project would meet it's deadline. | The Contractor was requested to use high early strength cement concrete mixes in the pavement in order to expedite the contract as much as possible.
2000-09-19 | Construction | Delays | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | There were concerns regarding whether the project would meet it's deadline. | The Contractor was requested to use high early strength cement concrete mixes in the pavement in order to expedite the contract as much as possible.
2000-09-19 | Environmental | Contaminated Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Oil drums and other possible contaminants were discovered while performing geotechnical investigations on site between Station 160+00 and Station 162+00. The soil in this area was extremely unstable. | A series of special temporary access roads had to be constructed in order to allow the Environmental Consultant access to this area to perform required testing and sampling. This work required the use of a large quantity of shot rock.
2000-09-19 | Environmental | Pollution | RELOCATION(O) | 6 | CAMPBELL | An impermeable barrier needed to be constructed between Stations 160+00 and 162+50 as a result of the work plan that was approved by the Superfund agency. | It was agreed to install an 8-mil polyethylene barrier on the remaining materials in this area after the storm system was completed and after the high strength geotextile fabric was installed. This impermeable barrier extended full width under the roadwa
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | Oil drums and other possible contaminants were discovered while performing geotechnical investigations on site between Station 160+00 and Station 162+00. The soil in this area was extremely unstable. | A series of special temporary access roads had to be constructed in order to allow the Environmental Consultant access to this area to perform required testing and sampling. This work required the use of a large quantity of shot rock.
2000-09-19 | Construction | Delays | RELOCATION(O) | 6 | CAMPBELL | There were concerns regarding whether the project would meet it's deadline. | The Contractor was requested to use high early strength cement concrete mixes in the pavement in order to expedite the contract as much as possible.
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | A section of exposed grade from Station 156+61 to Station 158+80 was found to be unstable. | The Geotechnical Branch of the Division of Materials recommended removing the existing treated soil type material down to the founding in-situ clay layer and placing Type III Geotextile Fabric. This area was then brought up to the proposed subgrade eleva
2000-09-19 | Design | Adjacent Projects | RELOCATION(O) | 6 | CAMPBELL | The City of Louisville requested that the exposed side of the gravity walls constructed alongside Central Avenue have uniform texturing via the use of form liners. This work was requested in order to provide a suitable match for other proposed masonry tr | Form liners were added to the front face of the gravity walls to a depth of 12 inches below the proposed finished grade.
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | A section of exposed grade from Station 156+61 to Station 158+80 was found to be unstable. | The Geotechnical Branch of the Division of Materials recommended removing the existing treated soil type material down to the founding in-situ clay layer and placing Type III Geotextile Fabric. This area was then brought up to the proposed subgrade eleva
2000-09-19 | Right-of-Way | Fencing | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The Right-of-Way fence was to be mounted to the tops of the gravity walls. However , this mounting would result in a hole at the top of the walls , which may have led to cracking at each location where the fence was to be mounted on the wall. | An alternate method was used to mount the fence on the walls (See Attached Detail Sheet). It is recommended that the attached detail be used on walls that have a narrow width.
2000-09-19 | Environmental | Contaminated Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | Crushed barrels containing oil were encountered on the project. | The Division of Environmental Analysis and the Superfund agencies were contacted regarding this matter. LAW Engineering was retained as an advisor to the Department in order to help proceed with the mitigation process for the contamination found in this
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | Crushed barrels containing oil were encountered on the project. | The Division of Environmental Analysis and the Superfund agencies were contacted regarding this matter. LAW Engineering was retained as an advisor to the Department in order to help proceed with the mitigation process for the contamination found in this
2000-09-19 | Design | Adjacent Projects | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The City of Louisville requested that the exposed side of the gravity walls constructed alongside Central Avenue have uniform texturing via the use of form liners. This work was requested in order to provide a suitable match for other proposed masonry tr | Form liners were added to the front face of the gravity walls to a depth of 12 inches below the proposed finished grade.
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | Crushed barrels containing oil were encountered on the project. | The Division of Environmental Analysis and the Superfund agencies were contacted regarding this matter. LAW Engineering was retained as an advisor to the Department in order to help proceed with the mitigation process for the contamination found in this
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | A field review of the project showed that there were areas of unstable subgrade in the area where the existing Crittenden Drive was widened at Rt. Station 143+53 and Rt. Station 146+61. | This area was undercut by a depth of two feet and Geotextile Fabric Type III was used and backfilled with Crushed Aggregate Size No. 3. An edge drain type system consisting of perforated 4-inch pipe and 4-inch non-perforated pipe was installed in this ar
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | A field review of the project showed that there were areas of unstable subgrade in the area where the existing Crittenden Drive was widened at Rt. Station 143+53 and Rt. Station 146+61. | This area was undercut by a depth of two feet and Geotextile Fabric Type III was used and backfilled with Crushed Aggregate Size No. 3. An edge drain type system consisting of perforated 4-inch pipe and 4-inch non-perforated pipe was installed in this ar
2000-09-19 | Geotechnical | Unsuitable Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | A field review of the project showed that there were areas of unstable subgrade in the area where the existing Crittenden Drive was widened at Rt. Station 143+53 and Rt. Station 146+61. | This area was undercut by a depth of two feet and Geotextile Fabric Type III was used and backfilled with Crushed Aggregate Size No. 3. An edge drain type system consisting of perforated 4-inch pipe and 4-inch non-perforated pipe was installed in this ar
2000-09-19 | Geotechnical | Unsuitable Material | RELOCATION(O) | 6 | CAMPBELL | A section of exposed grade from Station 156+61 to Station 158+80 was found to be unstable. | The Geotechnical Branch of the Division of Materials recommended removing the existing treated soil type material down to the founding in-situ clay layer and placing Type III Geotextile Fabric. This area was then brought up to the proposed subgrade eleva
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | The contract documents for the project required construction of a storm sewer under Central Avenue from Station 156+61 to Station 159+88. The existing soil in this area had been treated for lead contamination in accordance with the project documents. Ho | It was necessary to construct a base pad , mobilize a frac tank on site , and pump the water on site where it was stored until a proper disposal method could be determined.
2000-09-19 | Environmental | Contaminated Material | PREFINANCD CONVRSN(O) | 6 | CAMPBELL | The contract documents for the project required construction of a storm sewer under Central Avenue from Station 156+61 to Station 159+88. The existing soil in this area had been treated for lead contamination in accordance with the project documents. Ho | It was necessary to construct a base pad , mobilize a frac tank on site , and pump the water on site where it was stored until a proper disposal method could be determined.
2000-09-19 | Environmental | Contaminated Material | RELOCATION(O) | 6 | CAMPBELL | The contract documents for the project required construction of a storm sewer under Central Avenue from Station 156+61 to Station 159+88. The existing soil in this area had been treated for lead contamination in accordance with the project documents. Ho | It was necessary to construct a base pad , mobilize a frac tank on site , and pump the water on site where it was stored until a proper disposal method could be determined.
2000-05-17 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | The plan quantity of Concrete-CL AAA was underestimated. The plan quantity was originally 2043.2 cubic meters. However , an error of 120.5 cubic meters was found. | As per KY Specification 609.04.01 the quantity in excess of 2 percent was paid at contract price.
2000-05-17 | Design | Omission | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | No quantities were established for undercut and refill. | An additional quantity of excavation was set up on the contract.
2000-05-17 | Design | Omission | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | A pay item for a manual air release valve was omitted from the original contract and the utility designer requested that this item be included in the contract. | A Change Order compensated the Contractor for supplying and installing one manual air release valve in the 200-mm water main located Lt. Station 1+140.
2000-05-17 | Erosion Control Plan | Seeding | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | The Landscape Engineer recommended reseeding some areas with special seed. | An item for Special Seed-Sericea Lespedeza was established.
2000-05-17 | Geotechnical | Piling/Drilled Shaft | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | After the Division of Materials , Geotechnical Branch reviewed the cores from the shaft sites , it was determined that the Contractor should be compensated for the actual quantities used. | The quantities for Drilled Shaft 2135mm Common were decreased and the quantities for Drilled Shaft 2135mm Rock were increased. Also the quantities for the pay items Piles-Steel HP 310x79 and Test Piles were increased to compensate the contractor for the
2000-05-17 | Structures | Erosion Control | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | There was insufficient erosion control set up for the new bridge spanning the Kentucky River. | The Contractor was requested to place Rip-Rap for erosion control on slopes around End Bents 1 & 2. The stone was placed 5 feet outside the barrier wall limits on each side extending down to the bottom of the dirt slope.
2000-05-17 | Utilities | Inaccurate Location | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | While excavating for an entrance pipe located Lt. KY 52 , a 150mm sewer main was discovered closer to the road than what was shown on the plans. Consequently , the location of the entrance pipe would interfere with the culvert extension at KY 52 Lt. St | The sewer main was relocated and the Contractor was compensated for supplying and installing the approximately 39.6 meters of 150mm sewer main that was needed to reroute around the work area.
2000-05-17 | Structures | Guardrail | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | There was an oversight on the plans regarding the guardrail to bridge end connector. The Type A-1 Connector , which is used on divided highways , was set up in the plans. | A pay item for Guardrail Connector to Bridge End Type A-1 was deleted and the pay item Guardrail Connector to Bridge End Type A was added to the contract.
2000-05-17 | Design | Drainage | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | An existing pipe at KY 52 was to be removed. However , it was determined that if this pipe was removed it would leave a place for possible settlement and the trench would have to be filled with DGA and Bit. Base. | The decision was made to safeload the pipe in order to eliminate settlement in this area.
2000-05-17 | Geotechnical | Soils | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | During excavation Rt. Station 1+340-1+420 , water was seeping out from the sand layer on top and the shale , which made the sand slope unstable. | A bench was cut approximately 3 meters wide throughout this area and geotextile fabric and Channel Lining class III was used to stabilize the slope and allow drainage in this area.
2000-05-17 | Drainage | Ponding | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | While excavating for a pipe located Mainline Station 1+035 , a large quantity of water was discovered in the trench. | To correct this problem , perforated pipe was installed along the culvert pipe and a perforated pipe headwall was installed at the outlet.
2000-05-17 | Traffic | Lighting | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | There were concerns about nighttime visibility on the new bridge. | After a request from county officials to place lights on the bridge , the Contractor was requested to install PVC conduit through the barrier wall and modify the wall for pole bases and junction boxes as per Central Office Division of Traffic guidelines.
2000-05-17 | Structures | Piling/Drilled Shaft | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | There were concerns about the close proximity of Piers 5 & 6 to the water's edge. | The pay item Permanent Casings was added to the contract. This item compensated the Contractor for supplying and installing permanent 5/8-inch casing walls. In addition , the Contractor was allowed to use rings in lieu of spiral reinforcement in the do
2000-05-17 | Geotechnical | Investigation | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | The Geotechnical Branch of the Division of Materials requested that extra depth be obtained for several of the drilled shaft locations. | A pay item , Subsurface Exploration-Extra was added to the contract in order to compensate the Contractor for the extra depth as per Special Note for Drilled Shafts.
2000-05-17 | Design | Quantities | SAFETY-HAZARD ELIM(P) | 9 | ROWAN | An area located on the mainline from Station 1+000 to Station 1+460 required a rock (shale) cut , which was originally set-up to be undercut 0.2 meters. However , this area was undercut 0.3 meters and refilled with dirt for lime stabilization. | An additional quantity of roadway excavation was established to compensate the contractor for the extra 0.1 meter of cut plus refill.
2000-05-17 | Geotechnical | Elevations | PAVEMENT REHAB-INT(P) | 99 | ROWAN | Suitable rock for the culvert pipe at Sta. 83+60 was encountered at a lower elevation than the planned elevation. It was mentioned that the geotechnical investigation of the project area was probably insufficient since undercutting at various locations w | Additional quantities of concrete were needed in order to install the culvert pipe on a stable foundation.
2000-05-17 | Geotechnical | Slides | PAVEMENT REHAB-INT(P) | 99 | ROWAN | A slide occurred in the cut slope at approximate Lt. Sta. 36+00 due to the presence of moisture and the material consisting primarily of shale and alluvial formations. | Excavation , Channel Lining , and Geotextile Fabric were used to stabilize the slide.
2000-05-17 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There was insufficient drainage set up in the plans for Sta. 94+00. | A culvert pipe and headwalls were added to ensure proper drainage at this location.
2000-05-17 | Maintenance of Traffic | Changes | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There were several complaints about the phasing of the traffic control plan from the general public. In part , the commitment to Boyle County School to maintain traffic flow for buses made maintenance of traffic difficult. | The phasing of the traffic control plan was revised. The changes included use of temporary pavement stripping on the center and edge lines as necessary.
2000-05-17 | Design | Entrance | PAVEMENT REHAB-INT(P) | 99 | ROWAN | An entrance located at Lt. Sta. 52+50 had been overlooked in the design stage. | The entrance was subsequently added by permit and required installation of a 24 entrance pipe.
2000-05-17 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 99 | ROWAN | The original plans called for Type 1 Guardrail End Treatments , which were not appropriate for use along the public roadway. | Guardrail End Treatments Type 4 and Type 7 were installed at various locations to improve safety.
2000-05-17 | Erosion Control Plan | Silt Fence | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There were insufficient mechanisms set up to control and contain erosion within the disturbed limits. | A Change Order was established to add Silt Fence to the project.
2000-05-17 | Design | Guardrail | PAVEMENT REHAB-INT(P) | 99 | ROWAN | The original plans called for Type 1 Guardrail End Treatments , which were not appropriate for use along the public roadway. | Guardrail End Treatments Type 4 and Type 7 were installed at various locations to improve safety.
2000-05-17 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There was insufficient drainage set up in the plans to drain the subgrade at Sta. 60+00. | A 24 perforated pipe necessary for drainage was added via Change Order.
2000-05-17 | Environmental | Asbestos | PAVEMENT REHAB-INT(P) | 99 | ROWAN | An outhouse on Parcel 330 , being small and assumed unlikely to contain hazardous materials , had been neglected during the environmental reconnaissance of the project area. | A Change Order was needed to remove and dispose of Asbestos Containing Material found in the roof of the outhouse.
2000-05-17 | Maintenance of Traffic | Safety | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There were potentially unsafe conditions along Detour No. 1 due to fill slopes that were greater than 3:1. It was noted that a more detailed traffic control plan should have addressed this item. | Installation of 1 , 850 feet of temporary guardrail and three Type 7 End Treatments provided adequate safety measures in this area.
2000-05-17 | Construction | Safety | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There were steep , unsafe slopes at Lt. Sta. 57+50. | The slopes were flattened , which eliminated the need for guardrail. However , flattening the slopes required an extension to the length of 54 pipe at this location.
2000-05-17 | Traffic | Markings | PAVEMENT REHAB-INT(P) | 99 | ROWAN | There were no items set up in the plans for delineating turning lanes where the old US 68 met the new road. | A Change Order was needed to install Permanent Stripping and Stop Bars for turning lanes where old US 68 meets the new road.
2000-05-17 | Design | Omission | PAVEMENT REHAB-INT(P) | 99 | ROWAN | The plans showed three riffle structures , but the proposal inadvertently omitted one. | The omitted riffle structure was added by Change Order.
2000-05-17 | Erosion Control Plan | Seeding | PAVEMENT REHAB-INT(P) | 99 | ROWAN | The field inspection of the fill areas within the Right-of-Way limits revealed numerous rills and gullies. There were numerous barren areas with much of the remaining areas exhibiting sparse vegetation. Lack of vegetation success in the aforementioned a | A Change Order was established to reapply Seeding and Protection , Special Seeding , Sodding , and Agriculture Limestone.
2000-05-17 | Drainage | Omission | PAVEMENT REHAB-INT(P) | 99 | ROWAN | Detour drainage control measures had not been provided in the original plans. | Installation of temporary drainage pipes Lt. Sta. 50+00 for Detour No. 1 and Lt. Sta. 507+00 and 517+00 for Detour No. 2 was paid for via Change Order.
2000-05-17 | Right-of-Way | Coordination | PAVEMENT REHAB-INT(P) | 99 | ROWAN | The project was let while Right-of-Way litigation initiated by several property owners was still ongoing. | A Change Order was necessary to relocate the entrance shown at Lt. Sta. 78+50 to Sta. 72+25 , extend the entrances at Lt. Sta. 65+00 and Rt. Sta. 72+96 , and add an entrance at Rt. Sta. 82+00. These changes required installation of guardrail as a safet
2000-05-17 | Erosion Control Plan | Omission | PAVEMENT REHAB-INT(P) | 99 | ROWAN | Erosion and siltation of nearby ponds was occurring. It was noted that the Erosion Control Guidelines of Design Memo 8-98 were not in effect at the time this project was let. | Additional silt checks and Channel Lining Class II were added.
2000-04-05 | Pavement | Repair | RELOCATION(O) | 7 | BOYLE | The roadway surface on both directions of I-75 from Sta. 402+00 to 423+00 and on Dixie Highway contained potholes that posed a safety hazard to motorists. | A Change Order allowed the emergency work and traffic control required to repair these potholes. These sections required milling and resurfacing to maintain safe driving surfaces throughout the rest of the winter season.
2000-04-05 | Maintenance of Traffic | Omission | RELOCATION(O) | 7 | BOYLE | Necessary realignment of existing traffic signals with the traffic lane reconfigurations during the various construction phases on Dixie Highway was not addressed in the plans. | This item was addressed via Change Order.
2000-04-05 | Maintenance of Traffic | Safety | RELOCATION(O) | 7 | BOYLE | Pedestrians and school children with no bus service would have to cross the bridge on southbound I-75 from Kyle's Lane to Orchard Road. | Temporary lighting was provided as a means of pedestrian safety.
2000-04-05 | Geotechnical | Cut-Slope | RELOCATION(O) | 7 | BOYLE | There were various cut sections on the project where undercutting was not warranted or feasible. | Geotextile Fabric Type III was installed to help stabilize the subgrade in these cut sections.
2000-04-05 | Pavement | Repair | RELOCATION(O) | 7 | BOYLE | Broken and settled pavement was encountered at the northern approaches to River Road Bridge , which were adjoining this project from I-75 Sta. 424+68 to 426+50. | Twelve-inch non-reinforced PCC pavement was constructed to replace the broken and settled pavement.
2000-04-05 | Drainage | Error | RELOCATION(O) | 7 | BOYLE | There was a 2 ft error in the plans , which caused the storm sewer and three drainage boxes to be installed in the wrong location. | A Change Order allowed installation of a 15-inch Junction Box and a Curb Box Inlet Type B in order to maintain proper drainage at this location.
2000-04-05 | Traffic | Signals | RELOCATION(O) | 7 | BOYLE | An existing Signal System and utility pole on the Northeast corner of Orchard Road and Dixie Highway interfered with completion of the sidewalk and curb construction. | The existing Signal System was removed from the existing utility pole on the Northeast corner of Orchard Road and Dixie Highway and reinstalled on a new pole.
2000-04-05 | Structures | Phasing | RELOCATION(O) | 7 | BOYLE | Phased construction of the Northbound I-75 Bridge over Orchard Road had resulted in settlement cracking in the approach slabs. | Granular backfill was replaced with Flowable Fill at both bridge ends.
2000-04-05 | Design | Guardrail | RELOCATION(O) | 7 | BOYLE | Guardrail was not designed properly to protect traffic from a 2:1 slope between Ramp A and the mainline from Sta. 504+50 to 510+00. | Guardrail and End Treatments Type 1 and 2A were added at this location.
2000-04-05 | Design | Guardrail | RELOCATION(O) | 7 | BOYLE | Guardrail was not designed properly to protect traffic from a 2:1 slope between Ramp A and the mainline from Sta. 504+50 to 510+00. | Guardrail and End Treatments Type 1 and 2A were added at this location.
2000-04-05 | Geotechnical | Unsuitable Material | RELOCATION(O) | 7 | BOYLE | Unstable material was encountered in the area of the detention pond which would not safely allow the use of mowing equipment for future maintenance activities. | Special excavation operations were performed in the area of the detention pond in order to remove and refill the unstable material.
2000-04-05 | Structures | Piling/Drilled Shaft | RELOCATION(O) | 7 | BOYLE | The original bridge plans had specified Piers 1 and 2 of the Northbound I-75 bridge over Rivard Drive be located in close proximity to the existing utilities and the existing spread footings. However , this would cause conflicts with the existing utilit | The proposed spread footings were eliminated and Piers 1 and 2 were placed on Drilled Shafts.
2000-04-05 | Drainage | Bridge Ends | RELOCATION(O) | 7 | BOYLE | The Dixie Highway bridge abutment along Northbound I-75 did not drain properly to an existing Drop Box Inlet at Sta. 387+95 Right of Centerline. | A Change Order added an 8-inch plastic pipe in order to sufficiently drain the Dixie Highway bridge abutment. This item was necessary both for drainage and due to the difficulty of performing excavation in rock.
2000-04-05 | Utilities | Existing Utilities | RELOCATION(O) | 7 | BOYLE | Planned Curb Box Inlets Type A on the Dixie Highway at Lt. and Rt. Sta. 37+86. could not be used because of a conflict with underground utilities. | Drop Box Inlets Type 16G and 15 Slotted Drain pipes were installed to maintain proper drainage.
2000-04-05 | Design | Omission | RELOCATION(O) | 7 | BOYLE | Necessary thermoplastic markings , crosswalks , and left turn skips on Dixie Highway were not included in the plans. | A Change Order was established for the installation of these required items.
2000-04-05 | Design | Guardrail | RELOCATION(O) | 7 | BOYLE | The guardrail from Sta. 472+00 to 475+00 was not properly designed to provide access to the Detention Pond which was part of this project. | End Treatment Type 2A and End Treatment Type 3 were added to provide access to the Detention Pond. These end treatments required 350 LF of guardrail installation and removal.
2000-04-05 | Design | Guardrail | RELOCATION(O) | 7 | BOYLE | The guardrail from Sta. 472+00 to 475+00 was not properly designed to provide access to the Detention Pond which was part of this project. | End Treatment Type 2A and End Treatment Type 3 were added to provide access to the Detention Pond. These end treatments required 350 LF of guardrail installation and removal.
2000-04-05 | Utilities | New Utilities | RELOCATION(O) | 7 | BOYLE | The plans called for boring beneath I-75/I-71 to install a 36-inch storm sewer. | The 36 storm sewer was rerouted by raising the final grade of Orchard Road , which also eliminated the sag in Orchard Road and provided a more aesthetically pleasing slope. This change allowed the use of more shallow trenches which eliminated concerns a
2000-04-05 | Pavement | Design | RELOCATION(O) | 7 | BOYLE | There were concerns regarding the pavement design for Dixie Highway (US 27) based on its unsuitable subgrade , numerous utilities , and extremely tight working area imposed by traffic phasing. The original design would have required undercutting in an | The pavement design for US 27 was changed to include a 10-inch PCC Base widening that would tie into the existing concrete pavement which was overlaid with 1/2 inch surface course.
2000-04-05 | Maintenance of Traffic | Striping | RELOCATION(O) | 7 | BOYLE | The existing 12 permanent tape sustained damage from various traffic changes. | A Change Order was approved to replace much of the existing 12-inch permanent tape.
2000-04-05 | Pavement | Repair | RELOCATION(O) | 7 | BOYLE | The existing concrete pavement near the centerline of Dixie Highway from Sta. 40+00 to 43+50 deteriorated immediately after milling operations and exposure to vehicular traffic. | A Change Order was established to remove the pavement and construct 10-inch PCC pavement in its place.
2000-04-05 | Traffic | Lighting | RELOCATION(O) | 7 | BOYLE | Demolition and reconstruction of the old and new bridges had significantly impacted traffic in the area. There were concerns regarding visibility and safety on the Dixie Highway Bridge over I-75/I-71. | Visibility was improved by installing , removing , and relocating the temporary lighting on the Traffic Control Barrier Wall from Sta. 48+00 to 54+00 on Dixie Highway during all the various traffic phases.
2000-04-05 | Pavement | Shoulders | RELOCATION(O) | 7 | BOYLE | Mainline shoulders were being utilized to carry traffic during the various construction phases and several transverse joints had begun to fail under traffic and required immediate repair. | A Change Order was issued to allow use of load transfer assemblies in all of the mainline shoulders and to allow emergency repair work to be performed in the left shoulder of Southbound I-75.
2000-04-05 | Design | Omission | RELOCATION(O) | 7 | BOYLE | Relocation of ARTIMIS signs was not addressed on the plans. | A Change Order was approved to remove and reinstall the ARTIMIS 1/10 mile reference markers from the exiting median barrier wall to the new median barrier wall along the entire length of the project.
2000-04-05 | Drainage | Bridge Ends | RELOCATION(O) | 7 | BOYLE | Insufficient drainage was established for the bridge deck. It was deemed necessary to provide a more maintainable drainage system for the structure. | Addition of a manhole and fiberglass pipe allowed the deck drainage to flow with the bridge slope to the north end of the structure at Abutment #1.
2000-04-05 | Right-of-Way | Fencing | RELOCATION(O) | 7 | BOYLE | Part of stockade fence behind a residence on Orchard Road was missing. | The missing portion of fence was replaced in order to provide a tie-in to the Right-of-Way fence.
2000-04-05 | Geotechnical | Slides | RELOCATION(O) | 7 | BOYLE | A slide knocked down 600 linear feet of an existing 8-inch chain link fence , which was called for in the plans from Sta. 502+00 to 508+00 Right of Centerline on I-75 Northbound. The fence could not be reinstalled in the plan locations , due to the pre | The fence was moved back a distance and attached to guardrail posts to prevent further sliding of the fence.
2000-04-05 | Traffic | Safety | RELOCATION(O) | 7 | BOYLE | There was insufficient protection provided for the traveling public at a newly installed Cantilever Sign Structure and its base. The aforementioned problem was the result of an oversight in the plans , which utilized the existing cantilever sign structu | Four-hundred linear feet of guardrail , Guardrail End Treatments Types 1 & 2A , and Guardrail Connector to Bridge End Type A-1 were installed at Sta. 405+00 Right of centerline on Northbound I-75.
2000-04-05 | Maintenance of Traffic | Striping | RELOCATION(O) | 7 | BOYLE | There was not proper striping set up for the final lane configuration. | The existing 12 gore tape from entrance ramps on or adjacent to this project was removed and replaced with broken edge lines (6 skip line) to provide additional merging length. Also , thermoplastic arrows were installed in Exit Drop Lanes at I-75 Northb
2000-04-04 | Utilities | New Utilities | MAJOR WIDENING(O) | 7 | FAYETTE | There was a lack of sufficient cover for water utilities under the proposed roadway after the subgrade was placed at Spencer Drive Approach Sta. 48+43 to 49+60 , the entrance to Parcel 53 , and Rt. Sta. 503+16. | Water utilities consisting of a 12-inch , an 8-inch , and a 6-inch Ductile Iron Pipe were relocated.
2000-04-04 | Drainage | Elevation | MAJOR WIDENING(O) | 7 | CLARK | The drainage system located at Lt. Sta. 49+00 on Boat Ramp Road could not be built as designed due to changes in ground elevation caused by fill material that had been placed in the drainage area by the City of Wilder. These unintended changes were in pa | The roadway drainage system had to be revised to move the outlet point to Sta. 47+00.
2000-04-04 | Traffic | Omission | MAJOR WIDENING(O) | 7 | CLARK | Removal Pavement Markers and Pavement Markers Type V-M W were both left out of the plans. | These items were added via Change Order.
2000-04-04 | Construction | Ride Quality | MAJOR WIDENING(O) | 7 | CLARK | Upon completion of the project , there was a short section of old KY 9 that was left with poor rideability. John's Hill Road was also in poor condition. | A Change Order was established to resurface these sections.
2000-04-04 | Structures | Retaining Walls/MSE | MAJOR WIDENING(O) | 7 | CLARK | Due to variations in the RDZ , a Change Order was necessary to allow ongoing design changes to the Tieback Retaining Walls as needed. | The design changes included the addition of two anchors for Retaining Wall R1 to eliminate a low point. Aside from being aesthetically unappealing , the low point was determined to cause drainage problems if not corrected. A special tieback drill had t
2000-04-04 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 7 | FAYETTE | The ditches located right of Sta. 136+00 to 140+00 needed additional erosion control. However , this item had not been called for on the original plans. | A Change Order was established to add Channel Lining Class II for lining the ditches.
2000-04-04 | Design | Entrance | MAJOR WIDENING(O) | 7 | CLARK | An entrance that was required to a property off Banklick Road was left out of the plans. Unfortunately , all excess material had been wasted by that time. | A Change Order allowed the Contractor to excavate additional material needed to construct the entrance.
2000-04-04 | Design | Omission | MAJOR WIDENING(O) | 7 | CLARK | There was an oversight with regards to including the appropriate bid items in the plan summary. The bid proposal contained a special note with regard to Load Cells. However , this item was being used for the first time and did not have an average bid p | A Change Order was set up to allocate funds for tieback wall instrumentation , slope inclinometers , survey points , and load cells. All of these items were required to measure the loads in the anchor tendons and movement in the wall or water table.
2000-04-04 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 7 | FAYETTE | There were insufficient Erosion Control items included on the original plans because the Erosion Control requirements of Design Memo 8-98 were not effective at the time the plans were made. | A Change Order allowed the use of Channel Lining Class II , Silt Fence , Silt Trap Type A , and Modified Silt Trap to provide proper drainage control on the project.
2000-04-04 | Drainage | Ditches | MAJOR WIDENING(O) | 7 | CLARK | There were concerns regarding the potential for water to overflow a ditch onto the roadway surface and freeze. It was pointed out that the overflow problem was in part due to accumulated debris in the existing ditches and lack of maintenance activities. | A Change Order was established for the cost of excavating the ditch.
2000-04-04 | Drainage | Ponding | MAJOR WIDENING(O) | 7 | CLARK | Ponding of water was occurring at a Drop Box Inlet due to the relatively flat ditch grade on the right side of the new KY 9 centerline at Sta. 102+24. | The Drop Box Inlet was lowered by one foot to allow for proper drainage and prevent future ponding.
2000-04-04 | Right-of-Way | Easements | MAJOR WIDENING(O) | 7 | FAYETTE | A delay was encountered when trying to acquire right of entry for Parcel No. 53. | Temporary pavement wedging was constructed; project phasing and traffic control were revised from Sta. 100+50 to 504+00 to prevent a disturbance to this property.
2000-04-04 | Construction | Revisions | MAJOR WIDENING(O) | 7 | CLARK | Additional changes were required due to design modifications necessitated by variations in the RDZ along the Tieback Retaining Walls. | A Change Order was approved for the increased square footage of wall facing and masonry coating as well as additional anchors to be drilled at the impacted areas.
2000-04-04 | Drainage | Flooding | MAJOR WIDENING(O) | 7 | CLARK | A heavy rain on January 3 , 2000 , forced the closure of KY 9 due to flooding. Flooding problems were exasperated by the lack of drainage though various DBI's which had become clogged with floating straw. | A Change Order was established to deal with Drainage and Flood Repair. The required remedial action included cleaning the DBI's , re-grading , and shoulder work. Additionally , Walls L1 and L2 were backfilled to the top of the wall with an impermeabl
2000-04-04 | Drainage | Ditches | MAJOR WIDENING(O) | 7 | CLARK | The grade of an inlet ditch in the drainage area adjacent to Sta. 83+00 had been designed as a 2:1 slope , but was determined to be too steep. There were concerns that drainage would spill over the tieback wall during a significant rain fall event. | The ditch grade was flattened and a manhole was installed.
2000-04-04 | Construction | Permits | MAJOR WIDENING(O) | 7 | FAYETTE | An entrance located Right of Sta. 134+61 was constructed by permit and hence was not in the plans. | A Change Order was needed to construct standard curb and gutter to tie in with the curb and gutter at this entrance.
2000-04-04 | Traffic | Omission | MAJOR WIDENING(O) | 7 | CLARK | Thermoplastic Markers were not included in the plans. | Thermoplastic Markers were added per instruction from The Division of Traffic.
2000-04-04 | Maintenance of Traffic | Striping | MAJOR WIDENING(O) | 7 | FAYETTE | There was inadequate Temporary Pavement Striping set up to complete the project phasing. | A Change Order was approved to use additional Temporary Pavement Striping.
2000-04-04 | Construction | Earthwork | MAJOR WIDENING(O) | 7 | CLARK | Subsequent to the drilling and blasting operations in the area , poor quality rock was encountered from Sta. 147+50 to 154+50 left of the centerline. | Additional Excavation was added through a Change Order. This additional excavation was required to construct a 3:1 west slope.
2000-04-04 | Geotechnical | Investigation | MAJOR WIDENING(O) | 7 | CLARK | It was difficult to establish an appropriate design for a Tieback Retaining Wall as a result of variations in the actual Rock Disintegration Zone (RDZ) locations as compared to the plan locations. | A Change Order was issued for drilling additional core holes at various soldier pile locations along the wall. The variations in RDZ subsequently delayed the soldier pile drilling operations in order to allow for probing to determine the approximate loca
2000-04-04 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 7 | CLARK | Gray shale was discovered at the end of Wall R2 under the wing. There were concerns about the shale being susceptible to rapid weathering and consequent undermining. | The underlying gray shale was replaced with Crushed Aggregate No. 2.
2000-04-04 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 7 | FAYETTE | Unforeseen subsurface drainage was encountered in the mainline subgrade. | Perforated pipe was installed to the Left of Sta. 123+90.
2000-04-04 | Construction | Subsurface | MAJOR WIDENING(O) | 7 | CLARK | In the superelevated section , an undesirable pocket of DGA formed below the underdrain system. | Consequently , the subgrade in the ditch was exposed to allow the subgrade to drain , thus avoiding soft areas in the shoulder.
2000-04-04 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 7 | CLARK | It was determined that it would be beneficial to facilitate a complete closure of the section of KY 9 just north of existing Carlisle Road to just south of Johns Hill Road. | This was accomplished by maintaining access to Carlisle Road and Banklick Road via a detour across property previously established on the Construction Easement. While additional Detour Signing was needed , several items such as Temporary Guardrail , Tr
2000-04-04 | Pavement | Design | MAJOR WIDENING(O) | 7 | FAYETTE | Due to rapidly progressing residential , business , and industrial development in the area and its impact on the future Average Daily Traffic , the pavement design was determined to be inadequate. | It was decided to modify the use of performance grade asphalt binders on the project. Due to increased development , this project warranted the use of PG70-22 in lieu of PG64-22 on the final asphalt base and surface for the mainline and turning lanes.
2000-04-04 | Maintenance of Traffic | Omission | MAJOR WIDENING(O) | 7 | CLARK | Subsequent to phased construction of KY 9 at Old Carlisle Road , Vine Street , Boat Ramp Road , and Banklick Road temporary access was needed. | Dense Grade Aggregate (DGA) was used for temporary accesses.
2000-04-04 | Geotechnical | Unsuitable Material | MAJOR WIDENING(O) | 7 | CLARK | There were variations in the RDZ from Sta. 141+50 to Sta. 147+70. | Free Draining Backfill was added along the shear key.
2000-04-04 | Geotechnical | Safety | MAJOR WIDENING(O) | 7 | CLARK | The installation of piezometers and inclinometers at various locations below and above the walls was originally the responsibility of the Geotechnical Branch. However , the close proximity of power lines did not provide enough clearance needed for the D | Installation of these devices was deferred to the Contractor via Change Order.
2000-02-25 | Drainage | Ponding | RELOCATION(O) | 12 | JOHNSON | Unpredictable ground water seepage was occurring in the pavement between the left driving lane and the storage lane at various locations throughout the five lane section of the project. | A Change Order was issued to install an underdrain system in order to intercept the ground water seepage. This item included all equipment and labor to install a 12-inch fin drain between the driving lane and storage lane , non-perforated pipe to the ex
2000-02-25 | Design | Access | RELOCATION(O) | 12 | JOHNSON | The Mayor of Corbin requested that a four foot sidewalk and entrance pavement be added on the left side of 18th Street from approximate Sta. 168+50 to the Corbin Bypass intersection. | A Change Order was implemented per the request of the Mayor. The area was well developed with both residential and commercial properties , which warranted the change. Thirty two additional workings day were allowed for this Change Order.
2000-02-25 | Utilities | Relocation | RELOCATION(O) | 12 | JOHNSON | There were numerous utilities in the same location. Specifically , a gas line was installed at the location of the proposed sewer line. | A Change Order was necessary to conduct design exploration to locate the exact location of underground utilities in order to facilitate the redesign of sewer line construction at various locations.
2000-02-25 | Geotechnical | Embankment Stabilization | RELOCATION(O) | 12 | JOHNSON | The Geotechnical Branch requested the use of Mechanical Roadbed Stabilization be changed. | Mechanical Roadbed Stabilization was replaced with Fabric underlain Granular Embankment resulting in a decrease of $112 , 960.
2000-02-25 | Utilities | Relocation | RELOCATION(O) | 12 | JOHNSON | It was necessary to avoid the existing gas and telephone lines that were occupying the proposed location of sewer lines. However , the local utility company requires ductile iron pipe and granular backfill be used under all pavement. | The contractor was paid a lump sum to install 12 ductile iron pipe (DIP) , 8 DIP crossing , and 6 laterals in the existing roadway from Sta. 118+32 to Sta. 123+72 under traffic. The extra cost included additional stone backfill , removal of existing P
2000-02-25 | Construction | Contracts | RELOCATION(O) | 12 | JOHNSON | It was noted that 10 , 000 SY of Geotextile Fabric intended for embankment working platform were omitted from the original contract. | A Change Order adding these quantities was approved.
2000-02-25 | Utilities | New Utilities | RELOCATION(O) | 12 | JOHNSON | There were concerns about a 12 sewer line construction damaging a nearby building. While considering the alternatives , it was important to avoid a court injunction which could halt construction and/or result in a contractor's claim. | It was determined that a bore would be most economical and viable solution to facilitate the sewer line construction and avoid a delay. The proposed sewer line installation was done by open trench method. The contractor was compensated for non-typical b
2000-02-25 | Erosion Control Plan | Omission | RELOCATION(O) | 12 | JOHNSON | The plans did not conform to the requirements of Design Memo No. 8-98. | Silt Traps , Silt Checks , Silt Fence , and Straw Bales were selectively placed throughout the project area.
2000-02-25 | Design | Underground Tank | RELOCATION(O) | 12 | JOHNSON | The original bid item was set up to remove an underground tank system which consisted of one tank and the associated piping. During construction , it was discovered that two tanks were at this location. | A Change Order was necessary for the removal two underground storage tanks encountered during the construction phase in Parcel No. 97 and Parcel No. 6.
2000-02-25 | Drainage | Elevation | RELOCATION(O) | 12 | JOHNSON | The original construction of two entrances at Sta. 170+33 and Sta. 170+70 were causing drainage problems. The entrances were constructed with excessive swale , which caused scraping of the underside of truck trailers against the concrete. | A Change Order was issued to modify these two entrances. However , during the reconstruction of the entrances , the sewer lines were damaged. This item included the cost of repairing damage to the sewer lateral left of Sta. 170+33 caused by modifying
2000-02-25 | Utilities | Plans | RELOCATION(O) | 12 | JOHNSON | The plan summaries specified gate valves whereas the layout sheets indicated butterfly valves. Corbin Utilities and the design engineer indicated that they intended to use butterfly valves. | A Change Order was approved to replace all 12 and 16 water gate valves with butterfly valves. Two 12 gate valves were already installed and had to be removed and replaced.
2000-02-25 | Design | Entrance | RELOCATION(O) | 12 | JOHNSON | The original location of an entrance from Sta. 139+69 to Sta. 140+09 did not accommodate future development. To enhance future development in this area , it was decided that the entrance be moved. | This change necessitated removal and reinstallation of a previously installed traffic signal consisting of two steel strain poles , the control box and the base.
2000-02-24 | Design | Entrance | RECONSTRUCTION(O) | 12 | KNOTT | Two entrances had been left out from the original plans. | A Change Order was issued to authorize construction of the two entrances on two properties near Sta. 38+75 on Quillen Chapel Road. These entrances required two 18-inch entrance pipes. One Inlet Headwall was already placed which had to be removed and res
2000-02-24 | Geotechnical | Slides | RECONSTRUCTION(O) | 12 | KNOTT | A slip occurred during the construction of a channel lined ditch (Type III) to the right of Quillen Chapel Road at Sta. 62+00 to 65+00. | A Change Order was made for an item called Special Slip Excavation. Due to the physical location of the slip , it was difficult to remove the material. It was agreed that the removed material would be deducted from the roadway excavation item.
2000-02-24 | Drainage | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The contract plans included headwalls throughout the project. However , no concrete or steel quantities were included in the bid items for the construction of these small drainage structures. | A Change Order was established to add the necessary quantities for these items.
2000-02-24 | Design | Guardrail | RECONSTRUCTION(O) | 12 | KNOTT | It was determined in the field that sufficient clearance was not available to install a Type 4 End Treatment on the access ramp between KY 1428 and KY 321 as designated in the plans. | A Type 1 End Treatment was installed in lieu of the Type 4 End Treatment.
2000-02-24 | Drainage | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The contract plans included headwalls throughout the project. However , no concrete or steel quantities were included in the bid items for the construction of these small drainage structures. | A Change Order was established to add the necessary quantities for these items.
2000-02-24 | Maintenance of Traffic | Signage | RECONSTRUCTION(O) | 12 | KNOTT | It was determined that there was not enough advance warning to the traffic detouring across the ramps during the removal of the old bridge structure. | A Change Order was established for a variable message board.
2000-02-24 | Design | Quantities | RECONSTRUCTION(O) | 12 | KNOTT | The quantities set up in the plans for concrete and steel reinforcement were not adequate. | A Change Order was issued for additional quantities of concrete and steel reinforcement to be used for permanent signing platforms.
2000-02-24 | Pavement | Design | RECONSTRUCTION(O) | 12 | KNOTT | The initial pavement design utilized Bituminous Coated Drainage Blanket and 10 of DGA. This was done to accommodate the traffic under phase construction. However , when Maintenance-of-Traffic plans indicate placing traffic on driving lanes prior to pla | The pavement design on this project was changed to 4 of DGA , 9.75 Bituminous Base and 1.5 Bituminous Surface.
2000-02-24 | Drainage | Cross Drains | RECONSTRUCTION(O) | 12 | KNOTT | There were wet areas located within ramp #3. | The wet areas required drainage blankets with 400 ft of 4-inch perforated pipe.
2000-02-24 | Pavement | Design | RECONSTRUCTION(O) | 12 | KNOTT | The initial pavement design utilized Bituminous Coated Drainage Blanket and 10 of DGA. This was done to accommodate the traffic under phase construction. However , when Maintenance-of-Traffic plans indicate placing traffic on driving lanes prior to pla | The pavement design on this project was changed to 4 of DGA , 9.75 Bituminous Base and 1.5 Bituminous Surface.
2000-02-24 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 12 | KNOTT | From approximate station 124+00 to station 142+50 it was determined that the existing original ground was very soft and unstable. | It was decided to raise the proposed grade in order to bridge over the unstable area in lieu of undercutting. This was accomplished by applying Type III Filter Fabric with a rock fill at the request of the Geotechnical Branch.
2000-02-24 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 12 | KNOTT | From approximate station 124+00 to station 142+50 it was determined that the existing original ground was very soft and unstable. | It was decided to raise the proposed grade in order to bridge over the unstable area in lieu of undercutting. This was accomplished by applying Type III Filter Fabric with a rock fill at the request of the Geotechnical Branch.
2000-02-24 | Design | Shoulders | RECONSTRUCTION(O) | 12 | KNOTT | When removing the shoulders of the Mountain Parkway for the construction of the ramp tie-ins , the surface scaled off onto the mainline leaving a jagged edge. | To prevent an uneven surface and also to seal the tie-in joints , an 18-inch edge key was milled along the mainline in the said areas.
2000-02-24 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 12 | KNOTT | Upon field inspection , it was determined that the area where a retaining wall was to be built from left station 120+00 to 123+00 was unstable. | In order to stabilize this area , Filter Fabric Type III with a No. 2 Stone Backfill was used.
2000-02-24 | Erosion Control Plan | Slope Protection | RECONSTRUCTION(O) | 12 | KNOTT | Run-off was causing erosion on the shoulders and the established vegetation along the fill slope was also showing signs of excessive erosion and/or damage. | The addition of an asphalt wedge curb and a flume (Type 1) to divert run-off to a special ditch treated with Class III channel lining was necessary to control erosion.
2000-02-24 | Structures | Omission | RECONSTRUCTION(O) | 12 | KNOTT | Bridge quantities had been specified in the bridge plans but inadvertently left off the bid proposal sheets. | A Change Order was needed to add the required quantities for two spans of beams , decks , and estimated steel reinforcement for the construction of the bridge over Mountain Parkway.
2000-02-24 | Maintenance of Traffic | Omission | RECONSTRUCTION(O) | 12 | KNOTT | A Traffic Control Plan had not been established for the construction of the bridge. | A Change Order was set up for the Traffic Control Plan. Hayden Bridge submitted the Traffic Control Plan , which was approved by the Department. The plan called for Barrels which were required for channelization. Traffic signs and 240 linear feet of C
2000-02-24 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 12 | KNOTT | Upon field inspection , it was determined that the area where a retaining wall was to be built from left station 120+00 to 123+00 was unstable. | In order to stabilize this area , Filter Fabric Type III with a No. 2 Stone Backfill was used.
2000-02-24 | Drainage | Diversion Drainage | RECONSTRUCTION(O) | 12 | KNOTT | Unanticipated run-off occurred in the area near Station 125+84. | A drainage structure was placed at Station 125+84 to control the unanticipated run-off in this area.
2000-02-24 | Drainage | Diversion Drainage | RECONSTRUCTION(O) | 12 | KNOTT | Unanticipated run-off occurred in the area near Station 125+84. | A drainage structure was placed at Station 125+84 to control the unanticipated run-off in this area.
2000-02-24 | Structures | Guardrail | RECONSTRUCTION(O) | 12 | KNOTT | The median pier was setup for guardrail around the pier and Type 4 and Type 5 End Treatments on each end. This created a problem for the construction of Grade and Drain for these end treatment types. | Subsequently , after discussion with the Division of Construction and Design , it was determined to use Crash Cushion Type DC at this location , as Type 4 and Type 5 End Treatments were no longer commonly being recommended in this type of application.
2000-02-24 | Structures | Fencing | RECONSTRUCTION(O) | 12 | KNOTT | After construction of a retaining wall from Lt. Station 118+38 to Station 123+00 , it was decided to install a 6-foot chain link fence at the top of the wall in order to protect pedestrians. | The wall had to be drilled in order to anchor the fence posts. The PCR team recommended that any wall four feet or higher should be designed with a minimum six-foot high chain link fence.
2000-02-24 | Structures | Fencing | RECONSTRUCTION(O) | 12 | KNOTT | After construction of a retaining wall from Lt. Station 118+38 to Station 123+00 , it was decided to install a 6-foot chain link fence at the top of the wall in order to protect pedestrians. | The wall had to be drilled in order to anchor the fence posts. The PCR team recommended that any wall four feet or higher should be designed with a minimum six-foot high chain link fence.
2000-02-24 | Construction | Revisions | RECONSTRUCTION(O) | 12 | KNOTT | An access ramp located between KY 1428 and KY 321 was to be closed during construction of a culvert , so it was decided that it would be feasible to reconstruct this ramp as part of the contract for this project. | This work involved breaking and seating the existing concrete pavement , placing two courses of Bituminous Base and one course of Bituminous Surface. Also , the existing shoulders were reconstructed using the same pavement design. DGA and Chip-Seal Sh
2000-02-24 | Construction | Revisions | RECONSTRUCTION(O) | 12 | KNOTT | An access ramp located between KY 1428 and KY 321 was to be closed during construction of a culvert , so it was decided that it would be feasible to reconstruct this ramp as part of the contract for this project. | This work involved breaking and seating the existing concrete pavement , placing two courses of Bituminous Base and one course of Bituminous Surface. Also , the existing shoulders were reconstructed using the same pavement design. DGA and Chip-Seal Sh
2000-02-24 | Pavement | Shoulders | RECONSTRUCTION(O) | 12 | KNOTT | The plans called for 6 ft earth shoulders from Sta. 35+00 to 48+00. However , due to the nearby industrial site heavy truck traffic was expected. | A Change Order was needed to upgrade the 6 ft shoulders from earth to Crushed Stone Base.
2000-02-24 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The Best Management Plan (BMP) for this project called for the use of Sedimentation basins at specific locations. | Sedimentation basins were added via Change Order and placed at the locations specified by the BMP.
2000-02-24 | Design | Guardrail | RECONSTRUCTION(O) | 12 | KNOTT | It was determined in the field that sufficient clearance was not available to install a Type 4 End Treatment on the access ramp between KY 1428 and KY 321 as designated in the plans. | A Type 1 End Treatment was installed in lieu of the Type 4 End Treatment.
2000-02-24 | Design | Shelved Plans | RECONSTRUCTION(O) | 12 | KNOTT | Erosion control was not included on the original plans as the Erosion Control requirements of Design Memo No. 8-98 were not in effect at the time the plans were submitted. | A Change Order was made for the placement of Silt Fence and Silt Trap Type A.
2000-02-24 | Erosion Control Plan | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The Best Management Plan (BMP) for this project called for the use of Sedimentation basins at specific locations. | Sedimentation basins were added via Change Order and placed at the locations specified by the BMP.
2000-02-24 | Structures | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The plans did not indicate how to construct the bridge pier without disturbing the pipe. | A Change Order was needed to cover the cost of 42 ft of an 8-inch pipe that was damaged during the construction of the bridge pier.
2000-02-24 | Design | Guardrail | RECONSTRUCTION(O) | 12 | KNOTT | It was determined in the field that sufficient clearance was not available to install a Type 4 End Treatment on the access ramp between KY 1428 and KY 321 as designated in the plans. | A Type 1 End Treatment was installed in lieu of the Type 4 End Treatment.
2000-02-24 | Drainage | Elevation | RECONSTRUCTION(O) | 12 | KNOTT | The very wet area on Ramp #1 from Sta. 112+00 to 114+25 required Channel Lining Type 3 capped with crushed aggregate no. 2 over Geotextile Fabric Type IV. However , after placement of the 30-inch pipe , it was found that the fill material had begun to | This necessitated the pipe and the headwalls to be removed and re-laid at a higher elevation using additional aggregate underneath the pipe. Once the fill material was constructed over the pipe , it was noted that additional bridging was needed. Theref
2000-02-24 | Design | Guardrail | RECONSTRUCTION(O) | 12 | KNOTT | It was determined in the field that sufficient clearance was not available to install a Type 4 End Treatment on the access ramp between KY 1428 and KY 321 as designated in the plans. | A Type 1 End Treatment was installed in lieu of the Type 4 End Treatment.
2000-02-24 | Geotechnical | Unsuitable Material | RECONSTRUCTION(O) | 12 | KNOTT | A ditch was to be excavated on the right side of Ramp #3 from Sta. 304+90 to 306+50. Due to the unstable nature of saturated soil and presence of excessive moisture/water in the immediate area it was decided not to cut the toe of the slope out. | A Change Order was set up for the installation of a 30-inch culvert pipe in the exact location of the ditch. The pipe allowed for improved stability of the slopes coming towards the ditch. Standard headwalls and 160 ft of pipe were used. All changes to
2000-02-24 | Construction | Earthwork | RECONSTRUCTION(O) | 12 | KNOTT | More than half way through the job , it was discovered that the project was not going to be embankment-in-place. This was partly due to a large margin of error in the flown survey data , which was said to have been caused by the dense population of pin | The cost item for embankment-in-place was changed to excavation. A more accurate method should have been employed to compute the project earthwork. More excavation would have been anticipated if additional cross-sections were taken and computations were
2000-02-24 | Right-of-Way | CAP | RECONSTRUCTION(O) | 12 | KNOTT | The construction of an adjacent retaining wall destroyed septic systems at both residences on parcel # 13. | An agreement with the property owner at this location indicated that if any damage at all was done to the septic system then a new system would be installed. Consequently , the contractor performed work in order to restore the septic systems for this pa
2000-02-24 | Right-of-Way | CAP | RECONSTRUCTION(O) | 12 | KNOTT | The construction of an adjacent retaining wall destroyed septic systems at both residences on parcel # 13. | An agreement with the property owner at this location indicated that if any damage at all was done to the septic system then a new system would be installed. Consequently , the contractor performed work in order to restore the septic systems for this pa
2000-02-24 | Design | Omission | RECONSTRUCTION(O) | 12 | KNOTT | The removal and resetting of perforated headwalls along Mountain Parkway around the ramp tie-ins was left out of the original plans. | A Change Order was set up to address the removal and resetting of perforated headwalls.
2000-02-18 | Structures | Granular Pile Core | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | Granular pile core was not used on this project. | This was an administrative decision. The Contractor did not like pipe pile; H-pile was preferred. The Contractor asked about changing to H-pile prior to bidding process , but geotech wanted to pipe pile because of scouring concerns.
2000-02-18 | Structures | Omission | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | Guardrail Connectors were shown on standard drawings , but not included as bid items. | A contract item was approved for Guardrail Connectors.
2000-02-18 | Structures | Omission | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | No Curb Box Inlets were set up on this project. | Twenty-five feet of curb was installed at each bridge end connector.
2000-02-18 | Structures | Omission | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | As indicated on Standard Drawing RBC-001-09 , Island Header Curb was required for this project. However , no bid item was established. | A Constructability Review may have identified this oversight.
2000-02-18 | Structures | Erosion Control | BRIDGE REPLACEMENT(P) | 10 | MENIFEE | Erosion control was not installed in accordance with the design plans during construction. | Better inspection or communication of the erosion control process was needed.
2000-02-17 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | An AT&T structure was located on the plans , but it was not set up as a bid item to be removed. | Removal of the AT&T structure , which was built like a fallout shelter , was approved.
2000-02-17 | Design | Shelved Plans | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The project was designed in early 2000 and sat on a shelf for three years. Standards for some items had changed causing omissions in the design plans. | This project had to be updated to current design standards , such as the project was initially not required to include ADA requirements.
2000-02-17 | Maintenance of Traffic | Changes | NEW INTERCHANGE(O) | 10 | WOLFE | Traffic control was to be set up with temporary traffic signals at each end of the bridge. It was determined that sight distance from one bridge end to the other was acceptable and the temporary traffic control devices would not be necessary. | This set up a decrease of $7 , 200 from the original contract.
2000-02-17 | Erosion Control Plan | Seeding | NEW INTERCHANGE(O) | 10 | WOLFE | The project was seeded once in the fall of 1998. However , due to the small application rates of the Forest Service Seed Mix , which was a contract requirement , sufficient vegetation growth was not obtained. | The entire area was re-seeded with the original quantities to obtain sufficient coverage after the slide had been corrected.
2000-02-17 | Design | Elevations | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | There was a design change to the project. The original design had the removal of all asphalt and rock on the right side of mainline. The new design changed the elevation at the curb and gutter through this area. | The new design caused the contractor to re-stake the project in this area.
2000-02-17 | Geotechnical | Quantities | NEW INTERCHANGE(O) | 10 | WOLFE | The excavation quantities at Abutment #2 exceeded the quantities as shown on the bridge plans. Once reaching the bottom of footing elevation for Abutment #2 as shown on the bridge plans , a mud seam was encountered which necessitated removal. | Additional excavation quantities had to be set up.
2000-02-17 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | An existing storm sewer was found on Sand Lane. | This required another junction box to be installed.
2000-02-17 | Erosion Control Plan | Quantities | NEW INTERCHANGE(O) | 10 | WOLFE | Additional Channel Lining Class III was needed for erosion control while the remainder was used for bedding to accommodate construction equipment and the detour road. | An additional quantity of Channel Lining Class III had to be set up due to the insufficient quantities.
2000-02-17 | Maintenance of Traffic | Detours | NEW INTERCHANGE(O) | 10 | WOLFE | Traffic had to be shifted around the excavation resulting in a small detour. | A total of 168 linear feet of barrier was used along the detour alignment as protection to the motorists. The contractor furnished the barrier and the $21.42 price per linear foot included installation and removal. Barrier wall owned by the department w
2000-02-17 | Maintenance of Traffic | Safety | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | A decision was made that it would be more convenient and safer for the traveling public to close the road and install the pipe at night. | Bid items for Message Boards and Barricades were needed to detour and block traffic from entering work area , which was closed to traffic at night.
2000-02-17 | Design | Quantities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | There was not enough quantity set up for Fabric Geotextile Ty IV to go all around the pipe. Earlier design did not use fabric on pipe. | Additional quantities were added for Fabric Geotextile Ty IV.
2000-02-17 | Utilities | Relocation | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Additional paving was needed to cover utility relocation. | We need to have a standard practice of paving over disturbed easement areas (e.g. , utility relocations).
2000-02-17 | Geotechnical | Soils | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Unstable soil conditions required a structural lining to enable drilling. | All 4 holes for pole bases were re-drilled; the pole base was encased and bentonite soil was packed around each pole.
2000-02-17 | Utilities | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | There was an error in calculating the original total of fabric needed to complete the placement of the storm sewer pipe. | Additional fabric for pipe was added.
2000-02-17 | Pavement | Design | NEW INTERCHANGE(O) | 10 | WOLFE | The roadway approaches were constructed of durable rock. The approaches consisted of a highly compacted , dense subgrade , relatively low traffic volume (150 per day current , 275 per day projected for year 2016) , and short paving lengths on each si | Asphalt Binder Class I was placed instead of Asphalt Base and Asphalt Surface.
2000-02-17 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Additional junction boxes were needed to align a storm sewer out of the path of future signal pole bases. | An additional quantity of junction boxes was ordered.
2000-02-17 | Geotechnical | Soils | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Contractor was not able to drill holes needed for signal pole bases due to poor soil qualities on this project. | The typical method of installation had to change , which caused an increase in time and materials.
2000-02-17 | Pavement | Thickness | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The outside edge of the driving lane had thin and inferior pavement. | The roadway was extended and widened widening farther than planned in order to have adequate pavement thickness.
2000-02-17 | Construction | Temporary Fencing | NEW INTERCHANGE(O) | 10 | WOLFE | A split rail fence did not allow the contractor sufficient workspace. | The split rail fence had to be relocated to a temporary location while construction progressed. Once construction was complete , the split rail fence had to be relocated , as close as possible , to the original location. Additional split rail fence w
2000-02-17 | Structures | Retaining Walls/MSE | NEW INTERCHANGE(O) | 10 | WOLFE | The contract required a stone masonry on both sides of the barrier wall at the request of the Forestry Service. Mortar alone would not withstand the stresses the wall would face from the bridge movements as well as the weathering effect of freezing and t | It was decided to place non-shrinking grout behind the stone wall to prevent water from being trapped in the cavity and the stone from breaking at the joints and separating from the barrier wall.
2000-02-17 | Design | Plans | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The existing centerline and edge line cross slope did not match plans. | Additional staking was needed to retake project.
2000-02-17 | Design | Slopes | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | There was an error in cross slope on the mainline. | Asphalt milling was needed to correct the existing slope of the asphalt to conform to the proposed slope of the new roadway.
2000-02-17 | Maintenance of Traffic | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | No bid items were set up for Temporary Striping and Remove Existing Striping even though these items were called for in the Maintenance of Traffic plans. | A check list or Constructability Review may have identified this omission.
2000-02-17 | Right-of-Way | Easements | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | Utility easement had to be purchased for the city of Henderson after buying Right-of-Way. | A Constructability Review may have revealed this oversight.
2000-02-17 | Design | Borrow/Waste | NEW INTERCHANGE(O) | 10 | WOLFE | A borrow site had to be acquired out of the U.S. Forest Service area. The borrow site , obtained by the contractor , was located approximately one mile from the job site on KY 715. Repeated hauling over the road with the borrow material damaged the th | To repair this section of roadway , an Item Extra Work-Asphalt Patching was set up. This item provides for repair of the damaged pavement areas by patching with Asphalt Binder Class I.
2000-02-17 | Erosion Control Plan | Omission | NEW INTERCHANGE(O) | 10 | WOLFE | Erosion control items were not set up on the initial plans. Once construction began , it was decided to implement the department's policy dealing with erosion control. | Five-hundred (500) tons of No. 2 stone was setup to construct rock silt checks to capture erodible material and keep it from entering the Red River tributary , Gladie Creek.
2000-02-17 | Geotechnical | Elevations | NEW INTERCHANGE(O) | 10 | WOLFE | Upon removal of the mud seam , mass concrete was needed to restore the elevation of the bottom of the footing as shown on the bridge plans. | Additional concrete quantities had to be set up and 6.33 cubic yards of concrete was ordered at $125.00 per cubic yard.
2000-02-17 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | An existing storm sewer structure did not need to be replaced. | The KYTC agreed to tie-in and not to replace.
2000-02-17 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The ADA Detectable Warnings were listed on the plans stating they should be separate bid items , but were included in the bid proposal. | A contract item was added for ADA Detectable Warnings.
2000-02-17 | Design | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | A side road was missing from the plans. | An edge key was needed for the side road.
2000-02-17 | Design | Adjacent Projects | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The existing asphalt surface , where the new asphalt surface was to tie in , was badly deteriorated. | In order to make a smooth transition , an additional 325 LF of existing roadway was resurfaced.
2000-02-17 | Design | Plans | NEW INTERCHANGE(O) | 10 | WOLFE | Construction of Abutment #2 required approximately half of the existing road. The plans did not show this. | Traffic had to be shifted around the excavation resulting in a small detour.
2000-02-17 | Structures | Omission | NEW INTERCHANGE(O) | 10 | WOLFE | The contractor lacked a suitable place to pump water that was trapped around Intermediate Bent Number 1 and Intermediate Bent Number 2. | A dewatering structure had to be constructed.
2000-02-17 | Drainage | Omission | BRIDGE REPLACEMENT(P) | 10 | BREATHITT | The pipe sheet called for the construction of a Drop Box Inlet Type 13S; however , it was not shown in the Pipe Drainage Summary and was not set up as a bid item. | An additional Drop Box Inlet Type 13S was approved.
2000-01-19 | Construction | Revisions |  |  |  | Since the project was on an accelerated schedule , the Louisville Water Company was unable to relocate the hydrants soon enough to meet the December 1 , 1997 completion date. | In order not to delay the project , it was agreed to allow the Contractor to relocate the hydrants and also lower approximately 20 linear feet of 12 water main and two domestic service lines. The Louisville Water Company supplied all materials necessary
2000-01-19 | Design | Radius |  |  |  | The radii at the corners of Second Street and Jefferson Street , as well as Second Street and Market Street , were constructed at the specified 15 feet. However , after their construction the City of Louisville determined that these radii would be ins | It was agreed to increase the radius to 30 feet and to modify the drainage at the corner of Second Street and Jefferson Street. These radii changes required the relocation of a fire hydrant at the intersection of Second and Market Street. This type of 3
2000-01-19 | Construction | Contracts |  |  |  | After the project was let , it was discovered that the Contractor for the Commonwealth Convention Center expansion project had an agreement with the City of Louisville to close Third Street beginning December 1 , 1997. This closure was to be for approx | A Change Order was necessary to compensate the Contractor for accelerating the project schedule. In order to expedite the project to meet the December 1 , 1997 deadline the Contractor proposed to work on the leftmost and rightmost lanes concurrently. T
2000-01-19 | Erosion Control Plan | Sodding |  |  |  | As required by the contract , the Jefferson County Agricultural Extension Agent analyzed the existing soil for suitability. Their analysis concluded that the existing soil on the project was unsuitable and needed to be replaced. Contract notes required | Since the survival of these plants was considered of high importance , it was agreed to remove all of the existing soil within these confined areas and place topsoil meeting the requirements of the contract. The corresponding Change Order encompassed on
2000-01-19 | Utilities | Stacked Utilities |  |  |  | The plans indicated that the proposed 18 inch storm sewer crossing Second Street at Station 59+58 was to drain into a proposed manhole which was to be constructed over an existing combination sewer. When work began it was discovered that there was a bric | It was agreed to modify the precast manhole to fit the existing vault and lay the 18 inch storm sewer at a lower elevation in order to avoid utilities.
2000-01-19 | Design | Special Note |  |  |  | The plans indicated that an existing control cabinet and disconnect switch located in a vault at Station 56+90 be removed and relocated to an area outside the limits of the roadway. There were no notes in the project documentation to indicate requirement | It was agreed to install new equipment in the final location and transfer the service in order to minimize the period of time that the parking garage would be without electrical service.
2000-01-19 | Traffic | Omission |  |  |  | The plans indicated locations for Stop Bars , Crosswalks , and Pavement Marking Arrows. However no bid quantities were established for these items of work. | It was agreed to install the Stop Bars and Crosswalks at locations specified in the contract plans and to install the Turn Arrows at locations specified by the Project Engineer.
2000-01-18 | Erosion Control Plan | Omission | WIDENING | 5 | JEFFERSON | Additional measures were necessary for erosion control. | A dewatering basin and temporary silt fence were added to the contract for the Best Management Plan (BMP) for erosion control.
2000-01-18 | Maintenance of Traffic | Timing | NEW ROUTE(O) | 5 | JEFFERSON | Traffic was placed on the relocated section of the roadway for several days before paving operations could begin. | Traffic Bound Base was added to the contract and used to maintain the roadway under traffic.
2000-01-18 | Erosion Control Plan | Omission | NEW ROUTE(O) | 5 | JEFFERSON | Additional measures were necessary for erosion control. | As part of the Best Management Plan (BMP) for erosion control on this project temporary silt fence , silt traps and permanent silt checks were added to the contract. Also , water was set up on the Raven Curve section of this project for dust control.
2000-01-18 | Design | Entrance | NEW ROUTE(O) | 5 | JEFFERSON | There were sight-distance issues at an entrance along the Raven curve site. | The entrance at the Raven curve site was relocated in order to improve the sight-distance at this location.
2000-01-18 | Pavement | Striping | NEW ROUTE(O) | 5 | JEFFERSON | The original quantity of pavement striping was underestimated and was not sufficient to place centerlines and edge lines on the full length of the project. | Pavement Striping quantities were increased.
2000-01-18 | Drainage | Existing Pipe | WIDENING | 5 | JEFFERSON | Two existing pipes under KY 160 at approximate stations 10+240 and 10+274 were supposed to be removed. | These existing pipes were safeloaded to allow the existing condition of KY 160 to remain intact since it would not require open cut trenches on the roadway.
2000-01-18 | Pavement | Approaches | NEW ROUTE(O) | 5 | JEFFERSON | The section of new roadway did not match the section of old roadway safely at the end of the project. | The old pavement was removed approximately 17 meters past the ending station and replaced with new pavement in order to provide a better transition from the new roadway to the old roadway.
2000-01-18 | Drainage | Omission | WIDENING | 5 | JEFFERSON | An area under the proposed roadway fill was constantly wet with running water. | Perforated pipe was used to drain water from under the proposed roadway fill.
2000-01-18 | Geotechnical | Safety | NEW ROUTE(O) | 5 | JEFFERSON | The end of the cut at Right Station 40+060 to 40+080 was severely fractured and presented a danger of rock falling into the roadway. | The fractured area was removed and an additional quantity of roadway excavation was set up to accomplish the work.
2000-01-18 | Drainage | Culvert | NEW ROUTE(O) | 5 | JEFFERSON | There was inadequate drainage for a small area to the left of the new entrance. | A culvert pipe was needed under the entrance to provide drainage for the entrance. The Contractor proposed using a Type S polyethylene pipe. This change was allowed providing there was a minimum of two feet of cover over the pipe.
2000-01-18 | Drainage | Stream Mitigation | WIDENING | 5 | JEFFERSON | The main stream flow was originally set up to flow through the middle culvert barrel , which would alter the natural flow of the stream. | The 10' x 8' triple barrel culvert was reworked to accommodate the natural flow of the stream. A diversion wall was placed to allow the flow to go through an end barrel , which accommodated the natural flow of the stream.
2000-01-18 | Materials | Backfill | NEW ROUTE(O) | 5 | JEFFERSON | Crushed stone base was more readily available than DGA and there was no change in the unit price for this item. | Crushed Stone Base was substituted for DGA.
2000-01-18 | Design | Waste Areas | NEW ROUTE(O) | 5 | JEFFERSON | Guardrail was blocking an entrance that was added to the job in order to access a waste area on this parcel located right of Station 40+228. | Forty-two meters of guardrail was removed on Parcel No. 3. The Terminal Section No. 1 on the existing End Treatment Type 2A was reused at no additional charge to the Department. All holes that were left by the removal of the guardrail posts were filled a
2000-01-18 | Pavement | Approaches | WIDENING | 5 | JEFFERSON | The plans did not address how KY 160 should be tied into existing KY 899 near the end of the project at Station 5+200. | Bituminous milling and texturing were used to tie into the existing KY 899.
2000-01-18 | Drainage | Drop Box Inlets | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns about the Drop Box Inlet Type 1 located left at Station 40+020 creating an unsafe situation for the traveling public. | The apron and grate on the Drop Box Inlet Type 1 were modified to provide a safer situation for the traveling public.
2000-01-18 | Traffic | Safety | NEW ROUTE(O) | 5 | JEFFERSON | There was a drop off at the repaired area as well as a gas well located within 7 meters from the edge of pavement of the new road on the outside curve right at Station 8+150. | Guardrail was needed to protect the drop off at the repaired area and to transition to a safe location at each end and also to protect the public from hitting the gas well near the edge of the pavement.
2000-01-18 | Drainage | Headwalls | NEW ROUTE(O) | 5 | JEFFERSON | There were concerns about inadequate drainage in the ditch line at Stations 40+020 and 40+275. | The concrete headwalls at the inlet ends of the pipes at these locations were replaced with Drop Box Inlets Type 1.
2000-01-18 | Materials | Backfill | WIDENING | 5 | JEFFERSON | Crushed stone base was more readily available than DGA and there was no change in the unit price for this item. | Crushed Stone Base was substituted for DGA.
2000-01-18 | Drainage | Flooding | NEW ROUTE(O) | 5 | JEFFERSON | During the project , flooding damaged the existing road at the beginning of the Raven curve site. | The Contractor was required to use Traffic Bound Base on the section for Maintenance of Traffic.
2000-01-18 | Geotechnical | Embankment Stabilization | WIDENING | 5 | JEFFERSON | Additional measures were needed to stabilize a creek bank. | Channel lining was relocated along the existing channel to stabilize the creek bank after it had been used to control erosion as part of the BMP plan.
2000-01-18 | Traffic | Raised Pavement Markers | WIDENING | 5 | JEFFERSON | The contract plans required pavement markers Type IV. However , the pavement markers needed to accommodate snow removal on this route. | The pavement markers were changed to Type V , which were already in place on KY 160 on both sides of this project.
2000-01-18 | Geotechnical | Embankment Stabilization | NEW ROUTE(O) | 5 | JEFFERSON | The existing road was cracking and settling due to erosion of the creek bank at the beginning of the project on the Raven section of the project. The damaged section extended back beyond the project limits approximately 40 meters. | Railroad Rails-Drilled , Cribbing , Excavation , and Backfill were needed for the embankment failure repair in order to make a good transition from the new section of roadway to the repaired section of the existing roadway.
1999-12-15 | Structures | Omission | MAJOR WIDENING(O) | 11 | LAUREL | A bid item for masonry coating was not included in the original bid items. | A Change Order was set up to establish quantities of masonry coating.
1999-12-15 | Structures | Communication | MAJOR WIDENING(O) | 11 | LAUREL | The plans called for removing 25 feet of guardrail at each bridge end. However , the new deck was slightly wider than the one it was replacing. | Additional guardrail had to be removed so that the new rail was in alignment with the constructed barrier wall.
1999-12-15 | Structures | Painting | MAJOR WIDENING(O) | 11 | LAUREL | The Shear Connectors were to be painted after being welded onto the existing girders. However , the contractor requested not to paint them. | The contractor gave the Department a credit for not painting the shear connectors.
1999-12-15 | Maintenance of Traffic | Shoulders | MAJOR WIDENING(O) | 11 | LAUREL | As outlined in the traffic control design plans , traffic was shifted over onto the existing shoulder at the bridge ends. During phase 1 , the shoulders began to fail. | Patching material was used to stabilize the shoulder. In order to avoid this problem during phase II , the shoulder was excavated 6 inches and backfilled with Class A Concrete. The concrete was overlaid with Bituminous Concrete Surface. This shoulder sta
1999-12-15 | Structures | Reinforcement Steel | MAJOR WIDENING(O) | 11 | LAUREL | During the removal of the existing backwalls , it was found that the existing steel reinforcement was in bad condition. | Stirrup bars were used to splice with new steel reinforcement.
1999-12-15 | Pavement | Quantities | MAJOR WIDENING(O) | 11 | LAUREL | There was an over-run of Concrete Class AA on each bridge due to the depth of concrete over the girders and overhangs. The contract plans indicated a 7 deck depth. However the concrete depth of these bridges averaged 9 1/2 inches. | A Change Order was set up to decrease quantities of Concrete Class AA.
1999-12-15 | Maintenance of Traffic | Signage | MAJOR WIDENING(O) | 11 | LAUREL | Several mobile home manufacturers were located near the Tennessee State Line. Also , significant boat traffic was expected within the area. | An extra set of wide load advisory signs were erected near the Tennessee State Line. These signs were installed in order to give the traveling public ample warning of the narrow bridge conditions ahead. Also , Bridge Work Overhead signs were hung from
1999-12-15 | Maintenance of Traffic | Changes | MAJOR WIDENING(O) | 11 | LAUREL | The contractor was supposed to use Type J Barrier Walls as specified in the contract bid items. | The contractor used state owned 9-M Barrier Walls in lieu of the Type J Barrier Wall. This was used as temporary barrier wall and allowed the contractor to use state owned barrier wall , resulting in a savings to the Department.
1999-12-14 | Design | Median | MINOR WIDENING(O) | 11 | CLAY | There were concerns regarding the grade tie-in at the intersection of Crossridge Avenue and Campbell Lane. | A greater length of median had to be removed on Crossridge Avenue in order to make an acceptable grade tie-in with Campbell Lane.
1999-12-14 | Construction | Inspection | MAJOR WIDENING(O) | 11 | WHITLEY | All of the work mentioned in the previous two issues was deemed necessary by the Division of Construction in the final construction report of February 2 , 1999. | Included in this change order was a lump sum total of $2 , 500 as compensation to the contractor for mobilization and temporary signing needed to perform the work required by the final report.
1999-12-14 | Drainage | Error | MINOR WIDENING(O) | 11 | CLAY | An error on the pipe sheet resulted in a drop box being installed in the wrong location. | Since this box was already connected to a string of culvert pipe , the box was converted to a junction box and an additional drop box installed.
1999-12-14 | Geotechnical | Sinkhole | MINOR WIDENING(O) | 11 | CLAY | A sinkhole was to be capped and covered with fill right of Station 48+89 on the Smallhouse Road Approach. However , this sinkhole was necessary to maintain drainage for the area. | The sinkhole was capped around an existing standpipe to utilize it for drainage. A drop box inlet was added to complete the fill and provide drainage.
1999-12-14 | Drainage | Omission | MINOR WIDENING(O) | 11 | CLAY | An additional entrance was proposed left of Station 219+25 , but the existing entrance pipe was not replaced when the roadway was widened. | This entrance pipe had to be replaced to maintain the proper drainage for an existing parking lot.
1999-12-14 | Geotechnical | Subsurface | MINOR WIDENING(O) | 11 | CLAY | During the widening operation , several areas of unsuitable subgrade were discovered. | Because of the time of year and the moisture in the soil , these areas were undercut and refilled with No. 2 stone in order to facilitate the project schedule.
1999-12-14 | Design | Omission | MINOR WIDENING(O) | 11 | CLAY | An entrance was added at Sta. 261+60 Rt. | Curb and gutter was already installed in this area and had to be removed.
1999-12-14 | Drainage | Quantities | MINOR WIDENING(O) | 11 | CLAY | Three additional drop boxes were shown on the plans but were not included in the bid quantities. | Three additional Drop Box Inlets Type 11 were added.
1999-12-14 | Materials | Asphalt Mixtures | MINOR WIDENING(O) | 11 | CLAY | The bituminous concrete bid prices for the job mix formula asphalt content needed to be adjusted. | A Change Order adjusted the bituminous concrete bid prices for the job mix formula asphalt content.
1999-12-14 | Drainage | Existing Pipe | MINOR WIDENING(O) | 11 | CLAY | There was an entrance pipe at Station 48+70 Lt. on the Smallhouse Road Approach that was not shown on the plans. | The pipe was removed and replaced in order to maintain the existing drainage.
1999-12-14 | Utilities | Plans | MINOR WIDENING(O) | 11 | CLAY | A sewer line was mistakenly designed to be installed just off the proposed utility easement in order to avoid an existing permanent sign. | The sewer line was re-aligned and a manhole was added in order to stay on the easement.
1999-12-14 | Design | Quantities | MINOR WIDENING(O) | 11 | CLAY | There were insufficient quantities of several items to construct an entrance approach left of Station 87+99. | Additional quantities of Embankment In Place , Concrete , Sidewalk , Curb and Gutter , Crushed Stone Base , Entrance Pipe , and Bituminous Pavement were needed to provide the entrance approach.
1999-12-14 | Pavement | Type | MINOR WIDENING(O) | 11 | CLAY | The surfacing material on the project was originally Bituminous Concrete Surface Class I. However , It must be noted that there is heavy traffic not only on Campbell Lane but also US 231. | The pavement type was changed to incorporate polymer into the surfacing quantities to help reduce rutting and movement at intersections.
1999-12-14 | Maintenance of Traffic | Diversions | MINOR WIDENING(O) | 11 | CLAY | The contractor could not build the diversion at Stations 65+00 to 72+50 because there was a utility pole that had to be avoided. The pole could not be moved in time to maintain the project schedule. | The contractor requested to construct temporary pavement widening on the right side of the existing pavement. This reduced the length and earthwork quantities for the detour by 20%.
1999-12-14 | Drainage | Pipes | MINOR WIDENING(O) | 11 | CLAY | Changes in the lengths of slotted drain pipe were received after construction had begun. | Not all of these changes could be incorporated since some of the boxes and curb and gutter had been already installed; however , additional lengths were installed where possible.
1999-12-14 | Traffic | Signals | MINOR WIDENING(O) | 11 | CLAY | The Division of Traffic requested that signals be installed at Crossridge Avenue. | A Change Order added the necessary quantities.
1999-12-14 | Traffic | Signals | MINOR WIDENING(O) | 11 | CLAY | An existing traffic loop was damaged during curb construction. | A temporary traffic loop was installed to accommodate traffic phasing.
1999-12-14 | Design | Omission | MINOR WIDENING(O) | 11 | CLAY | There were existing pavement markers at the Scottsville Road-Campbell Lane intersection which planned to receive Bituminous Milling & Texturing. | A bid item was added for removing the existing pavement markers at the Scottsville Road-Campbell Lane intersection prior to receiving Bituminous Milling & Texturing.
1999-12-14 | Geotechnical | Sinkhole | MINOR WIDENING(O) | 11 | CLAY | Two sinkholes were encountered on the project. | Items were added for capping the two sinkholes encountered on the project.
1999-12-14 | Environmental | Asbestos | MINOR WIDENING(O) | 11 | CLAY | During the waterline relocation , an existing asbestos water main was encountered that was to be connected to the new relocated water main. | A certified waste handling firm was required to perform the saw cut and abatement work.
1999-12-14 | Drainage | Coordination | MINOR WIDENING(O) | 11 | CLAY | A drop box installed left of centerline at Station 213+92 was too high to accept drainage from an adjacent parking lot when the parking lot was reconstructed. | The box had to be removed and reconstructed to the proper grade.
1999-12-14 | Utilities | Existing Utilities | MINOR WIDENING(O) | 11 | CLAY | Widening on Scottsville Road required that two existing street lights be relocated. | The Department provided the pole bases and conduit. The local utility installed the light poles.
1999-12-14 | Utilities | Omission | MINOR WIDENING(O) | 11 | CLAY | Water services at Stations 279+85 Rt. and 271+50 Rt. were connected to the existing water main after the utility plans were finalized. | Waterline items were needed to connect two existing services at Stations 279+85 Rt. and 271+50 Rt.
1999-12-14 | Geotechnical | Sinkhole | MINOR WIDENING(O) | 11 | CLAY | A sinkhole opened up during construction at approximate Station 73+52 Rt. This area was frontage for a church , and right of way negotiations were ongoing at the time. | he church's request that a manhole and a grate be installed was granted. Also , a permanent drainage easement was also taken in this area so that the sinkhole area could pond water during a storm event.
1999-12-14 | Utilities | Existing Utilities | MINOR WIDENING(O) | 11 | CLAY | There was a conflict with a series of overhead electric lines that could not be repositioned because of the nearby airport restrictions on alignment and height. | An additional strain pole base had to be drilled at Station 305+10 Lt.
1999-12-14 | Utilities | Existing Utilities | MINOR WIDENING(O) | 11 | CLAY | The existing water main at Crossridge Avenue was in conflict with the proposed storm sewer installation. | The water main had to be relocated.
1999-12-14 | Utilities | Inaccurate Location | MINOR WIDENING(O) | 11 | CLAY | An existing sewer line was not shown on the plans at Station 305+59 Rt. | Additional waterline tees and bends were needed in order to avoid the existing sewer line.
1999-12-14 | Geotechnical | Sinkhole | MINOR WIDENING(O) | 11 | CLAY | A sinkhole was discovered below the original ground surface at Station 286+00. | Since the resulting cavern was quite large , the void was bridged using Class A Concrete.
1999-12-14 | Traffic | Signals | MINOR WIDENING(O) | 11 | CLAY | The entrance to a church was relocated to a point opposite of the mall entrance at Station 293+96. | A revision in the intersection signalization was required.
1999-12-14 | Drainage | Temporary Drainage | MINOR WIDENING(O) | 11 | CLAY | The contractor was advised , that a partial width of the final surface course must be placed prior to winter in order to minimize water penetration and to provide positive pavement drainage to the gutter. | The contractor requested to substitute a 1-3/4 inch binder course for the same thickness of base and use a bituminous wedge , to be removed later , to provide drainage to the gutter. This also allowed the use of temporary striping instead of removable t
1999-12-14 | Traffic | Signals | MINOR WIDENING(O) | 11 | CLAY | It was decided to provide power for the traffic signalization on the project using underground service. | Additional conduit and trenching/backfilling were added.
1999-12-14 | Construction | Temporary Fencing | MAJOR WIDENING(O) | 11 | WHITLEY | There were concerns regarding the safety of the public and workers along the excavation area. | A Safety Fence was installed along the excavation area.
1999-12-14 | Drainage | Omission | MINOR WIDENING(O) | 11 | CLAY | There was insufficient drainage set up for a parking lot left of Station 257+50. | A drop box and culvert pipe were added to drain a parking lot left of Station 257+50.
1999-12-14 | Drainage | Error | MINOR WIDENING(O) | 11 | CLAY | The storm sewer was redesigned from Station 293+26 to the end of the project. | A drop box inlet had to be reconstructed due to the redesign of the storm sewer.
1999-12-14 | Utilities | New Utilities | MINOR WIDENING(O) | 11 | CLAY | The local Municipal Utilities decided to utilize underground crossings rather than aerial. | Therefore , underground conduits were placed as shown on the electrical utility plans. Since this was a betterment for the utility , the utility paid the difference in cost between the underground and aerial installation.
1999-12-14 | Pavement | Shoulders | MINOR WIDENING(O) | 11 | CLAY | The original typical section called for only a four foot width of the shoulder to be removed and reconstructed along Scottsville Road (US 231). This was both impractical to construct and would provide no additional strength in the shoulder area. | As a result , the entire shoulder width of 10 feet was removed and reconstructed. Additional quantities of Bituminous Concrete Surface were added to patch utility and storm sewer crossings of the existing roadway.
1999-12-14 | Pavement | Quantities | MAJOR WIDENING(O) | 11 | WHITLEY | Insufficient quantities of Asphalt Concrete Surface Class I-O were set up in the original contract. | An additional 29.793 metric tons were added via Change Order.
1999-12-14 | Right-of-Way | CAP | MINOR WIDENING(O) | 11 | CLAY | There were many items needed because of right of way agreements with adjacent property owners that weren't in the original plans. | Increases in Embankment In Place , Culvert Pipe , Entrance Pipe , Curb and Gutter , Sidewalk , Concrete Entrance Pavement , Crushed Stone Base , Traffic Bound Base , and Bituminous Pavement were required because several entrances were added or wid
1999-12-14 | Construction | Delays | MAJOR WIDENING(O) | 11 | WHITLEY | The work on this project had already begun with the setting of detour signs on March 5 , 1998 , when Breathitt County Board of Education requested temporary cessation of work until the end of the school year on May 11 , 1998. In the mean time , heavy | This action necessitated removal of and replacement of all detour signs. Additionally , mud and debris had to be removed and cleaned before work could resume.
1999-12-14 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 11 | WHITLEY | The original right-of-way for this project was acquired for the construction of a bridge , which was subsequently changed to that of an elliptical pipe. This resulted in very limited working area for the contractor. The property owner allowed the contr | Silt basin , rock checks (Silt Trap Type II) , straw bales , as well as final seeding and protection were added. Extra quantities of Channel Lining Class III were needed to construct the flow line and for slope protection at the inlet and outlet of th
1999-12-14 | Drainage | Diversion Drainage | MAJOR WIDENING(O) | 11 | WHITLEY | Roadway run-off was flowing down the shoulder slopes. Efforts were necessary in order to prevent saturation of the shoulder slopes on the low side/outlet end of the curve. | Additional Channel Lining Type III was used to construct a surface drainage ditch near the wing wall along with an asphalt wedge curb on the low side of the curve.
1999-12-14 | Utilities | Inaccurate Location | MINOR WIDENING(O) | 11 | CLAY | An existing telephone cable between Stations 293 and 304 right of centerline interfered with the placement of a storm sewer system. The telephone cable was incorrectly located by the utility company. | In order to avoid a four to six week delay in construction , an offset storm sewer system was constructed approximately two feet behind the sidewalk with no utility interference.
1999-12-14 | Utilities | Existing Utilities | MINOR WIDENING(O) | 11 | CLAY | An existing traffic signal strain pole and underground telephone cable interfered with the location of a proposed 18 equivalent cross drain pipe. | The proposed 18 equivalent cross drain pipe was relocated; however , this required two additional drop box inlets and additional 10 feet of cross drain pipe.
1999-12-14 | Drainage | Quantities | MAJOR WIDENING(O) | 11 | WHITLEY | Fill slope settlement occurred over the elliptical pipe at the outlet end , and areas around the wing walls eroded. | Additional quantities of Channel Lining Type III were needed to correct the settlement and erosion.
1999-12-14 | Drainage | Quantities | MINOR WIDENING(O) | 11 | CLAY | There was insufficient drainage set up for a low area adjacent to an existing entrance right of Station 289+40. | Additional entrance pipe was needed to drain the low area.
1999-10-27 | Utilities | Existing Utilities | PAVEMENT REHAB-PRI(P) | 3 | TODD | Two 1.5 inch copper service lines connecting to two houses were encountered during an investigation of field conditions but had not previously been identified by the utility company. | A Change Order was established for the relocation of the two service lines.
1999-10-27 | Construction | Contracts | MAJOR WIDENING(O) | 3 | WARREN | There was an issue with finding suitable bituminous pavement reinforcement material for the project. The tensar product that was specified in the contract was not available and the replacement tensar grid material was $1.00 more per square yard. Also , | A Change Order was set up to provide suitable bituminous pavement reinforcement material while the more expensive material was used at intersections between layers of pavement as an experimental product.
1999-10-27 | Structures | Standard Drawings | MAJOR WIDENING(O) | 3 | WARREN | The expansion dams on the bridges needed to be brought up to current standards. | A Change Order was necessary to change the expansion dams from 5 x 3 angles to 5/8 x 8 flat plates.
1999-10-27 | Utilities | Inaccurate Location | PAVEMENT REHAB-PRI(P) | 3 | TODD | It was conjectured that an AT&T telephone pole had not been shown or correctly located on the plans. | A Change Order was approved to compensate the Contractor for relocation of the AT&T telephone pole and the associated anchors.
1999-10-27 | Utilities | Communication | PAVEMENT REHAB-PRI(P) | 3 | TODD | The Morehead Utility Plant Board did not approve of the use of plastic casing spacers for the construction of sewer pipe. | A Change Order was approved at the request of the Morehead Utility Plant Board to change the proposed plastic casing spacers to metal ones.
1999-10-27 | Geotechnical | Subsurface | MAJOR WIDENING(O) | 3 | WARREN | Extremely unstable subsoil conditions warranted stabilization throughout the entire project although the contract plans only required stabilization in certain areas. Water was more apparent at some locations , however , once construction began it was n | Because of these factors , roadway stabilization was performed throughout the entire project during the construction phase. A Change Order was necessary to provide a layer of filter fabric and bank gravel throughout the entire project.
1999-10-27 | Environmental | Asbestos | MAJOR WIDENING(O) | 3 | WARREN | After excavation began asbestos pipe was discovered at Station 195+60 in an area being excavated for construction of a culvert. Also , asbestos shingles were found buried in the area of Station 48+30 to 48+70. | A Change Order was necessary to provide pay items for removing asbestos cement pipe and asbestos material from the project site in accordance with established procedures.
1999-10-27 | Right-of-Way | CAP | MAJOR WIDENING(O) | 3 | WARREN | The installation of sewer line and encasements between Station 41+80 and 46+00 was required as a result of a settlement between the State and the property owner. | A Change Order was necessary to provide contract items in order to install the sewer line and encasements and the work was performed after the road had already opened to traffic.
1999-10-27 | Maintenance of Traffic | Omission | PAVEMENT REHAB-PRI(P) | 3 | TODD | Temporary Pavement Markers Type IV A were needed to construct the construction zone diversion in accordance with Standard Drawing TSC-250-04 , but this item had been inadvertently left out of the plans. | Temporary Pavement Markers were added via Change Order.
1999-10-27 | Pavement | Repair | PAVEMENT REHAB-PRI(P) | 3 | TODD | Several sudden settlements of considerable magnitude occurred on US 60 during the winter months of 1999 , which required immediate attention due to traffic safety concerns. | The Contractor stockpiled cold mix on the project in order to perform expedient emergency repairs. Several times during the winter months the Contractor had to mobilize both labor and equipment on a moment's notice to repair the roadway.
1999-10-27 | Utilities | Existing Utilities | PAVEMENT REHAB-PRI(P) | 3 | TODD | The original plans called for relocating a 16 water line , which would have caused an interruption of water service for some costumers. | At the request of the Morehead Utility Plant Board , 16 Butterfly Valves and 16 Temporary Line Stoppers were installed at the tie-in locations for the 16 line water line. This was done in lieu of relocation and helped avoid a disruption of service.
1999-10-27 | Pavement | Repair | PAVEMENT REHAB-PRI(P) | 3 | TODD | Precipitous localized settlement of the pavement on mainline US 60 posed a major safety hazard to the travelling public. | Emergency Pavement Milling of mainline US 60 was performed. The milling operation was successful in the symptomatic treatment of settlement and reduction of traffic hazards.
1999-10-27 | Drainage | Quantities | MAJOR WIDENING(O) | 3 | WARREN | There was insufficient drainage set up from Station 11+96 to Station 13+00 and from Station 15+19 to Station 16+18. | A Change Order was necessary to increase contract items in order to facilitate drainage at these stations.
1999-10-27 | Pavement | Quantities | MAJOR WIDENING(O) | 3 | WARREN | Bank gravel quantities were underestimated due to the extremely unstable soil conditions encountered on the project. | An additional quantity of bank gravel was needed to stabilize the subgrade.
1999-10-27 | Design | Intersection | MAJOR WIDENING(O) | 3 | WARREN | There were concerns about protecting a potential drop-off condition at the intersection of KY 121 & KY 58/80. | Snap back tubular markers were added to the contract in order to protect the drop-off condition.
1999-10-27 | Pavement | Omission | MAJOR WIDENING(O) | 3 | WARREN | Traffic Bound Base was shown on the plans , but no bid item was set up on the contract. This item was needed to provide access to businesses during construction of the project. | A Change Order was necessary to provide a bid item for Traffic Bound Base.
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | Workers were exposed to contamination while working in the cut and fill areas. | Physical examinations were required for three workers.
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | A subsurface soil investigation was needed to determine the extent of the contamination that was encountered in the roadway cut. | It was necessary to compensate the contractor for the cost incurred for the subsurface soil investigation of the contaminated material.
1999-10-21 | Materials | Concrete Mix | MAJOR WIDENING(O) | 8 | CUMBERLAND | The concrete test cylinders for a section (20.5 CY of Class A Concrete) of the top slab of the 7'x7' culvert at Sta 434+14.86 did not meet the required strength and the concrete test cores broke at 3000 psi. | It was recommended by the Division of Construction to accept this concrete with a price adjustment.
1999-10-21 | Geotechnical | Coffer Dam | MAJOR WIDENING(O) | 8 | CUMBERLAND | Excavation for a cofferdam was needed at Bridge Abutment No. 1. | Bridge Abutment No. 1 was monitored for hazardous gases during an excavation for a cofferdam.
1999-10-21 | Construction | Delays | MAJOR WIDENING(O) | 8 | CUMBERLAND | The project had been delayed from October 10 , 1988 to March 31 , 1992 due to contaminated waste found in the cut area , Sta 412+00 to Sta 422+50. | Lump sum Compensation for Delay included the following items: General Administrative Costs $89 , 041.00 , Railroad Protective Insurance Premium $2 , 875.00 , Staking $4 , 169.00 , Equipment Re-Mobilization $24 , 761.00 , Maintenance and Traffic Contro
1999-10-21 | Construction | Delays | MAJOR WIDENING(O) | 8 | CUMBERLAND | Because of the delay in the project as a result of the contaminated soil , the prices on the new job mix proportions had changed. | The new job mix prices were increased to reflect inflation from July , 1987 to September , 1993.
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | There was contaminated soil in the roadway cut from Sta. 414+50 to 418+00 on the KY 17 to KY 16 Connector Road. | All work was suspended by a Stop Work Order dated November 30 , 1987. This stop work order was partially rescinded on May 9 , 1988 , when the contractor was directed to proceed with all work except in the above contaminated soil area. Since the contr
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | Contaminated soil needed to be placed in the fill area. | Portable air monitors and gas detectors were required for on site air monitoring at the fill area.
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | The Division of Waste Management , Department for Environmental Protection , Natural Resources and Environmental Protection Cabinet required several items because of the contaminated soil found on this project. | A Change Order was needed to pay for physical examinations and training for the Contractor's and the Transportation Cabinet's personnel; monitoring and testing equipment; site security; undercutting , aeration and capping contaminated soils and the insta
1999-10-21 | Environmental | Underground Tank | MAJOR WIDENING(O) | 8 | CUMBERLAND | During construction an underground storage tank was discovered approximately 60 feet Rt. Sta 431+25. | No solution was given.
1999-10-21 | Construction | Temporary Fencing | MAJOR WIDENING(O) | 8 | CUMBERLAND | Unauthorized persons needed to be prevented from entering the project. | A security fence was erected around the contaminated cut and fill area by the contractor , Rt. And Lt. Sta 406+00 to Sta 421+00. Fence was given to maintenance once the project was finished.
1999-10-21 | Materials | Backfill | MAJOR WIDENING(O) | 8 | CUMBERLAND | The soil backfill at abutments No. 1 and No.2 was not acceptable to CSX railroad. Although the backfill was previously acceptable , the new inspector for CSX Railroad rejected this backfill. | The approved backfill consisted of #4 and #57 stone backfill placed on Table II fabric.
1999-10-21 | Construction | Delays | MAJOR WIDENING(O) | 8 | CUMBERLAND | All 1 , 066 linear feet of BCCS pipe was delivered to the project in anticipation of laying pipe Rt. of Sta 410+66 to 421+50. Due to the extended delay in the project , the bituminous coating on the pipe had weathered and cracked. | Pipe was repaired by cleaning then recoating the damaged area with approved coating.
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | There were concerns that the contaminated silt might erode from the cut and fill areas of the project limits and get into the adjacent streams. | Contractor was directed by KDOT to construct a silt check/siphon dam to control and catch contaminated silt that may erode from the cut and fill areas of the project limits and into adjacent streams. Siphon dam was located in the ditch at approximately 15
1999-10-21 | Environmental | Contaminated Material | MAJOR WIDENING(O) | 8 | CUMBERLAND | The Kentucky Department of Transportation directed the contractor to place contaminated material on fill in approximately six inch lifts. | Each lift was disked to allow the contaminates to evaporate.
1999-10-21 | Drainage | Pipes | MAJOR WIDENING(O) | 8 | CUMBERLAND | The backfill was not draining properly. | Six inch perforated pipe was placed behind the railroad bridge abutments to drain backfill.
1999-10-20 | Design | Omission | MAJOR WIDENING(O) | 8 | PULASKI | There were concerns regarding traffic safety at Station 3429+95 and Station 3549+50. | Guardrail end treatments were added to improve safety at these two areas.
1999-10-20 | Construction | Wells | NEW ROUTE(O) | 8 | PULASKI | A water well was uncovered during the removal of a one story frame house on Parcel Number 5. | The water well located Right of Sta. 105+80 was plugged in accordance with Section 711.03.02 of the Standard Specifications for Road and Bridge Construction.
1999-10-20 | Construction | Contracts | NEW ROUTE(O) | 8 | PULASKI | The project should have included the realignment of a side road but since the project was under bridge replacement funds , it could not be extended to include the side road. | Reconsider funding when additional work may be required.
1999-10-20 | Structures | Guardrail | NEW ROUTE(O) | 8 | PULASKI | There was insufficient cover over the culvert at Station 712+83 to install guardrail. | The guardrail post had to be anchored to the top slab of the culvert.
1999-10-20 | Drainage | Omission | NEW ROUTE(O) | 8 | PULASKI | A junction box was shown on the pipe sheets but was omitted from the pipe summary. | A Change Order was necessary to add the junction box.
1999-10-20 | Construction | Contracts | NEW ROUTE(O) | 8 | PULASKI | The precast manufacturer was having problems obtaining forms for the 7' x 4' box sections for a culvert. | A 72 equivalent concrete pipe was constructed instead of the precast 7' x 4' box culvert at KY 103 Approach Station 67+45.
1999-10-20 | Drainage | Omission | MAJOR WIDENING(O) | 8 | PULASKI | There was unsuitable drainage from Station 3587+00 to 3588+32. | A culvert pipe and a modified drop box inlet were added.
1999-10-20 | Geotechnical | Piling/Drilled Shaft | NEW ROUTE(O) | 8 | PULASKI | An aquifer or spring was encountered during construction. Since subsurface drilling is performed at defined locations , the aquifer was not discovered until construction began. | At the direction of the geotechnical branch , piles were driven lower to achieve proper driving resistance and pile tip elevations.
1999-10-20 | Design | Shelved Plans | NEW ROUTE(O) | 8 | PULASKI | The project was let using an older requirement for crushed stone base. | A Change Order revised the gradation and deduction table for the crushed stone base on the project. The contractor used crushed stone base that met the newer requirements.
1999-10-20 | Pavement | Striping | MAJOR WIDENING(O) | 8 | PULASKI | The proposal called for the striping operation to be performed as the fresh asphalt was placed. However , the reflectorization of the paint was not good. | It was decided to use temporary pavement striping and then perform permanent striping after the bituminous surface cured.
1999-10-20 | Drainage | Pipes | NEW ROUTE(O) | 8 | PULASKI | The use of soil in depressed medians to support vegetative growth was questioned when rock roadbed is specified. It was felt that the soil in the median would create a dam that trapped water in the rock roadbed material. | Perforated pipes could be included in the rock roadbed to help prevent the trapping of water.
1999-10-20 | Environmental | Asbestos | NEW ROUTE(O) | 8 | PULASKI | During the removal of a frame dwelling from the construction site , asbestos material was found inside the dwelling. The audit was conducted by a certified asbestos contractor who found asbestos present in 5400 square feet of roof shingles and 456 squar | This material was removed and disposed in accordance with the current Kentucky Environmental Protection Agency , Division for Air Quality Regulations. Dwellings taken in the right of way process should be inspected for asbestos and other harmful materia
1999-10-20 | Maintenance of Traffic | Detours | NEW ROUTE(O) | 8 | PULASKI | The detour set up in the roadway plans for KY 103 Approach was deleted at the request of the contractor. | The work was completed under traffic using flag people.
1999-10-20 | Design | Quantities | MAJOR WIDENING(O) | 8 | PULASKI | There were excess quantities of Channel Lining Class II , Silt Checks , Emulsified Asphalt RS-2 , Traffic Bound Base , and Crushed Stone Base. | A Change Order was set up to decrease quantities.
1999-10-20 | Structures | Reinforcement Steel | NEW ROUTE(O) | 8 | PULASKI | The reinforcing steel for the shafts was set up as a separate bid item. | It should have been incidental to the cost of the shaft.
1999-10-20 | Construction | Railroads | NEW ROUTE(O) | 8 | PULASKI | There was debris on the railroad right of way that was also within the right of way of the roadway. | The contractor was compensated for cleaning up the debris.
1999-10-20 | Pavement | Design | NEW ROUTE(O) | 8 | PULASKI | Bituminous concrete base was to be placed directly on the rock roadbed. However , the limestone on this project was very hard to crush , and the tolerances for rock roadbed construction could not be met. | The pavement design was changed to place four inches of crushed stone base on the rock roadbed in order to create a smoother surface for paving operations. The depth of bituminous base was reduced by one inch.
1999-10-20 | Structures | Elevation Difference | NEW ROUTE(O) | 8 | PULASKI | The water table was higher than what was indicated because an aquifer or spring was encountered during construction. | A Change Order was necessary to raise the grade of the bridge pier footers.
1999-10-20 | Construction | Railroads | NEW ROUTE(O) | 8 | PULASKI | The project could not be opened because of a conflict with a railroad crossing. | Change Orders compensated the contractor for maintaining a road closure on the project for nearly two years.
1999-10-20 | Right-of-Way | Fencing | NEW ROUTE(O) | 8 | PULASKI | The debris and mud from the 1997 flood destroyed a right-of-way fence on the project. | A Change Order was necessary to replace the right-of-way fence.
1999-10-20 | Structures | Reinforcement Steel | NEW ROUTE(O) | 8 | PULASKI | The transverse bars in the top and bottom of the bridge slab were interchanged on the project plans and were insufficient. | A Change Order was made to correct the bridge deck reinforcement. Also , the size of the reinforcement bars in the bottom deck was increased from a #6 to a #7 bar. This increased the amount of steel reinforcement by 638 pounds.
1999-10-20 | Erosion Control Plan | Omission | NEW ROUTE(O) | 8 | PULASKI | A ditch needed Channel Lining. | A Change Order was set up to add Channel Lining for the ditch.
1999-10-20 | Pavement | Coordination | NEW ROUTE(O) | 8 | PULASKI | There was some duplication of rock roadbed quantities between the grade and drain and surfacing contracts. | There was some rock roadbed to be placed on the grade and drain project at the tie-in points.
1999-10-20 | Drainage | Ponding | NEW ROUTE(O) | 8 | PULASKI | Cross sections were not provided for a farm haul road and more fill was needed than was indicated on the plans. | An additional quantity of 24 pipe was needed to prevent water from ponding in this area.
1999-10-20 | Construction | Ride Quality | MAJOR WIDENING(O) | 8 | PULASKI | The contract contained a Special Note for Bituminous Pavement Rideability. | Lump sum adjustments were made for pavement rideability.
1999-10-20 | Geotechnical | Cut-Slope | NEW ROUTE(O) | 8 | PULASKI | The overburden benches were left off the top of the rock cuts with the overburden slopes coming right down to the rock cut face. There have been problems with erosion and stability since the underlying rock has many solution features and crevices. | The use of an overburden bench on top of the rock would have prevented some of the problems by moving the toe of the overburden slope back from the rock cut face.
1999-10-20 | Pavement | Omission | MAJOR WIDENING(O) | 8 | PULASKI | Contract items necessary for median crossovers were omitted. | Bituminous Surface Class I 20/30 was added to the contract for the median crossovers.
1999-10-20 | Pavement | Striping | MAJOR WIDENING(O) | 8 | PULASKI | It was agreed that D-10 Division of Traffic would do the corrective work that the contractor was supposed to perform. | The contractor agreed to reimburse the Department for the cost of restriping 2500 L.F. of pavement.
1999-10-20 | Construction | Railroads | NEW ROUTE(O) | 8 | PULASKI | The project could not be opened because of a conflict with a railroad crossing. | Change Orders compensated the contractor for maintaining a road closure on the project for nearly two years.
1999-10-20 | Structures | Geotextile Fabric | NEW ROUTE(O) | 8 | PULASKI | There was an insufficient amount of geotextile fabric. | Additional geotextile fabric was needed in order to place the fabric as it was shown on the contract plans.
1999-10-20 | Maintenance of Traffic | Signage | NEW ROUTE(O) | 8 | PULASKI | People did not know to change their driving habits when through intersections were changed or when new roadways were open. | Message boards , signs , rumble strips , and other traffic control devices should be included in projects to let people know about road closures or changes in traffic flow patterns.
1999-10-20 | Geotechnical | Slides | MAJOR WIDENING(O) | 8 | PULASKI | A slide occurred on the project which blocked the roadway. | The contractor received a lump sum payment for emergency work to remove the slide.
1999-10-20 | Materials | Asphalt Mixtures | NEW ROUTE(O) | 8 | PULASKI | The unit bid price for bituminous concrete materials needed to be determined based on the approved job mix formula asphalt content. | A Change Order adjusted the unit bid price for the bituminous concrete materials based on the approved job mix formula asphalt content.
1999-10-20 | Structures | Piling/Drilled Shaft | NEW ROUTE(O) | 8 | PULASKI | There were problems concerning the drilled shaft foundation on the bridge on the Auburn Bypass. The plans only specified a two foot rock socket for the shafts. | The sockets had to be extended to compensate for the solution features in the rock.
1999-10-20 | Geotechnical | Elevations | NEW ROUTE(O) | 8 | PULASKI | The original ground elevations were higher that what was indicated on the contract drawings. | Structure Excavation Common was increased for two culverts.
1999-10-20 | Geotechnical | Communication | NEW ROUTE(O) | 8 | PULASKI | It was noted that many items from the Geotechnical Notes are not making it into the final plans. Additional stripping of topsoil was required by the Geotechnical Notes but was not included in the bid quantities. | The Geotechnical Branch stated that they are trying to review projects before letting to catch these omissions.
1999-10-20 | Design | Intersection | NEW ROUTE(O) | 8 | PULASKI | The use of Y or curved type tie-ins between the old and new roadways was questioned. Most of the tie-ins have to be built under traffic , and the Y or curved tie-ins are difficult to construct and maintain traffic. | The use of T type tie-ins was recommended.
1999-10-20 | Materials | Asphalt Mixtures | MAJOR WIDENING(O) | 8 | PULASKI | The plans contained a Special Note for control and acceptance of asphalt mixtures. | Lump sum adjustments were made for bituminous mixtures as per the Special Note for control and accepatance of asphalt mixtures.
1999-10-20 | Geotechnical | Top of Rock | NEW ROUTE(O) | 8 | PULASKI | Rock was found at a higher elevation than expected during excavation for a 8' x 5' double box culvert. | This required that the rock be removed two feet below the footing elevation so that the culvert would rest on the same material throughout its length.
1999-10-20 | Erosion Control Plan | Calculations | NEW ROUTE(O) | 8 | PULASKI | The cross section of the constructed ditch differed from what was used in the channel lining calculations. | An additional quantity of channel lining was needed to place channel lining as it was shown on the plans.
1999-10-20 | Traffic | Raised Pavement Markers | NEW ROUTE(O) | 8 | PULASKI | The project did not comply with the Department's Uniform Traffic Control. | Pavement Markers Type IV-MW were added.
1999-10-20 | Design | Quantities | NEW ROUTE(O) | 8 | PULASKI | Guardrail quantities were insufficient. | Additional guardrail was required because of a box culvert next to the roadway shoulder and because of the cantilever signal structures at the railroad crossing.
1999-10-20 | Design | Guardrail | NEW ROUTE(O) | 8 | PULASKI | The proposed guardrail end treatments did not conform to the Department's compliance plan for guardrail terminals on NHS routes. | The Type 4 Guardrail End Treatments were replaced with Type 1 Guardrail End Treatments.
1999-10-20 | Design | Guardrail | NEW ROUTE(O) | 8 | PULASKI | The proposed guardrail end treatments did not conform to the Department's compliance plan for guardrail terminals on NHS routes. | The Type 4 Guardrail End Treatments were replaced with Type 1 Guardrail End Treatments.
1999-10-20 | Design | Safety | NEW ROUTE(O) | 8 | PULASKI | There was insufficient protection for the traveling public at an at-grade crossing. | A Change Order was necessary to install additional guardrail.
1999-10-20 | Drainage | Pipes | NEW ROUTE(O) | 8 | PULASKI | Larger pipes are more difficult to match up , and gaps between the pipes can occur. This can allow soil to infiltrate between the pipe joints. | Wider bands are needed to connect larger pipes.
1999-10-20 | Drainage | Existing Pipe | NEW ROUTE(O) | 8 | PULASKI | The 8' x 5' double box culvert was supposed to be an extension of an existing box culvert but the existing culvert was in poor condition. | The existing box culvert was removed and replaced.
1999-06-23 | Utilities | Existing Utilities | NEW ROUTE(O) | 1 | GRAVES | An 8 inch sewer line at centerline Sta. 402+75 was preventing the construction of a box culvert. | The contractor was compensated for temporarily relocating the sewer line so the construction of the box culvert could proceed.
1999-06-23 | Design | Borrow/Waste | NEW ROUTE(O) | 1 | GRAVES | The plans indicated this would be a Waste project with a bid item of ROADWAY EXCAVATION; however , during construction there apparently was not enough material from the roadway cuts to build the embankments , so it ended up actually requiring borrow (i | This was an initial 2-lane with 4-lane ultimate ROW , so the additional material was obtained from within ROW limits with no change order. The swell factor for larger jobs with large cuts needs to be investigated closely so that the earthwork quantities
1999-06-23 | Right-of-Way | Fencing | NEW ROUTE(O) | 1 | GRAVES | There was a need to enclose the existing right of way left of Sta. 370+90 to Sta. 377+15.50 from where excess right of way was previously sold. | A Change Order was issued to construct a permanent right of way fence.
1999-06-22 | Maintenance of Traffic | Plan |  |  |  | The plans did not allow for 2 lanes of traffic to be maintained throughout this area in a manner safe for the travelling public due to grade differentials. | Additional granular material and geotextile were added so shoulders would have the same pavement design as mainline. This project would have benefitted from a constructability review.
1999-06-22 | Geotechnical | Subsurface |  |  |  | Estill County commonly faces additional geotechnical issues such as New Albany Shale and saturated material. | Place-holder bid items and quantities could possibly be set up to allow for a variety of mitigation measures , but this will skew the contract price and be more costly than change order process.
1999-06-22 | Construction | Coordination |  |  |  | Waterline construction was directly affected by construction sequence; the waterline could not be completed until the New Albany Shale cut was completed. Cut-slopes were constructed in very sensitive clay shales which are very problematic. | The Geotechnical Branch recommended using a direct bore method with a polyethylene pipe to prevent any disturbance to the New Albany Shale which was required to be covered with 4 feet of clay material. The cut-slopes were stabilized with fabric and crush
1999-06-22 | Maintenance of Traffic | Changes | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Traffic control within Hazard required revision to maintenance of traffic per plans , including a detour which was not included in the plans. | Better communication with city officials may have brought this situation to light earlier.
1999-06-22 | Maintenance of Traffic | Changes | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Traffic control within Hazard required revision to maintenance of traffic per plans , including a detour which was not included in the plans. | Better communication with city officials may have brought this situation to light earlier.
1999-06-22 | Design | Plans | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Adjacent property site construction (building removal and new construction) required drainage accommodation and curb adjacent to sidewalk. | Update site survey if necessary , and review for impacts to final plans prior to letting.
1999-06-22 | Design | Plans | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Adjacent property site construction (building removal and new construction) required drainage accommodation and curb adjacent to sidewalk. | Update site survey if necessary , and review for impacts to final plans prior to letting.
1999-06-22 | Design | Plans | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Adjacent property site construction (building removal and new construction) required drainage accommodation and curb adjacent to sidewalk. | Update site survey if necessary , and review for impacts to final plans prior to letting.
1999-06-22 | Maintenance of Traffic | Changes | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Traffic control within Hazard required revision to maintenance of traffic per plans , including a detour which was not included in the plans. | Better communication with city officials may have brought this situation to light earlier.
1999-06-22 | Drainage | Ponding | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Upon steel truss erection , it was observed that water was standing in the low chord of the truss. | Central Office Bridge Design produced a four hole drill design to help evacuate the water.
1999-06-22 | Utilities | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | During construction , it was found that many utilities were either not located correctly on the plan sheets or were omitted. Plan quantities for utility relocation were insufficient to complete the work. | Various utility quantities were adjusted according to existing and newly uncovered field utility conditions.
1999-06-22 | Utilities | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | During construction , it was found that many utilities were either not located correctly on the plan sheets or were omitted. Plan quantities for utility relocation were insufficient to complete the work. | Various utility quantities were adjusted according to existing and newly uncovered field utility conditions.
1999-06-22 | Utilities | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | During construction , it was found that many utilities were either not located correctly on the plan sheets or were omitted. Plan quantities for utility relocation were insufficient to complete the work. | Various utility quantities were adjusted according to existing and newly uncovered field utility conditions.
1999-06-22 | Drainage | Ponding | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Upon steel truss erection , it was observed that water was standing in the low chord of the truss. | Central Office Bridge Design produced a four hole drill design to help evacuate the water.
1999-06-22 | Drainage | Ponding | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Upon steel truss erection , it was observed that water was standing in the low chord of the truss. | Central Office Bridge Design produced a four hole drill design to help evacuate the water.
1999-06-22 | Traffic | Signals | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Signal plans and traffic configuration were changed as a result of a post-letting city request. | Heightened coordination with local officials should be used for projects within city limits.
1999-06-22 | Design | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Stamped concrete sidewalk bid items and incidental work was ambiguous , so bidding was unclear and adjusted via change order. | Plan notes for unusual work items may warrant review by construction staff and/or constructability staff.
1999-06-22 | Design | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Stamped concrete sidewalk bid items and incidental work was ambiguous , so bidding was unclear and adjusted via change order. | Plan notes for unusual work items may warrant review by construction staff and/or constructability staff.
1999-06-22 | Design | Omission | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Stamped concrete sidewalk bid items and incidental work was ambiguous , so bidding was unclear and adjusted via change order. | Plan notes for unusual work items may warrant review by construction staff and/or constructability staff.
1999-06-22 | Traffic | Signals | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Signal plans and traffic configuration were changed as a result of a post-letting city request. | Heightened coordination with local officials should be used for projects within city limits.
1999-06-22 | Traffic | Signals | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Signal plans and traffic configuration were changed as a result of a post-letting city request. | Heightened coordination with local officials should be used for projects within city limits.
1999-06-22 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Concrete was miscalculated on structure plans. Haunches were not calculated and included in the plan set. | A more thorough check of calculations may have caught this error.
1999-06-22 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Concrete was miscalculated on structure plans. Haunches were not calculated and included in the plan set. | A more thorough check of calculations may have caught this error.
1999-06-22 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 1 | LIVINGSTON | Concrete was miscalculated on structure plans. Haunches were not calculated and included in the plan set. | A more thorough check of calculations may have caught this error.
1999-03-24 | Geotechnical | Cut-Slope | MAJOR WIDENING(O) | 2 | DAVIESS | Fractures and mud seams remained in the rock walls after the cuts were originally presplit and excavated. | A Change Order was necessary for Slope changes and to excavate additional material from rock cuts Lt. Station 212+00 to 217+50 and Rt. Station 217+50 to Station 218+00.
1999-03-24 | Drainage | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | The culvert pipes at Stations 111+25 , 114+40 , and 164+00 were installed during part-width construction of the roadway in order to facilitate traffic. These pipes were located in rock fills and had shallow cover heights. | Crushed Aggregate No. 8 Stone was added in order to backfill the culvert pipes.
1999-03-24 | Construction | Wells | MAJOR WIDENING(O) | 2 | DAVIESS | A well was encountered during construction at Station 152+75. | The well was capped and filled in accordance with Section 711 of the Standard Specifications.
1999-03-24 | Drainage | Pipe Sizing | MAJOR WIDENING(O) | 2 | DAVIESS | The plans called for a 42-inch culvert pipe to be set up at Station 222+60. However , current fill height charts required a larger pipe at this location due to a 90-foot embankment. | A Change Order was necessary to install 54-inch pipe in lieu of 42-inch culvert pipe.
1999-03-24 | Construction | Earthwork | MAJOR WIDENING(O) | 2 | DAVIESS | Unsuitable material was encountered at various locations on the project. | The contractor undercut these areas and an additional quantity of roadway excavation was needed to complete the work.
1999-03-24 | Pavement | Design | MAJOR WIDENING(O) | 2 | DAVIESS | The original plans called for one layer of base and surface with earth shoulders. However , the Division of Design Pavement Branch was provided with updated traffic projection information which indicated this route would have significant truck traffic. | This Change Order was necessary to revise the mainline and shoulder pavement design throughout the project. The Division of Design Pavement Branch made a pavement design revision utilizing two courses of base and paved shoulders.
1999-03-24 | Design | Slopes | MAJOR WIDENING(O) | 2 | DAVIESS | A slope revision was made on the project Lt. Station 133+00 to Station 135+00. | Additional excavation was required.
1999-03-24 | Drainage | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | here was no channel lining established for a ditch from Rt. Station 120+00 to Station 125+50. | A Change Order was necessary to channel line the ditch.
1999-03-24 | Drainage | Elevation | MAJOR WIDENING(O) | 2 | DAVIESS | A ditch grade was too low and the fill slope was too steep which created a need for guardrail Lt. Station 269+25 to Station 274+00. | A Change Order was necessary to construct a drop box inlet in lieu of a sloped & flared headwall at the inlet of the 24-inch culvert pipe Lt. of Station 272+40. This change allowed the new ditch grade to be raised and the fill slope to be flattened which
1999-03-24 | Design | Guardrail | MAJOR WIDENING(O) | 2 | DAVIESS | The plans did not comply with the current design standard for guardrail systems. | A Change Order was necessary to install Type 4A end treatments in lieu of Type 4 End Treatments.
1999-03-24 | Design | Guardrail | MAJOR WIDENING(O) | 2 | DAVIESS | The plans did not comply with the current design standard for guardrail systems. | A Change Order was necessary to install Type 4A end treatments in lieu of Type 4 End Treatments.
1999-03-24 | Erosion Control Plan | Omission | MAJOR WIDENING(O) | 2 | DAVIESS | There was inadequate erosion control throughout the project. This project was let prior to the requirement of erosion control plans. | Additional silt checks , Silt Fence , and one Silt Trap Type A were added through a Change Order.
1999-03-24 | Erosion Control Plan | Channel Lining | MAJOR WIDENING(O) | 2 | DAVIESS | The contractor wanted to use Class IV Channel Lining for riffle structures in lieu of Riffle Structure-Dumped Stone. | Due to the ample supply of rock on the project the project engineer allowed the contractor to use this material. The structures were constructed in accordance with the plans and specs and the material met the same specs as the original bid item.
1999-03-24 | Geotechnical | Top of Rock | MAJOR WIDENING(O) | 2 | DAVIESS | While excavating for the box culvert at station 185+80 , unsuitable rock was encountered at the plan footing grade. | An additional quantity of concrete was needed in order to increase the footing depth down to sound rock as required by the plans.
1999-03-23 | Design | Safety | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The slopes Rt. of Sta. 50+50 to Sta. 54+00 KY 69A Connector were flattened to 4:1 in order to eliminate guardrail. | A Change Order was needed to establish a unit price for Metal End Section of an 18 inch pipe. This type of headwall was needed to meet safety standards.
1999-03-23 | Drainage | Pipes | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The contractor requested to use a ten gauge 78 inch diameter corrugated steel pipe in lieu of the corrugated structural plate steel pipe which was specified on the plans. | The request was granted.
1999-03-23 | Pavement | Type | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The bituminous mixes had a JMF different from the Target Asphalt Content established in the Proposal. | New unit prices were established for bituminous mixes having a JMF different from the Target Asphalt Content established in the Proposal. This change was in accordance with the £Special Note for Asphalt Cement Quantity When Laboratory Mix Design is Requi
1999-03-23 | Maintenance of Traffic | Detours | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The detour shown on the plans encroached up to about two feet from a dwelling. | The pavement taper from Sta. 9+89 to 17+89 had to be readjusted , the grades revised , and the existing pavement salvaged. These adjustments eliminated the need for the detour , caused less disruption to traffic through Hawesville , and shortened the
1999-03-23 | Maintenance of Traffic | Changes | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Certain items were no longer needed due to the previous revision which eliminated the need for a proposed detour. | A Change Order was established to reflect the reduction in certain items.
1999-03-23 | Maintenance of Traffic | Plan | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | There was a need for temporary traffic control on the KY 69 connector to the project. The connector was completed but could not be opened to traffic until US 60 was opened. | A unit price for temporary traffic control was established. The price for this item included installation , maintenance , and removal of necessary signs , barricades , barrels and other items necessary to close this portion of KY 69 until opened to t
1999-03-23 | Design | Shoulders | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The typical sections shown on the plans needed to be modified where guardrail was added. These areas had already been constructed according to the project plans and had to be changed to meet the new guardrail standards. | A Change Order was set up to establish a unit price for shoulder embankment in order to construct the slopes to a ╜¥ per foot fall as shown on the standard drawings for Type 3 and Type 2A End Treatments.
1999-03-23 | Maintenance of Traffic | Changes | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this change was to establish items to trench and stabilize the widened portions of the salvaged pavement and to undercut and stabilize areas where the pavement had to be completely removed. | The areas were excavated one foot below the subgrade elevation. Once the areas were excavated , Number 2 stone along with geotextile was placed in the area.
1999-03-23 | Design | Omission | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Water wells were shown on the plans however there were no provisions explaining the procedure to close the water wells. | A Change Order was set up to establish a unit price to plug water wells at a Sta. 205+90 , 207+85 , and 237+15 that were encountered during construction.
1999-03-23 | Design | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The curb and gutter along with the sidewalk did not match the existing site conditions. | Additional quantities of Barrier Header Curb were used behind the sidewalk at various locations along the right side from Sta. 16+00 to 20+00.
1999-03-23 | Utilities | Existing Utilities | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Texas Gas Co. had installed a new pipeline across the area of the proposed roadway prior to letting the project. The back slope of a proposed channel change could not be stabilized on the back slope due to the backfill pipeline. | Therefore a 60 inch corrugated steel pipe was installed near the gas line and backfilled with native soil.
1999-03-23 | Erosion Control Plan | Channel Lining | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The existing material for use as embankment was very sandy and highly erodible. Additional quantities of channel lining were needed to keep the ditches from washing out. | A Change Order was set up to establish additional quantities of Channel Lining Class III to be used throughout the project for erosion control.
1999-03-23 | Geotechnical | Berms | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | During construction of the roadway embankment in this area , pore pressure readings from instrumentation in place were high enough that it was felt that an embankment failure could occur at any time. The contractor stopped placing any additional materia | It was also decided in consultation with the Geotechnical Branch that a berm 50 foot wide , 30 foot high with 2:1 side slopes be constructed along the toe of the fill to provide lateral support to the embankment and thus reduce the possibility of failure
1999-03-23 | Geotechnical | Slides | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | On the left side of the cut slope , Stations 1290-1294 , a slide had occurred due to the excessive underground water and unstable material on the cut slope. | To correct this slide , unsuitable material was removed and wasted. Geotextile Fabric , Type IV along with sandstone rock was used to restore the original slope as recommended by the Geotechnical Branch , Division of Materials.
1999-03-23 | Erosion Control Plan | Seeding | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this Change Order was to allow the contractor the option of using other tacking agents other than SS-1H for Seed and Protect , Method II. | Hydro-Stik , from Finn Corp. and Agro Tack , from ADI were other viable options on the project.
1999-03-23 | Drainage | Culvert | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | A profile grade revision changed the low point of the vertical curve. | Additional quantities of culvert pipe were needed because of the profile grade revision.
1999-03-23 | Geotechnical | Subsurface | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this change order was to establish funds and a pay item for Channel Lining Class III. The project was let with Channel Lining Class IV , as well as rock roadbed. All of the rock on the project was primarily shale , most of which was not | The site was reviewed by the Geotechnical Section and they agreed that the rock was not suitable for Channel Lining Class IV.
1999-03-23 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | There was insufficient drainage from the wick drains to the sides of the fill. | Additional quantities of Drainage Blanket ô Embankment were used from Sta. 152+00 to Sta. 162+00.
1999-03-23 | Maintenance of Traffic | Detours | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The original detour item included costs for detours at both ends of the project but the one from Sta. 9+86 to Sta. 24+00 was eliminated. | An item was established for construction of one detour at the east end of the project from Sta. 188+00 to Sta. 200+00. This item reflects the savings in eliminating the second detour.
1999-03-23 | Utilities | Existing Utilities | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | There were sanitary sewer lines that were in conflict with the reconstruction of US 60 through Hawesville from Sta. 10+00 to Sta. 22+00. | A Change Order was set up to establish items associated with relocating existing sanitary sewer lines. It was agreed that Hale , Riney , and Gilmore Inc. Surveying and Engineering complete the plans as set forth by the City of Hawesville.
1999-03-23 | Drainage | Culvert | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this change was to establish items to allow the box culvert at Sta. 161+47 to withstand an anticipated 39 inches of settlement in the original ground. | Additional camber was added to the culvert with relief joints to allow deflection and to control cracking. In order for this to be done , the foundation had to be undercut and stabilized one foot below the bottom of the slab with crushed stone six to ei
1999-03-23 | Construction | Contracts | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this change was to correct an error in Change Order Number 3. | The unit price for Maintain and Control Traffic was deleted instead of the unit price for Detour Construction.
1999-03-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The guardrail throughout the project did not meet current standards. | A Change Order was set up to modify contract items and establish new unit prices in order to construct guardrail throughout the project.
1999-03-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The guardrail throughout the project did not meet current standards. | A Change Order was set up to modify contract items and establish new unit prices in order to construct guardrail throughout the project.
1999-03-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Drainage was insufficient in locations where new guardrail end treatments were to be constructed. | A Change Order was set up to establish a unit price for Drop Box Type 5 to be used at these locations.
1999-03-23 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Drainage was insufficient in locations where new guardrail end treatments were to be constructed. | A Change Order was set up to establish a unit price for Drop Box Type 5 to be used at these locations.
1999-03-23 | Drainage | Pipes | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Four inch perforated pipe was needed to insure drainage in the Number 2 Stone Stabilization which was used for trenching and undercutting. | The pipe was placed in the edges of the trench and connected to drainage boxes in the area.
1999-03-23 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Water was getting trapped from Sta. 13+56 to Sta. 16+10. | A Change Order was set up to establish an item to drain the trapped water.
1999-03-23 | Pavement | Repair | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | There were cracks in the existing PCC pavement. | An item was established for sawing and resealing the cracks in the existing pavement.
1999-03-23 | Design | Omission | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The existing centerline stripe on the bridge was offset to match the existing road and the existing lane width was narrower than the new portions. | The existing stripes were removed by sandblasting and the bridge was restriped to match the new construction.
1999-03-23 | Pavement | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Areas where the existing pavement was salvaged and widened did not match the new typical sections. | An item was established for leveling and wedging the bituminous pavement in areas where it had been salvaged and widened. The price was based upon the asphalt content of the mix that was used and was not eligible for price adjustment based on asphalt con
1999-03-23 | Construction | Earthwork | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The purpose of this change order was to add a bid item for Waste Excavation. The project was bid with 1 , 119 , 132 yards of embankment-in-place which required 155 , 087 cubic yards of borrow material. Instead , it appeared that the project had 150 , 0 | The contractor agreed to furnish and place sandstone , from a borrow site , in the required areas to complete the project if the department agreed to pay to waste the remaining yards of material in the cut area from Sta. 1294+00 to 1310+00.
1998-04-09 | Structures | Quantities | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | The plain reinforcement steel for the Husband Road Viaduct over Old Benton Road and the P & L Railroad was underestimated. | A Change Order was necessary to increase steel reinforcement quantities on the project.
1998-04-09 | Geotechnical | Subsurface | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | Extremely swampy conditions were encountered when excavation on the project began. It was not possible to construct the 8 cement modified roadbed as was required in the plans. | It was decided to raise the grade and construct a 16 granular embankment with geotextile fabric. This alternative facilitated drainage and provided a working platform on which to construct the new pavement system. A Change Order was necessary to provide
1998-04-09 | Utilities | Plans | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | During construction , two manholes , which were not shown on the plans , were discovered in the intersection of Wayne Sullivan Drive and Beltline Highway. | These two manholes required new castings and reconstruction in order to conform to their new grades.
1998-04-09 | Traffic | Signals | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | Frontage Road No. 4 now handles all traffic from former Oaks Road and Old Benton Road. The Division of Traffic requested that traffic signals be installed at the intersection of New Husbands Road and Frontage Road No. 4. | A Change Order was necessary to install traffic signals at the intersection of New Husband's Road and Frontage Road No. 4.
1998-04-09 | Maintenance of Traffic | Safety | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | While Kentucky Street was closed to traffic , the traveling public was making an illegal and dangerous turn using private property. | Flexible guide posts Type 3 were installed to discourage this hazardous maneuver.
1998-04-09 | Structures | Guardrail | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | Change Order No. 8 moved the barrier wall on the bridge to separate vehicular traffic from the sidewalk. This necessitated placing guardrail in the utility strip between the sidewalk and the curb , which didn't allow enough room for the Type 4A End trea | A Change Order was necessary to substitute guardrail end treatment Type 7 for guardrail end treatment Type 4A.
1998-04-09 | Construction | Coordination | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | A tree , located off the right-of-way , was killed by the adjacent road construction thus creating a hazard for the property owner. | The contractor was required to completely remove the dead tree and stump on Parcel 56.
1998-04-09 | Design | Omission | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | The contract plans required electrical conduit and junction boxes but they were inadvertently omitted from the contract bid items. | A Change Order was necessary to establish bid items for electrical conduit and junction boxes for the barrier walls of the bridge over the P & L Railroad.
1998-04-09 | Pavement | Type | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | The contractor was able to obtain Crushed Stone Base at the same cost of DGA. | The project team decided to use Crushed Stone Base because it would better facilitate drainage of the subgrade. A Change Order was necessary to substitute Crushed Stone Base in lieu of DGA Base.
1998-04-09 | Design | Shelved Plans | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | The existing grades on Old Benton Road were incompatible with the grades on the new construction. Between the time the plans were prepared and the project was let , Old Benton Road was resurfaced which necessitated a transition to tie in to the plan gra | A Change Order was necessary to add a bid item for Asphalt Pave Milling and Texturing to the contract.
1998-04-09 | Structures | Reinforcement Steel | PAVEMENT REHAB-INT(P) | 99 | FAYETTE | The spacing of the steel reinforcing was not adequate to accommodate the aggregate of the concrete mix. | The spirals for the column reinforcement was changed from #4 bar with a 3 pitch and a 4 ft diameter to a #5 bar with a 3.25 pitch and a 4'-2 diameter.
1998-04-08 | Geotechnical | Subsurface | NEW ROUTE(O) | 7 | MERCER | There was insufficient rock roadbed on the grade and drain project. The rock roadbed was to come from rock excavation on the project , and the estimates of available rock were incorrect because of the solution features and crevices in the limestone. | Rock had to be purchased to complete the rock roadbed.
1998-04-08 | Materials | Asphalt Mixtures | NEW ROUTE(O) | 7 | MERCER | The unit bid price for bituminous concrete materials needed to be determined based on the approved job mix formula asphalt content. | A Change Order adjusted the unit bid price for the bituminous concrete materials based on the approved job mix formula asphalt content.
1998-04-08 | Maintenance of Traffic | Contract | NEW ROUTE(O) | 7 | MERCER | A diversion at the beginning of the project that was built and signed by the grade and drain contractor had to be utilized on the surfacing contract. | A Change Order was set up for signing , barricades , and barrels for the surfacing contractor to maintain this diversion.
1998-04-08 | Pavement | Coordination | NEW ROUTE(O) | 7 | MERCER | There was some duplication of rock roadbed quantities between the grade and drain and surfacing contracts. | There was some rock roadbed to be placed on the grade and drain project at the tie-in points.
1998-04-08 | Design | Guardrail | NEW ROUTE(O) | 7 | MERCER | The proposed guardrail end treatments did not conform to the Department's compliance plan for guardrail terminals on NHS routes. | The Type 4 Guardrail End Treatments were replaced with Type 1 Guardrail End Treatments.
1998-04-08 | Design | Guardrail | NEW ROUTE(O) | 7 | MERCER | The proposed guardrail end treatments did not conform to the Department's compliance plan for guardrail terminals on NHS routes. | The Type 4 Guardrail End Treatments were replaced with Type 1 Guardrail End Treatments.
1998-04-08 | Pavement | Type | NEW ROUTE(O) | 7 | MERCER | The Contractor wanted to use Crushed Stone Base instead of DGA. | The use of Crushed Stone Base instead of DGA was allowed as it had been used on the other sections of US 68 and was acceptable to the Pavement Design Section.
1998-04-07 | Drainage | Ditches | MAJOR WIDENING(O) | 7 | CLARK | Additional ditches were needed to avoid future problems. | Ditches were added to the project and were lined with Channel Lining Class IV. The final fuel price adjustment was added.
1998-04-07 | Geotechnical | Settlement | MAJOR WIDENING(O) | 7 | CLARK | Many of the large fills on this job have settled. Dips in the guardrail and cracks in the pavement have developed because of this. Many of the dips and cracks have occurred at the cut-fill transition. | It may be necessary to provide a waiting period before paving to allow this settlement to occur. It also may be necessary to perform settlement analysis on large fills even though no structure is involved. Changes in the benching techniques at cut-fill tr
1998-04-07 | Design | Borrow/Waste | MAJOR WIDENING(O) | 7 | CLARK | Splitting construction sections in the middle of a cut has sometimes been done for balance on a project. | Stopping construction sections in the middle of a cut should be avoided because constructability should take precedence over balance.
1998-04-07 | Design | Plans | MAJOR WIDENING(O) | 7 | CLARK | Ground lines were incorrect on the plans. This was probably due to the quality of the aerial photography used on the project. | Additional quantities of excavation were required because of incorrect ground lines. Aerial photography in the mountainous terrain is moderately accurate but not close enough to provide sufficient information for accurate plans. The age of the aerial pho
1998-04-07 | Design | Communication | MAJOR WIDENING(O) | 7 | CLARK | Insufficient coordination with the Department of Mines caused issues including relocation of roadways during construction in order to avoid silt ponds. | Closer coordination with the Department of Mines should be followed during the design phase in areas with extensive strip or underground mining.
1998-04-07 | Right-of-Way | Fencing | MAJOR WIDENING(O) | 7 | CLARK | There are considerable differences of opinion on where right of way fence should or should not be installed. Operations prefer that fence be installed everywhere to avoid encroachment. Others feel that fence needs to be installed in areas to prevent hun | Some clear guidance with input from all divisions should be provided for construction personnel.
1998-04-07 | Design | Entrance | MAJOR WIDENING(O) | 7 | CLARK | The grades on entrances in mountainous terrain are often allowed to be too steep. | Although the design requirements allow a 20% grade , it is probably too steep for most normal entrances.
1998-04-07 | Environmental | Wells | MAJOR WIDENING(O) | 7 | CLARK | A gas well did not show on the plans; but it might have been a recent installation. | An access road to the gas well was added.
1998-04-07 | Geotechnical | Mine | MAJOR WIDENING(O) | 7 | CLARK | Active strip mining and the removal of spoil material also increased the excavation needed. | Excavation quantities were added. A smaller pipe was used to drain the coal auger holes that were backstowed.
1998-04-07 | Drainage | Stream Mitigation | MAJOR WIDENING(O) | 7 | CLARK | Gabion mattresses were set up to prevent erosion on the channel change at Joe's Branch , but the contractor proposed a value engineering change. | The mattresses were changed to Channel Lining Class III.
1998-04-07 | Geotechnical | Cut-Slope | MAJOR WIDENING(O) | 7 | CLARK | There was unstable material at the top of cuts. | Additional quantities of excavation were required to remove the unstable material.
1998-04-07 | Design | Quantities | MAJOR WIDENING(O) | 7 | CLARK | There were additional quantities of excavation. | Overhaul was added and a minor amount of fuel price adjustment was included.
1998-04-07 | Design | Borrow/Waste | MAJOR WIDENING(O) | 7 | CLARK | Areas to flatten slopes and to waste material were not identified in the plans. | Areas to flatten slopes or to waste material should be identified in the plans. This helps construction personnel find areas to dispose of excess material.
1998-04-07 | Design | Relocation | MAJOR WIDENING(O) | 7 | CLARK | Joe's Branch Road was relocated to avoid silt ponds. | Additional drainage items were changed due to the relocation. Also , additional quantities of excavation were required because of the unsuitability of existing material. Much of the unsuitable materials was spoil from old strip mines.
1998-04-07 | Design | Quantities | MAJOR WIDENING(O) | 7 | CLARK | There were unnecessary quantities of pneumatic backstowing , shade trees , and Channel Lining Class 1A. | The excess quantities were eliminated.
1998-04-07 | Design | Plans | MAJOR WIDENING(O) | 7 | CLARK | Many plan sheets are so cluttered that it is hard to locate a place to add a revision. | Space needs to be left on plan sheets to allow for construction revisions. Allowing space on the plan sheets may eliminate the need for a separate revision sheet.
1998-04-07 | Drainage | Drop Box Inlets | MAJOR WIDENING(O) | 7 | CLARK | Drop boxes in rock cuts sometimes cannot be properly maintained. Rocks fall from the cut into the ditch and then may be transported by the water into the drop box. | The use of sloped and flared headwalls or safety headwalls may prevent this problem; however , it may require the addition of headwalls for pipes greater than 18 inches into the standards.
1998-04-07 | Environmental | Silt Ponds | MAJOR WIDENING(O) | 7 | CLARK | An access road was to be added across from Joe's Branch Road but there were some mine silt ponds discovered in that area. | The connection of Joe's Branch Road was moved approximately 300 feet back station to avoid the ponds. This required a culvert to be lengthened and grades of a channel change to be steepened. Other pipes and associated hardware had to be adjusted. Extra qu
1998-03-03 | Construction | Earthwork |  |  |  | Existing base failures in the mainline roadway needed to be repaired. | Excavation quantities were set up in order to repair the existing base failures.
1998-03-03 | Design | Piping |  |  |  | The plans did not match the existing pipe. | A 48 inch culvert was placed at Station 88+82.41 in order to match the existing pipe.
1998-03-03 | Design | Plans |  |  |  | The header curb at stations 76+17 to 78+00 and left Station 93+96 to 97+70 did not match existing ground elevations and was unsafe. | A Change Order was necessary to construct a retaining wall and handrail to replace the proposed header curb.
1998-03-03 | Pavement | Design |  |  |  | PMAC-10 was added to the final course of bituminous base and bituminous surface for driving lanes and turning lanes. | A Change Order was necessary to add the Special Note for Polymer-Modified Asphalt Cement to the contract.
1998-03-03 | Design | Piping |  |  |  | A water line was not long enough to maintain the required minimum cover in a slope at Station 103+00. | The 12 inch water line was extended to maintain the required minimum cover in the slope.
1998-03-03 | Drainage | Ditches |  |  |  | Subsurface water was encountered in the mainline subgrade at Station 107+00 to 111+00. | A Change Order was necessary to relocate the caution signal poles at the Redwing Drive intersection in order to allow construction of the ditchline and to install perforated pipe to allow for drainage.
1998-03-03 | Right-of-Way | Insufficient ROW |  |  |  | There were concerns that a roadway embankment would encroach upon two parcels. | A Change Order was made to construct additional an additional retaining wall in order to prevent the roadway embankment from encroaching on the parcels. Additional bituminous surface was needed to restore the existing pavement where the retaining wall wa
1998-03-03 | Drainage | Existing Pipe |  |  |  | The drainage system was not allowing drainage from the adjacent property. | A Change Order was necessary to reconstruct the drainage system at Lt. Station 88+00 to 91+00 to allow drainage from the adjacent property.
1998-03-03 | Right-of-Way | CAP |  |  |  | As per the right of way agreement on Parcel 22 , a light pole needed to be removed from the property. | The light pole Lt. Station 101+80 was removed and new conduit and wiring were installed to maintain the remaining lighting structures on the property.
1998-03-03 | Right-of-Way | Easements |  |  |  | The temporary easements were not easily visible on the plans. | The contractor and Department personnel felt that temporary easements need to be shown better on the plans.
1998-03-03 | Design | Entrance |  |  |  | There were several entrances throughout the project that needed to be maintained during construction. | Traffic bound base was set up in order to maintain the entrances throughout the project.
1998-03-03 | Design | Quantities |  |  |  | The final quantity of Bituminous Base met the criteria for an excessive underrun. | A Change Order was necessary to adjust the original unit bid price pursuant to Section 104.02.02 of the Department's Standard Specifications for Road and Bridge Construction.
1998-03-03 | Design | Plans |  |  |  | Cross-sections don't tie-in from the mainline to the intersection. This caused a problem in setting grades on superelevated sections. | The contractor and Department personnel would like to see extra cross-sections in the plans. This was suggested as a project specific solution. It is noted that intersection development sheets should be included in all applicable project plans.
1998-03-03 | Traffic | Pedestrian Signals |  |  |  | The pedestrian crossing buttons at one intersection on this project were placed behind the guardrail and were not easily accessible. | Department personnel would like to see a Standard Drawing or general note clarifying the requirements for pedestrian crossing buttons for persons with disabilities.
1998-03-03 | Utilities | Relocation |  |  |  | Utility delays could cause a bad public perception. | The utility relocation sub-contractors need supervision and inspection. Relocation plans may need to be checked closer by Department personnel to avoid conflicts. The contractor's personnel suggested a penalty such as liquidated damages be charged to th
1998-03-03 | Design | Relocation |  |  |  | The handrail at Lt. Station 91+87 to 93+77.5 was needed at Lt. Station 101+34 to 103+50. | A Change Order was necessary to modify prefabricated handrail and relocate it.
1998-02-25 | Structures | Specifications | PAVEMENT REHAB-PRI(P) | 99 | PERRY | The Type 4 Guardrail End Treatments called for in the plans did not comply with new specifications. | A Change Order was necessary to replace the Type 4 Guardrail End Treatments with Type 4A End Treatments in accordance with the new specifications.
1998-02-24 | Maintenance of Traffic | Diversions | ROCKFALL MITIGTN(P) | 10 | MENIFEE | There were concerns that the diversion would be unable to support the high volume of traffic and that high water might rise above the diversion during the winter months and cause a major disruption to the traveling public. | A Change Order was necessary to raise the embankment diversion grade 2 feet and to place an additional 3 inch lift of Class I Bituminous Base on the diversion. It was suggested that more attention be paid to the pavement design for diversion routes.
1998-02-24 | Construction | Omission | BRIDGE REPLACEMENT(P) | 10 | WOLFE | No staking item was set up for this project. | Review of Bid Items needed before letting.
1998-02-24 | Construction | Contracts | ROCKFALL MITIGTN(P) | 10 | MENIFEE | The construction of the new structure and roadway was halted for several months due to flooding. | A completion incentive was added to open the new facility to traffic by 12/16/94. Also it was agreed to allow a time extension so that if the new facility was opened by 12/16/94 any remaining work could be performed in the Spring of 1995 without the asse
1998-02-24 | Right-of-Way | Communication | BRIDGE REPLACEMENT(P) | 10 | WOLFE | Slopes of 2:1 were created on private owner's properties. To the owner's dissatisfaction of this steep slope and unmowable area the contractor re-graded for a less steep slope. | Communication to owners at the Right-of-way stage , the description of what will happen to their yards when the road is complete.
1998-02-24 | Structures | Piling/Drilled Shaft | ROCKFALL MITIGTN(P) | 10 | MENIFEE | One pier hit directly over the existing pier. It was very difficult to drive new concrete piling on existing concrete piles. | It was decided to reuse some of the existing piles.
1998-02-24 | Design | Test Case | ROCKFALL MITIGTN(P) | 10 | MENIFEE | This bridge was the first one in Kentucky to be constructed with seismic isolation bearings and needed to be performance tested. | A Change Order was necessary to establish a unit price for Dywidag material.
1998-02-24 | Structures | Erosion Control | ROCKFALL MITIGTN(P) | 10 | MENIFEE | There were concerns regarding the temporary structure and slope stability during a potential occurrence of high water. | A Change Order was necessary to lengthen the temporary structure twenty feet and protect the slopes using fabric and rock as requested by the Central and District Offices.
1998-02-24 | Erosion Control Plan | Omission | ROCKFALL MITIGTN(P) | 10 | MENIFEE | It was felt that there were not enough erosion control items set up on the original contract and that the erosion control plan should be more detailed. | Maintenance has driven sheet piling to help hold the embankment due to high water erosion. It was felt that this project should have had rip-rap placed on the slopes throughout for erosion control especially during high water periods.
1998-02-24 | Structures | High Grade | BRIDGE REPLACEMENT(P) | 10 | WOLFE | The bridge was designed on a 4% vertical curve. The ends of the beams were going to bear into the edge of the concrete at End Bent #1 and shift bearing. | Designers should keep in mind during design of higher sloped bridges to check the beam seats to make sure the beam ends do not conflict on the edges of concrete and change bearing. In this case , lead plates were added for more height so the beam could
1998-02-24 | Drainage | Temporary Drainage | ROCKFALL MITIGTN(P) | 10 | MENIFEE | The diversion was washed away by winter flooding. | A Change Order was necessary to establish items to reconstruct the diversion.
1998-02-24 | Erosion Control Plan | Seeding | BRIDGE REPLACEMENT(P) | 10 | WOLFE | Temporary seeding quantities were increased due to the timing of construction that went from the fall thru spring seasons. | Timing projects is hard to consider during design and calculating these types of quantities is even harder , therefore this issue is deemed unavoidable. Lump Sum payment should be set up for these items.
1998-01-07 | Pavement | Thickness |  |  |  | Updated traffic projections predicted higher volumes. | Pavement thickness was increased as per Central Office , Division of Design.
1998-01-07 | Erosion Control Plan | Seeding |  |  |  | Cuts were not seeded. | District personnel would like to see a note on the plans stating that cuts should be seeded as they are brought down.
1998-01-07 | Pavement | Design |  |  |  | The plans called for traffic to be maintained on DGA Base despite heavy truck traffic. | The pavement design was altered to allow the use of Bituminous Base for maintenance of traffic.
1998-01-07 | Pavement | Design |  |  |  | Performance grade asphalt binders were not called for in the plans. | A Change Order was necessary to permit the use of performance grade asphalt binders conforming to section 806.06 of the supplemental specifications.
1998-01-07 | Geotechnical | Top of Rock |  |  |  | The solid rock line was lower than what was shown on the plans for all 3 culverts on this project. | It was suggested that the contractor and Resident Engineer in the future check the surface elevations on drill holes in order to confirm plan elevations.
1998-01-07 | Geotechnical | Top of Rock |  |  |  | Rock elevations were found at different elevations other than what was designated on the plans. | Culvert footings at three different locations were redesigned using floating footer pads.
1998-01-07 | Structures | Phasing |  |  |  | The culvert at approximately station 258+00 was constructed part-width. This was very complicated to build. | Guardrail had to be installed in order to maintain safety in this area.
1998-01-07 | Design | Plans |  |  |  | Existing signs were taken down by the contractor and stored at a waste area. Most of the signs ended up destroyed or lost. | District personnel would like to see a note on the plans concerning salvaging and replacing signing.
1998-01-07 | Design | Alignments |  |  |  | There were concerns about the beginning and ending project tie-ins. There were grade differences in these two areas which resulted in forming a pocket of water. It was felt that the project may have been tied down at an undesirable point. | This area needed to be designed for pipe but no consideration was given to these grade differences.
1998-01-07 | Drainage | Pipes |  |  |  | There were concerns regarding erosion and shoulder stability. | Sloped inlets and outlets were added on entrance pipes.
1998-01-07 | Construction | Bench Marks |  |  |  | Some bench marks were off by as much as one foot on this project. | It was determined that levels should be checked more closely using a level in lieu of using trigonometric leveling.
1998-01-07 | Utilities | Relocation |  |  |  | After utility lines were relocated there still was not adequate clearance during construction for the contractor to fit equipment. | Utility lines on this project had to be relocated a second time.
1998-01-07 | Geotechnical | Slides |  |  |  | Several pop slides occurred on the project. The material from these slides had to be removed causing an overrun of Roadway Excavation. The material was hauled an average distance of 8100 feet due to the unavailability of a waste area , which resulted i | The area between the new road and existing facility could have been used for a waste area. There was a property in this area that wasn't bought during R/W negotiations but the Department ended up condemning it.
1998-01-06 | Traffic | Signals |  |  |  | The job was held up because of signal installation. | The signals should have been change ordered to allow the closing of this job.
1998-01-06 | Design | Quantities |  |  |  | The project encountered excavated material and waste site preparation in excess of plan quantity. | A Change Order was set up to reimburse the contractor.
1998-01-06 | Drainage | Drop Box Inlets |  |  |  | The contractor was directed to change the location of the drop box inlet Type 5 from Station 350+50 to Sta. 355+50. | The change in location required that the box be built in a sag rather than in grade condition.
1998-01-06 | Utilities | Relocation |  |  |  | Utility relocation was not completed by the specified dates. During the delay , a new building was constructed near Parcel 54. The close proximity of this building required the contractor to alter his blasting pattern. | The contractor changed his blasting pattern from thirty pounds of explosive to fourteen pounds of explosive. The contractor was reimbursed for additional mobilization costs.
1998-01-06 | Design | Median |  |  |  | It was decided to cross hatch the flush median islands with yellow pavement markings. | A Change Order was set up to reimburse the contractor.
1998-01-06 | Environmental | Underground Tank |  |  |  | Two 1 , 000 gallon underground storage tanks were found on Parcel 54. | The two storage tanks were removed and disposed by the contractor.
1998-01-06 | Design | Plans |  |  |  | The plans did not depict the existing sidewalk , curb , and gutter adjacent to the entrance on Moberly Road. | The contractor had to reconstruct a sidewalk with a modified ramp , Type 3 and curb and gutter at this location.
1998-01-06 | Pavement | Design |  |  |  | Heavy truck traffic exists within the area. | Polymer should have been set up in the pavement design initially.
1998-01-06 | Environmental | Asbestos |  |  |  | Asbestos material was present in the structures on Parcel 54. | Asbestos material had to be removed and disposed by the contractor.
1998-01-06 | Design | Intersection |  |  |  | There were concerns regarding potential vehicle accidents in the future at the intersection of KY 390 and US 127 due to heavy truck traffic. | There should have been a right turning lane installed from US 127 onto the bypass.
1998-01-06 | Erosion Control Plan | Omission |  |  |  | There were concerns about potential erosion and undermining of the entrance at Station 46+90. | A Flume Inlet Type 1 modified was installed.
1998-01-06 | Design | Borrow/Waste |  |  |  | There were some concern with how the RDZ area was classified for rock. There was much more material left over than anticipated. | Hauling could have been a problem if the adjacent property owners had not allowed fill areas.
1997-12-17 | Utilities | Plans | GRADE & DRAIN | 9 | MASON | The approach model was not blended into the mainline model to generate accurate disturb limits. Approach tie in areas , especially in cut areas , warrant conservative utility easements or relocations to allow for variances from anticipated site conditi | Designers need to be aware of complicatiojns that can occur with at-grade intersections. Modeling the mainline to adjacent roadways produces more accurate disturbed limits. The Roanoke Road and KY 393 intersection (utilities and drainage) was revised (f
1997-12-17 | Maintenance of Traffic | Omission | GRADE & DRAIN | 9 | MASON | Caution lights were needed at the intersection of KY 22 and the relocated section of KY 393 to provide for the temporary traffic condition. | KYTC installed these lights under a separate contract , but because of the delay getting the caution lights operational , the contractors work came to a standstill. A more extensive review of the situation for sight distance issues as related to tempo
1997-12-17 | Design | Communication | RELOCATION(O) | 9 | MASON | The final design of an access road to the University of the Cumberlands was included in the plans right up to the letting but was removed for administrative reasons. | Numerous meetings were held between the College administration , the district design staff , and JDQ. No increase in communication during the design phase of this project could have resolved the issue.
1997-12-17 | Drainage | Drop Box Inlets | SURFACE(O) | 9 | MASON | A new box inlet was supposed to replace an existing box which was determined suitable for reuse. | The box was changed from a Curb Box Inlet Type B to a Modified Type 13 in order to utilize the existing box. The old box was used with an updated lid.
1997-12-17 | Traffic | Omission | GRADE & DRAIN | 9 | MASON | Lighting items had to be added due to an omission on the plans. | A more thorough review by Traffic Operations may have prevented this oversight.
1997-12-17 | Design | Guardrail | GRADE & DRAIN | 9 | MASON | Temporary guardrail and related end treatment types were adjusted as necessary in an area that had been heavily wooded prior to clearing/grubbing operation. | Unavoidable.
1997-12-17 | Design | Guardrail | GRADE & DRAIN | 9 | MASON | Temporary guardrail and related end treatment types were adjusted as necessary in an area that had been heavily wooded prior to clearing/grubbing operation. | Unavoidable.
1997-12-17 | Pavement | Design | SIGNING(P) | 9 | MASON | The expansion material was not low enough in the joint between the shoulder and driving lane. As a result , several joints were damaged by PCCP Grinding and Texturing. | A Change Order was necessary to repair the joints that were damaged.
1997-12-17 | Geotechnical | Subsurface | GRADE & DRAIN | 9 | MASON | Unsuitable rock was discovered; and pond leaks and were causing this area to be wet. | More material had to be excavated to bring the ditch lines down to grade.
1997-12-17 | Geotechnical | Subsurface | RELOCATION(O) | 9 | MASON | Slide material was removed. It was suspected that deep mines were present in this area. | Another geotechnical boring located higher on the slope may have identified this issue. Additional right-of-way width is needed to allow for future maintenance in mountainous areas (e.g. , slide repair).
1997-12-17 | Pavement | Quantities | SIGNING(P) | 9 | MASON | There was excessive deterioration of the concrete pavement. | Additional partial depth patching was necessary.
1997-12-17 | Erosion Control Plan | Omission | GRADE & DRAIN | 9 | MASON | Geotextile Fabric Type I was called for per plan under Rip Rap (for armoring banks at abutments) and omitted from contract bid items. | A Constructability Review may have identified this omission.
1997-12-17 | Right-of-Way | CAP | GRADE & DRAIN | 9 | MASON | Drainage items were added to accommodate a ditch design change that was made in Right-of-Way stage but not fully incorporated into final plans. | There needs to be better communication of CAPs.
1997-12-17 | Utilities | Existing Utilities | GRADE & DRAIN | 9 | MASON | Close proximity of overhead transmission power lines caused a buildup of charge on the bridge itself. When the bridge was touched , it shocked. | The solution was to ground the overhead electric. To accomplish this , copper wires were driven into the north end of the bridge. Similar issues on future projects could be dealt with by including a Special Note in the Proposal calling attention to the
1997-12-17 | Environmental | Stream Mitigation | RELOCATION(O) | 9 | MASON | Site conditions in the planned mitigation areas were not conducive to construction of a successful stream channel. | Stream restoration items were deleted; in-lieu fees were paid instead.
1997-12-17 | Design | Guardrail | SIGNING(P) | 9 | MASON | There were some concerns regarding potential roadside hazards. | Safety headwalls were installed on the drainage structures (pipes , small culverts) to eliminate roadside hazards by allowing a reduction in the number of guardrail sections on the mainline.
1997-12-17 | Design | Guardrail | SIGNING(P) | 9 | MASON | There were some concerns regarding potential roadside hazards. | Safety headwalls were installed on the drainage structures (pipes , small culverts) to eliminate roadside hazards by allowing a reduction in the number of guardrail sections on the mainline.
1997-12-17 | Structures | Guardrail | SIGNING(P) | 9 | MASON | The bridge end connectors in the plans did not match with the existing field conditions. | The bridge end connectors were changed in order to match existing conditions.
1997-12-17 | Utilities | Communication | GRADE & DRAIN | 9 | MASON | Multiple issues (both addressed via change order and not so addressed) arose due to gas transmission lines in close proximity of material that must be removed with blasting. Hoe ramming was used to remove material in proximity of LG&E gas transmission. | The proposed recommendation was made that all gas transmission lines and associated stipulations be called out within contract documents so as to bring additional attention to them. Utility staff have adjusted review process to allow (as possible) for de
1997-12-17 | Geotechnical | Subsurface | GRADE & DRAIN | 9 | MASON | Roadway Excavation adjustment was necessary due to site conditions changing between site survey and letting (e.g. , solid rock was located at a higher grade than shown in the plans for abutment 1). | This location was addressed via Special Note in the proposal.
1997-12-17 | Design | Grade | GRADE & DRAIN | 9 | MASON | Property owners typically have difficulty in interpreting plan information. Driveway grades were improved and work was done via consent and release. | The recommendation was made that in cases where driveway grade is significantly steepened , additional easement be used to flatten grades if at all possible.
1997-12-17 | Construction | Inspection | GRADE & DRAIN | 9 | MASON | QC for Embankment was included in the contract and bridge abutment installation was performed with QC/QA. Bridge ends for South Fork , CurryÖs Fork settled and required correction. | This project did not have adequate quality control; more oversight was needed. The QC/QA process removed direct accountability.
1997-12-17 | Geotechnical | Slides | SIGNING(P) | 9 | MASON | There was an active slide that went unnoticed until construction work on the pipe outlets began. | A Change Order was necessary to correct the slide located in the southbound lanes at approximate Station 1258+10 to 1259+60 in Christian County.
1997-12-17 | Maintenance of Traffic | Phasing | SURFACE(O) | 9 | MASON | Additional items were needed in order to protect the bridge end when traffic was switched after partial completion of the median lane. | Temporary guardrail and temporary end treatments were added. The guardrail was needed because of the shift in traffic after two base courses.
1997-12-17 | Design | Quantities | SIGNING(P) | 9 | MASON | Unforeseen repairs were necessary on the project causing an overrun of several items. | Additional quantities for partial depth patching , full depth patching (at joints) , and traffic control were added.
1997-12-17 | Pavement | Shoulders | SIGNING(P) | 9 | MASON | The expansion material was not low enough in the joint between the shoulder and driving lane. This caused difficulties with obtaining the proper slope for the cross slope on the paved shoulders. | A Change Order was necessary to add milling and texturing to the contract. Milling and repaving were needed to achieve the proper cross slope for drainage on the paved shoulders.
1997-12-17 | Design | Phasing | RELOCATION(O) | 9 | MASON | Adjacent sections of the same corridor had different requirements for borrow and fill quantities. | Material from two separate areas were stockpiled. There needs to be a better balance between borrow and fill quantities within constructible sections of a corridor. Adjacent sections need to be considered during the phasing process.
1997-12-17 | Utilities | Plans | GRADE & DRAIN | 9 | MASON | Utility relocation plan change required change order to provide for Service Relocation. | Utility plan review should typically allow for adjustments as needed. The recommendation was made that additional review methods be incorporated into the existing process. Many utility related issues are unavoidable due to incomplete as-builts performed
1997-12-17 | Construction | Contracts | RELOCATION(O) | 9 | MASON | The number of working days allowed in the contract was too high. | The process for determining working days has already been changed. For contracts as of the date of this post-construction review: the working day methodology uses MS Project software in conjunction with concurrence from the Division of Construction.
1997-12-17 | Maintenance of Traffic | Signage | SURFACE(O) | 9 | MASON | The requirements of section F of the Special Note for Variable Message Signs were not met. | A Change Order was necessary to provide a variable message sign.
1997-12-17 | Geotechnical | Subsurface | RELOCATION(O) | 9 | MASON | Failed roadway material needed to be excavated. It is believed that springs feeding into the embankment have caused roadway failures in this area. | The Geotechnical Branch recommended placing finger drains along the toe of the slope to relieve water pressure.
1997-11-19 | Utilities | Existing Utilities | BRIDGE REPLACEMENT(P) | 1 | BALLARD | Plans were created with at the time current waterline information , but when the job was let , the year before the waterlines were updated and waterlines on the plans showed different casing sizes than the new existing. | Better communication with utility companies and access to current utility as-built plans. Projects that linger for an extended period of time may need to be reviewed closely and check for utilities that may have changed.
1997-11-19 | Design | Shoulders | MAJOR WIDENING(O) | 1 | MCCRACKEN | The plans called for 2.4 meter earth shoulders based on the ADT and as called for in the Standard Specifications. However , there were concerns regarding the design due to the considerably steep slopes needed to effectively control and prevent excessive | The planned earth shoulders were replaced with 2.4 meter full depth DGA shoulders. Additional quantities of DGA Base were established and a credit was rendered to the Contractor for not having to place excavated material back as per the plan.
1997-11-19 | Structures | Granular Pile Core | BRIDGE REPLACEMENT(P) | 1 | BALLARD | The plans showed Cohesive Pile Core but change to current Standards Specifications and Special Provision No. 69 - Granular Pile Core. | Projects need to be reviewed to reflect current standards.
1997-11-19 | Design | Intersection | BRIDGE REPLACEMENT(P) | 1 | BALLARD | Shugar's Hill Road had a steep slope going into US 127 then crossed over to KY 70. US 127 was in a curve and sight issues occurred due to grade differential. Milling occurred on the high side of US 127 (KY 70 side) and Shugar's Hill Road was built-up to | When tying grades at a curve when superelevation is involved , the designer must check the elevations to have proper tie in with at grade intersection.
1997-11-19 | Drainage | Omission | MAJOR WIDENING(O) | 1 | MCCRACKEN | A pipe for the planned entrance at Lt. Sta. 2+992 was not included in the plans , but was necessary for drainage of an existing ditch where the entrance was being constructed. | An additional entrance pipe was added via Change Order.
1997-11-19 | Erosion Control Plan | Seeding | MAJOR WIDENING(O) | 1 | MCCRACKEN | The Division of Construction had concerns that proposed Crown Vetch was not a suitable species to effectively hold in the place the sandy soil type of the project area. | Crown Vetch was replaced with Serecia Lespedeza as recommended by the Division of Construction.
1997-11-19 | Geotechnical | Slides | BRIDGE REPLACEMENT(P) | 1 | BALLARD | Hillslide off the project slid onto the existing KY 70 causing the road to be closed temporarily (3-days) and a detour was created for clean up. | Unforeseen cause and construction proceeded with the clean up to continue completion of the project.
1997-11-19 | Construction | Revisions | MAJOR WIDENING(O) | 1 | MCCRACKEN | There were concerns regarding maintenance of the DGA shoulders , which were added by Change Order , after construction was completed. | Asphalt Seal Aggregate and Emulsified Asphalt RS-2 were added for treatment of the shoulders to aid in their maintenance.
1997-10-21 | Erosion Control Plan | Seeding |  |  |  | Placing the Method II Seeding and Protection from Station 297+50 to Station 365+50 caused problems with the public because of tack overspray. | A Change Order was needed to install excelsior blanket in lieu of Method II Seeding. Central Office Division of Construction recommended this change during an erosion control review.
1997-10-21 | Pavement | Striping |  |  |  | There were concerns regarding the maintenance effort required to annually repaint the 4 inch pavement striping that was called for in the plans. | Thermoplastic Pavement Marking 4 inch was substituted for painted 4 inch pavement striping. This change was made due to thermoplastic striping having an estimated lifetime of six years.
1997-10-21 | Utilities | Omission |  |  |  | Marker tape and tracer wire are required by the City of Somerset's gas service for all plastic gas lines. Additionally , the Natural Resources & Environmental Protection Cabinet requires that waterlines within a 200' radius of oil or gas lines , underg | Items needed for compliance with these requirement were not included in the original utility plans; therefore , the items were added by Change Order.
1997-10-21 | Traffic | Signals |  |  |  | It was decided during construction to add a signal the Columbia Street intersection. | In order to expedite the project , the Department agreed to furnish the steel strain posts for the added signal.
1997-10-21 | Design | Quantities |  |  |  | There was an underrun of Asphalt Drainage Blanket Type II. | A Change Order was necessary to decrease quantities of Asphalt Drainage Blanket Type II.
1997-10-21 | Design | Omission |  |  |  | The quantities for removing and hauling guardrail were omitted from the contract plans. | A Change Order was necessary to establish quantities for removing and hauling guardrail.
1997-10-21 | Geotechnical | Embankment Stabilization |  |  |  | This was a widening project of an existing roadway and there were concerns about the condition of an existing retaining wall and possibility of existing embankment slipping. | A Change Order was established to construct additional embankment from Rt. Station 365+00 to Station 366+00 and also to fill in a cavern from Rt. Station 365+20 to Station 365+70. The embankment material was large crushed stone and the embankment was con
1997-10-21 | Utilities | Existing Utilities |  |  |  | A 24 inch storm sewer pipe conflicted with an 8x 8 fiber optics bank which runs perpendicular to the storm sewer pipe and also due to a conflict with an 8 inch waterline. | A Type C Manhole was constructed Lt. Station 357+85. The manhole allowed the fiber optics bank to pass through walls of the chamber and enabled normal drainage flow to continue through the 24 inch pipe.
1997-10-21 | Design | Intersection |  |  |  | There was a Construction Revision that involved a redesign of the median , which removed median crossovers and added left turn lanes at the major approaches and traffic generators. | Signalization was installed at the intersection of US 27 and Adams Street , the intersection of US 27 and Sallee Street , and at the intersection of US 27 and Columbia Street. The existing pavement was milled down to the failure layer at blowup location
1997-10-21 | Construction | Coordination |  |  |  | The median edge drain system was deleted due to a construction revision. However , the subcontractor had already delivered the materials and mobilized equipment for the construction of the edge drain system when the revision was made. | A Change Order was necessary to reimburse the contractor for documented cost for mobilization and bond related to the deletion of the median edge drain system.
1997-10-21 | Utilities | Plans |  |  |  | There were concerns regarding the method of installation of the utilities across mainline US 27. The original plans called for open trenches which were to be backfilled with flowable fill material. | The conduits were bored through the roadway embankments in lieu of an open cut trench. It was felt that traffic flow through this area was enhanced and the contractor's traffic control costs were reduced.
1997-10-21 | Drainage | Omission |  |  |  | Additional items were needed to connect an existing drain to a new storm sewer system on the project. | A Change Order was necessary to establish quantities for PVC Drain Pipe-8 Inch.
1997-10-21 | Geotechnical | Subsurface |  |  |  | The subgrade of the new outside lanes needed stabilization at various locations throughout the project where unsuitable material was encountered. | A Change Order was needed to provide crushed stone and geotextile fabric.
1997-10-21 | Pavement | Design |  |  |  | Also the existing pavement in the northbound lanes and adjacent approaches for the intersection of US 27 and Old KY 80 and the intersection of US 27 and KY 80 Bypass needed repair. | A 5 inch asphalt concrete overlay on the existing pavement in the northbound lanes and adjacent approaches was constructed.
1997-10-21 | Pavement | Design |  |  |  | The existing pavement in the southbound lanes and adjacent approaches for the intersection of US 27 and Old KY 80 West and the intersection of US 27 and Cumberland Parkway needed repair. | A Change Order was necessary to construct a 4 inch concrete overlay on the existing pavement in the southbound lanes and adjacent approaches.
1997-10-21 | Design | Quantities |  |  |  | There was an underrun of Bituminous Concrete Base Class I. | A quantity of Bituminous Concrete Base Class I was deducted from the project.
1997-10-21 | Design | Drainage |  |  |  | There were concerns raised by District and Central Office Highway Design regarding the suitability of the storm drainage system. | Larger culvert pipe was used to facilitate the storm drainage system changes. Two curb box inlets , located Rt. Station 358+05 and 358+72 , were changed from Type A to Type B due to a conflict with the existing right-of-way and a waterline. A special
1997-10-21 | Utilities | Relocation |  |  |  | While laying a string of 18 inch reinforced concrete pipe , an 8 inch gravity flow sanitary sewer line was encountered. | The string of 18 inch reinforced concrete pipe had to be relocated and laid at a different grade.
1997-10-21 | Design | Quantities |  |  |  | Items were set up for the removal of underground storage tanks in the contract , but no underground storage facilities were encountered on this project. | Items for the removal of underground storage tanks were deleted from the contract.
1997-10-21 | Design | Drainage |  |  |  | The original storm drainage system shown on the contract plans only provided surface ditches from an existing 24 inch pipe Rt. Station 354+10 to an existing outlet ditch Rt. of Columbia Street approach at Station 52+85. These plans were considered unsuit | The new system required a Manhole Type A Rt. approach Station 50+96 , a curb box inlet Type F Rt. approach Station 51+61 and a Drop Box Inlet Type 1 Rt. Approach Station 52+85.
1997-10-21 | Pavement | Design |  |  |  | The aggregate base construction was revised from the 12 inch layer of DGA as specified in the original contract plans in order to provide increased base stabilization for the inside (median) shoulders and the new left turn/storage lanes Lt. and Rt. from S | The revised base construction included geotextile fabric on the subgrade with a layer of #2 crushed aggregate and a layer of crushed stone base. The layer of #2 crushed aggregate extended from the edge of the existing pavement to the median ditchline and
1997-10-21 | Maintenance of Traffic | Omission |  |  |  | There was no item set up in the contract for traffic control during KTC's signal testing operation at the intersection of KY 80 and US 27 and the intersection of Cumberland Parkway and US 27. | The contractor was compensated for traffic control provided during the KTC's testing operation.
1997-10-21 | Pavement | Thickness | RELOCATION(O) | 12 | LETCHER | There were concerns regarding the durability of several commercial entrances throughout the project. | A Change Order increased the depth of Asphalt Base Class I from 2 to 4 at all commercial entrances within the project area.
1997-10-21 | Design | Omission | RELOCATION(O) | 12 | LETCHER | A portion of a four foot sidewalk was left out of the original plans. This area included several businesses , residences , one grade school , and one high school. | A Change Order was implemented to provide a 4' (foot) Concrete Sidewalk from RT. Sta. 26+70 to RT. 87+00.
1997-10-21 | Erosion Control Plan | Omission | RELOCATION(O) | 12 | LETCHER | There were concerns regarding potential erosion control problems on this project. | Silt Checks , Silt Traps , Silt Fence , and Straw Bales were selectively installed throughout the project area. Contract working days remained unchanged.
1997-10-21 | Design | Quantities | RELOCATION(O) | 12 | LETCHER | It was noted that an accurate quantity of TBB for maintenance of entrances is difficult to be estimated ahead of the construction phase. | A Change Order was necessary for additional quantities of Traffic Bound Base (TBB) needed to maintain numerous entrances within the project area.
1997-10-21 | Erosion Control Plan | Omission | RELOCATION(O) | 12 | LETCHER | Sodding of a utility strip was omitted. | A Change Order was set up to provide sodding.
1997-10-21 | Environmental | Underground Tank | RELOCATION(O) | 12 | LETCHER | There were four Underground Storage Tanks filled with contaminated water located at Stations RT. CL 45+92 , 46+00 , 46+08 , and 46+16. | A Change Order was approved to cover the cost of pumping and disposal of contaminated water found in the 4 USTs.
1997-10-21 | Geotechnical | Slides | RELOCATION(O) | 12 | LETCHER | There were several pockets of slides located at Stations 63+80 , 64+50 , 66+00 , and 78+00 that were not noticed until construction was under way. | A Change Order was required to correct the pockets of slides.
1997-10-21 | Design | Elevations | RELOCATION(O) | 12 | LETCHER | There were several areas where the existing asphalt surface elevations were higher than shown on the plan and profile sheets. | A Change Order was established for Milling and Texturing of existing asphalt surfaces.
1997-10-21 | Utilities | Existing Utilities | RELOCATION(O) | 12 | LETCHER | There were concerns regarding whether mainline pipes could maintain their integrity under load. | DGA was used to backfill the top 6 (on top of sub-grade) of all mainline pipe crossing to ensure the integrity of pipes under load.
1997-10-21 | Geotechnical | Subsurface | RELOCATION(O) | 12 | LETCHER | There were numerous areas encountered throughout the project where the sub-grade was very unstable. | A Change Order was required to undercut and stabilize , using granular embankment and geo-textile fabric , the numerous unstable areas.
1997-10-21 | Design | Quantities | RELOCATION(O) | 12 | LETCHER | A residential entrance constructed of cement concrete pavement RT of Sta. 92+67 was set up on the plan and profile sheets but left out from the plan quantities. | A Change Order was set up to establish the items necessary to construct this residential entrance.
1997-10-21 | Design | Safety | RELOCATION(O) | 12 | LETCHER | There were areas where the pavement edge drop-off exceeded 4 , which was thought to be unsafe for the traveling public. | A Change Order was set up to install a wedge of DGA in areas where the drop-off exceeded 4 inches.
1997-10-20 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | During removal of an existing box culvert and construction of the proposed culvert , a conflict occurred with the newly placed temporary slope. This issue should have been addressed on the original plans. | Shoring was required to complete the construction phasing.
1997-10-20 | Environmental | Asbestos | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | During construction , it was found that the barn within the right-of-way limits had asbestos shingles , which was unknown prior to letting. | The shingles were removed and bid item was added to contract for asbestos abatement. It was suggested that all buildings on proposed right-of-way should be investigated for potential environmental issues.
1997-10-20 | Design | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | An additional quantity of embankment in place was needed due to undercutting of unstable material at various locations. | Embankment in Place quantity was increased via Change Order.
1997-10-20 | Maintenance of Traffic | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Plan quantities for traffic bound base were insufficient to maintain traffic on the approach road at Lt Sta 189+10. | An additional quantity of traffic bound base was used.
1997-10-20 | Maintenance of Traffic | Striping | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Traffic was switched to the newly constructed roadway before final surface was placed. | Temporary striping was used for lane delineation.
1997-10-20 | Structures | Beams | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | A bridge beam delivered to the site had a thinner top slab than shown on the bridge plans. | The beam was analyzed by Central Office Bridges and was determined to be adequate. Since the actual beam thickness was different than the plans , a reimbursement was made to the highway department.
1997-10-20 | Erosion Control Plan | Silt Fence | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | There was insufficient erosion control set up from Rt Sta 181+00 to Sta 207+00. | Silt fence was added via Change Order to provide erosion control in this area. Erosion control on projects needs to be investigated during the design phase.
1997-10-20 | Maintenance of Traffic | Phasing | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The construction phasing presented on the plans seemed reasonable , but actual field conditions were prohibitive. | Temporary guardrail was installed in a different location than proposed to allow the necessary clearance for removal of an existing culvert and finish installing the end of a proposed culvert. The guardrail was installed in the center of the new shoulder
1997-10-20 | Design | Entrance | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The entrance at Rt Sta 206+50 was not wide enough to accommodate the farm machinery using it. | The entrance was widened by 2 to 3 feet for the farm machinery using it.
1997-10-20 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | An existing 25'x16' reinforced concrete bridge at Rt Sta 209+57 needed to be removed to open up an existing ditch. A bid item and note for this work was not set up on the initial plans because they were overlooked during the plan stage. | Bid items for this work were added to contract.
1997-10-20 | Construction | ROW | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Contractors on roadway projects are ignoring the fact that right-of-way markers need to be located. When they are located they are being installed in the wrong locations. | It was suggested that the state could take over setting of right-of-way markers. Another option , is for the state to check and verify the locations of markers and for penalties to be imposed for incorrect locations of markers.
1997-10-20 | Drainage | Omission | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | An existing double 8'x6'x60' reinforced concrete box culvert at Lt Sta 206+60 needed to be removed and replaced with a drainage ditch. A bid item for this work was not set up on the initial plans because the bid item and note were overlooked during the p | Bid items for this work were added to contract.
1997-10-20 | Environmental | Contaminated Material | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The existing barn within right-of-way limits also contained lead paint , which was not determined until construction began. | The barn was sealed under the guidelines of the Federal OSHA and was dismantled board by board. The work was accomplished using the Cost Plus method. It was suggested that all buildings on proposed right-of-way should be investigated for potential envir
1997-10-20 | Geotechnical | Subsurface | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Subsidence occurred on the shoulder from Lt Sta 210+40 to Sta 210+75. | The guardrail , pavement , and soil had to be removed and replaced. Fourteen inches of DGA base was installed prior to paving and restriping.
1997-10-20 | Design | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The plans required placing filter fabric in slough areas in preparation of placing rock embankment , but the Design quantity was insufficient. | The bid quantity was adjusted via Change Order.
1997-10-20 | Design | Special Note | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | There was no note on plans specifying that all embankments shall meet the settlement criteria before driving piles or working on end bents , which caused a problem with the Contractor. The Contractor wanted to proceed with construction on newly built em | District personnel instructed the Contractor not to begin the construction until all settlement had dissipated from the fill. The Contractor filed an intent of claim for the loss of time in working days.
1997-10-20 | Design | Railroads | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The original roadway plans specified placing a 4 inch reinforced concrete slope wall under the end bents that extended beyond railroad right-of-way limits. | An alternative of 12 inches crushed aggregate was presented to the railroad and approved , which resulted in savings of $21 , 788.50 to the Cabinet.
1997-10-20 | Design | Special Note | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | A special note for temporary guardrail was left out of the plans , because there were concerns about the issue of describing temporary guardrail. | A special note should have been set up for temporary guardrail.
1997-10-20 | Geotechnical | Subsurface | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Subsidence occurred on the shoulder from Lt Sta 205+50 to Sta 206+10. | The guardrail was removed , asphalt shoulder was milled and repaved , and guardrail was reinstalled.
1997-10-20 | Erosion Control Plan | Slope Protection | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | The shoulder and inslope had washed out from Rt Sta 185+35 to Sta 188+35. | The solution included grading , shaping , and replacing DGA base and paving the inslope with 1 1/2 of asphalt surface.
1997-10-20 | Geotechnical | Unsuitable Material | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Unstable material was encountered on the project in an area of embankment from Sta 198+00 to Sta 198+50 and from Sta 181+00 to Sta 186+00. | The unsuitable material was undercut 2.5 feet. Geotextile Fabric Type III was placed and 18 inches of granular embankment was placed and capped with 12 inches of embankment in place.
1997-10-20 | Geotechnical | Piling/Drilled Shaft | PAVEMENT REHAB-PRK(P) | 99 | HENDERSON | Although the bridge plans specified driving piles at the end bents , it was determined during construction that pre-drilling into the embankment material was necessary in order to attain a penetration of 10' or more into the original ground while develop | A Change Order was issued that included a bid item for pre-drilling of piles at the end bents. The required length of piling increased as a result.
1997-10-13 | Maintenance of Traffic | Timing | MAJOR WIDENING(O) | 6 | BOONE | Due to timing of project sections being constructed , it was deemed necessary to utilize KY 1836 to access a school. Therefore , safety improvements were added and an increased depth of pavement was necessary to accommodate the traffic. | When adjacent projects are being let in a similar time frame , a constructability review is needed.
1997-08-04 | Maintenance of Traffic | Part Width |  |  |  | Constructing tie-ins using part-width construction , under traffic , is very difficult. | It was suggested that temporary detours should be used wherever possible. If detours are not feasible , then consideration should be given to keeping grades reasonably close at the tie-in points.
1997-08-04 | Structures | Reinforcement Steel |  |  |  | Locations where the reinforcement cages were spliced together were extremely tight and interfered with the placement of concrete in columns. | Extra care should be taken when detailing reinforcing steel for bridge columns.
1997-08-04 | Design | Adjacent Projects |  |  |  | There was an increase in the amount of 4 permanent striping , removal of pavement markers , Bituminous Tack , and Bituminous Concrete Surface Class I-O to resurface remaining section of US 150 not originally part of the project. | When in design look at the condition of nearby road sections to see if they should be included in the project.
1997-08-04 | Design | Guardrail |  |  |  | Type 4A End Treatments were used instead of Type 4 and 7 End Treatments , this was to comply with the current standard drawings. | Check current standard drawings.
1997-08-04 | Materials | Asphalt Mixtures |  |  |  | This change order permitted the use of performance grade asphalt binders to conform to Section 806.06 of the supplemental Specifications. There was no change in project cost. | Review Supplemental Specifications in design process.
1997-08-04 | Design | Guardrail |  |  |  | Type 4A End Treatments were used instead of Type 4 and 7 End Treatments , this was to comply with the current standard drawings. | Check current standard drawings.
1997-08-04 | Erosion Control Plan | Silt Fence |  |  |  | Silt checks and basins were not adequate for this project. | Recommended setting up items for Silt fence , catch basins , and other erosion control devices.
1997-08-04 | Erosion Control Plan | Rock Checks |  |  |  | Suggested to not use straw bales as erosion control as they are commonly not strong enough. | Use of rock check dams suggested.
1997-08-04 | Drainage | Cross Drains |  |  |  | French drains can collect water from a much larger area where as spring boxes have a more limited area of collection. | Suggested that French drains be used instead of spring boxes.
1997-08-04 | Structures | Reinforcement Steel |  |  |  | Armored edge was replaced by Armored Plate per recommendation by Central Office. | Check current standards.
1997-08-04 | Design | Omission |  |  |  | An 18 entrance pipe was shown in the plans but not included in the bid items. | Make sure all items on plans are reflected in bid items.
1997-08-04 | Drainage | Bridge Ends |  |  |  | When large amounts of embankment settlement occur , the flow of water into the curb box can be affected and commonly the pipes are pulled apart as a result of such settlement. | It was suggested that flumes or channel lined ditches should be used at bridge ends rather than curb boxes. Flumes and ditches are much more forgiving to this type of settlement , and should be the first choice of drainage structure at bridge ends.
1997-08-04 | Construction | Specifications |  |  |  | The barrier wall Transitioned to a 6 high standard integral curb before the curb box. The current standards show the transition curb height of 4 inches. | Check current standards.
1997-07-29 | Design | Plans |  |  |  | Breaking projects into small construction and design sections may be less efficient and more costly than maintaining larger segments. | This must be evaluated on a case-by-case basis.
1997-07-29 | Maintenance of Traffic | Safety |  |  |  | The temporary barrier wall placed on the Phase II detour would have been unstable if placed on the outer shoulder in this fill area due to existing steep slopes. | The concrete barrier was replaced by guardrail. A chain link fence was also added above a cut section and retaining wall to provide protection for a residential area.
1997-07-29 | Drainage | Pipes |  |  |  | Because of a change in alignment a pipe would have been located too close to the edge of the road rendering it unusable. | The pipe was replaced.
1997-07-29 | Geotechnical | Slides |  |  |  | Twelve trees in the slide area were hanging over the railroad. | Trees had to be removed.
1997-07-29 | Geotechnical | Settlement |  |  |  | The ground experienced settlement during the winter season. | Additional tack as well as leveling and wedging were needed.
1997-07-29 | Drainage | Pipe Sizing |  |  |  | A twenty seven inch culvert pipe was difficult to locate for purchase and was more expensive. | A thirty inch pipe was used instead.
1997-07-29 | Materials | Asphalt Mixtures |  |  |  | Job mix formula asphalt contents were not adequate. | Corrected asphalt content with a change order.
1997-07-29 | Design | Plans |  |  |  | Construction notes and high water information are included on the profile sheets and the pipe sheets , causing some confusion and sometimes provided conflicting requirements. | Discussion with several offices needs to take place to resolve this issue.
1997-07-29 | Construction | Contracts |  |  |  | Removal of coal by the contractor may lead to liability problems for the Department. | A policy concerning coal extraction by contractors should be established.
1997-07-29 | Environmental | Wells |  |  |  | Two water wells were specified to be filled and capped. An additional well was located during construction. | A change order was made and the well was filled and capped.
1997-07-29 | Right-of-Way | Coordination |  |  |  | Consultants retain plans until right of way acquisition has been completed , so that they can make adjustments to the plans. It is very difficult to predict the hours necessary to perform this work. | An equitable way to reimburse the consultants for this activity should be developed.
1997-07-29 | Maintenance of Traffic | Plan |  |  |  | This section has experienced rutting and pavement failures due to heavy coal truck traffic because rock roadbed was replaced with an equivalent structure because of MOT concerns. | The pavement design should not have been adjusted based on maintenance of traffic concerns. The resident indicated they could have constructed the rock roadbed and handled the MOT concerns.
1997-07-29 | Pavement | Design |  |  |  | The Bituminous Base Class I may have not been adequate to support the heavy truck traffic. | The use of Bituminous Base Class K may have been a better choice.
1997-07-29 | Design | Plans |  |  |  | When select granular fill is required for a project , it is unclear if it must be quarry run or if it can be obtained from the roadway excavation. | Plans should indicate if the expected rock excavation on the project might be suitable for select granular fill with the engineers approval.
1997-07-29 | Geotechnical | Slides |  |  |  | A landslide occurred on the project in an area where the new fill tied into the existing road. | Railroad rails with lagging was installed to correct the problem.
1997-07-29 | Structures | RCBC | MAJOR WIDENING(O) | 4 | HARDIN | Heavy rain and flooding caused undermining of the bottom slab of a culvert. | Flowable fill was pumped under the slab to fill the voids.
1997-07-29 | Right-of-Way | Easements | MAJOR WIDENING(O) | 4 | HARDIN | A court decision was made in favor of the property owner. | A plan change was made to avoid the property.
1997-07-29 | Design | Omission | MAJOR WIDENING(O) | 4 | HARDIN | Butterfly valves and casing pipe was inadvertently omitted from the bid item list. | Be certain all bid items are reflected in the plans.
1997-07-29 | Geotechnical | Settlement | MAJOR WIDENING(O) | 4 | HARDIN | Problems are occurring with backfill settlement around pipes and behind bridge abutments , it is difficult to compact these areas. | The use of flowable fill around cross drains would work , however this could be expensive if only a few places need the fill.
1997-07-29 | Right-of-Way | Easements | MAJOR WIDENING(O) | 4 | HARDIN | A fence placed to keep property owners from falling in the water , made mowing and trash removal very difficult. | This area had to be cleared by small weed cutting machines. It was suggested that a construction easement might have been taken to get drainage of the creek.
1997-07-29 | Drainage | Pipes | MAJOR WIDENING(O) | 4 | HARDIN | A drain pipe outlet was found to be too low in elevation to drain into the proposed ditch. | The pipe was extended into an existing drop box. Check elevations for existing structures when changing ditch elevations.
1997-07-29 | Pavement | Striping | MAJOR WIDENING(O) | 4 | HARDIN | Plan Changes are being made that are not in accordance with anticipated lane arrangements. | Striping plans should be included in the design plans so that construction understands what the final anticipated lane arrangements should be.
1997-07-29 | Utilities | Relocation | MAJOR WIDENING(O) | 4 | HARDIN | The requirements of the city did not match well with current Department requirements. The jurisdiction for inspection of utility relocations was in question. The city required that utility backfill continue to the top of the subgrade which caused bumps | Coordinate projects with local governments before the projects begin the construction phase. Include local officials in the design process.
1997-07-29 | Design | Plans | MAJOR WIDENING(O) | 4 | HARDIN | Guardrail locations are not noted clearly on the plan sheets. | Use a table to note guardrail location and placement. A table could be included on each sheet or one table for the entire project could be inserted into the plans.
1997-07-29 | Utilities | Relocation | MAJOR WIDENING(O) | 4 | HARDIN | A detour tying proposed US 60 to existing US 60 at KY 519 was needed because utility pole relocations were not completed in a timely fashion on the mainline. The mainline was to be the original detour route. | Temporary guardrail was added for traffic control on the detour. Pedestrian signals were added for this phase of the bypass. Standard Header Curb was added to provide for access control.
1997-07-29 | Design | Quantities | MAJOR WIDENING(O) | 4 | HARDIN | Several items were inadvertently omitted from the plans. DGA Base was the major item (9000 tons) and it appeared to be a miscalculation of the quantity required for the shoulders. | Additional Quantities of: Rock Borrow , Pavement Striping , Type III Geotextile Fabric , and Traffic Bound Base were added. Quantities were also added for: DGA Base and Bituminous Tack Material.
1997-07-29 | Drainage | Pipes | MAJOR WIDENING(O) | 4 | HARDIN | An existing 24 pipe was to remain in place but was found to be unusable. | This pipe was removed and replaced. A sloped box outlet was also added for this pipe.
1997-07-29 | Design | Plans | MAJOR WIDENING(O) | 4 | HARDIN | Abbreviated plans do not have sufficient detail and require a great deal of engineering by the Department's construction personnel. | Do not use abbreviated plans.
1997-07-29 | Design | Plans | MAJOR WIDENING(O) | 4 | HARDIN | There is often not enough right-of-way for poles or guide wires , and previous roadway work or utility relocations commonly interferes with planned signal pole locations. | Signal plans should be coordinated with the rest of the plans.
1997-07-29 | Right-of-Way | Fencing | MAJOR WIDENING(O) | 4 | HARDIN | Once the ROW fence was constructed there was no way for the city to access fire hydrants and other facilities behind the fence. | Extra work was needed to provide breaks in the right of way fence so the city had easier access to fire hydrants and other facilities.
1997-07-29 | Utilities | New Utilities | MAJOR WIDENING(O) | 4 | HARDIN | The Crushed Aggregate No. 9 was not suitable for utility backfill , per city guidelines. | Used a Crushed Aggregate for Backfill to allow other suitable stone sizes to be used as backfill.
1997-07-29 | Right-of-Way | Coordination | MAJOR WIDENING(O) | 4 | HARDIN | Some Right of-Way Points were in error. | A construction revision was made.
1997-07-29 | Right-of-Way | CAP | MAJOR WIDENING(O) | 4 | HARDIN | Construction often has difficulty in dealing with property owners , as there is commonly disagreements over what is in the right of way agreement. | Include property owners in the planning process to give them a heads up as to what exactly is in the agreement.
1997-07-21 | Drainage | Omission |  |  |  | There were two culverts that were shown on the plans but left off the list of bid items. | The two culverts were added via Change Order.
1997-07-21 | Design | Entrance |  |  |  | An entrance Lt. Sta. 103+844 did not meet pertinent sight distance standards due to the location of solid rock at the entrance. | A Change Order was issued to pay for Roadway Excavation. This item was utilized to remove solid rock from the entrance to improve sight distance.
1997-07-21 | Drainage | Omission |  |  |  | The pipe needed to connect the existing drainage system into the new storm sewers at various locations was not included in the plans. | A non-perforated pipe was added to connect the existing drainage system into the new storm sewers.
1997-07-21 | Design | Entrance |  |  |  | The entrance pavement for some businesses could not be constructed £part-widthÖ without subjecting the property owner to unnecessary inconvenience and hardship. | The pavement was modified so it could be constructed in 24 hours.
1997-07-21 | Pavement | Design |  |  |  | An insufficient asphalt overlay (100 mm) was originally planned to be placed over the entire existing pavement. The original profile grades were calculated based on the proposed overlay , which did not take the correctness of the finished profile grades | A new profile grade (centerline) was established by the District to meet the minimum requirements of the proposed overlay and allow accurate calculation of the needed overlay in other areas. The new profile grade ensured that curb and gutter would follow
1997-07-21 | Construction | Subsurface |  |  |  | Upon removal of the existing shoulder pavement , unsuitable material was encountered. The material beneath the existing shoulders was saturated due to the presence of bleeders. | The bleeders were extended and unit prices for Geotextile Fabric Type III , Reshaping , and Compacting were established. These items were needed to stabilize the unsuitable material.
1997-07-21 | Erosion Control Plan | Channel Lining |  |  |  | After site conditions were assessed as per the project Erosion Control Plan , there was a need to help control and/or prevent erosion in areas that were not originally considered prone to erosion. | Quantities of Channel Lining Class III were increased in order to construct additional rock-lined ditches throughout the project area.
1997-07-21 | Traffic | Signals |  |  |  | Strain Pole Ground Conductor was needed to properly ground the Steel Strain Poles which were supplied by the Department for this project. Also additional excavation of mostly solid rock , was necessary to construct the signal poles to the planned grades | Unit prices for Strain Pole Ground Conductor and for Pole Base Excavation were established.
1997-07-21 | Drainage | Omission |  |  |  | There were concerns the use of Barrier Header Curb in parking lots to replace the existing curbs that were removed during construction might cause a disruption to the businesses. | Modified Barrier Header Curb was utilized in lieu of Barrier Header Curb at these locations. This item was £slip-formed¥ over asphalt pavement with steel reinforcement driven through the asphalt to ensure stability. The £slip-form¥ method minimized disr
1997-07-21 | Design | Entrance |  |  |  | The plans did not address how to deal with the £Right in/Right out¥ at the entrance Rt. Sta. 102+025. | A Change Order was established to reconstruct the existing median in the entrance. An item was established for £Standard barrier Median Type 2¥ , which was utilized to maintain the £Right in/Right out¥ through the entrance.
1997-07-21 | Design | Omission |  |  |  | An item for Pavement Marker Removal had not been set up on the plans. | A unit price for Pavement Marker Removal was established and the markers were removed and delivered to Nelson County State Maintenance facility.
1997-03-26 | Drainage | Omission | MAJOR WIDENING(O) | 6 | CAMPBELL | Pipes needed to connect edge drains to drainage boxes were left out of the plans. | Four inch non-perforated pipe was added at various locations to connect the edge drains to drainage boxes.
1997-03-26 | Structures | Painting | MAJOR WIDENING(O) | 6 | CAMPBELL | When the concrete guardrail block-outs on the bridges were removed , damage to the paint had inevitably occurred. | A Change Order was established to repair paint on the steel girders of the eastbound and westbound bridges.
1997-03-26 | Drainage | Pipes | MAJOR WIDENING(O) | 6 | CAMPBELL | Field conditions did not physically permit the use of 30 degree prefabricated bends as shown on the plans at Sta. 246+00 , 2411+00 , and 2418+00. | Instead , 18-inch junction boxes were installed at these locations and the prefabricated bends were delivered to Rowan County Maintenance and paid for at the invoice price.
1997-03-26 | Design | Intersection | MAJOR WIDENING(O) | 6 | CAMPBELL | It was determined that the I-64/KY Interchange was inadequate. | A Change Order was approved to implement an addition of a continuous turning lane on KY 32. This change comprised of all items necessary , including utility relocations , to construct the turning lane and included reconstruction of KY 32 for a distance
1997-03-26 | Utilities | New Utilities | MAJOR WIDENING(O) | 6 | CAMPBELL | The widening of KY 32 required switching from the old waterline to a new one. It was paramount to ensure that the water supply to the city and the hospital would not be interrupted. | A Change Order was approved to use a Quick Valve for the waterline switch. This procedure was requested by the City of Morehead and required special knowledge and equipment that was provided by a sub-contractor.
1997-03-26 | Drainage | Drop Box Inlets | MAJOR WIDENING(O) | 6 | CAMPBELL | Two unnecessary Drop Box Inlets (DBI) were encountered during the reconstruction of KY 32. | The DBI's were filled and capped.
1997-03-26 | Traffic | Signals | MAJOR WIDENING(O) | 6 | CAMPBELL | There were safety concerns regarding traffic at the intersection of KY 32 and the I-64 eastbound ramps. | Per direction from the Division of Traffic , traffic signals were constructed at the intersection.
1997-03-26 | Design | Access | MAJOR WIDENING(O) | 6 | CAMPBELL | There was insufficient information to construct temporary slip ramps for the project. | A Change Order was established for performing additional surveying needed to set the grades for the temporary slip ramps.
1997-03-26 | Drainage | Temporary Drainage | MAJOR WIDENING(O) | 6 | CAMPBELL | The necessity for additional drainage structures to prevent water from entering the roadway became apparent during the construction of median cross-overs. | A Change Order was established for installation of additional drainage structures such as pipes and modification inlet structures to prevent run-off from entering the roadway.
1997-03-26 | Drainage | Error | MAJOR WIDENING(O) | 6 | CAMPBELL | Previously constructed slope box outlets did not allow the required side slope for Slip Ramps B and C. This became apparent after the construction of the these slip ramps. | The previously constructed slope box outlets were relocated to allow the necessary side slope for the slip ramps.
1997-03-26 | Pavement | Shoulders | MAJOR WIDENING(O) | 6 | CAMPBELL | Westbound traffic on I-64 utilized a partial width of the shoulder as a driving lane , which caused excessive pavement failure posing a serious hazard to the traveling public. | A Change Order was set up for an emergency repair that required total removal and replacement of 1600 feet of pavement. This work was performed at night and required closing the westbound lane of I-64 and detouring the traffic via US 60.
1997-03-26 | Right-of-Way | Fencing | MAJOR WIDENING(O) | 6 | CAMPBELL | During the course of construction , a 60-foot section of woven wire Right-of-Way fence located between the eastbound and westbound Bullfork Bridge , Triplett Bridge , and bridge over KY 32 was inadvertently damaged. | The Right-of-Way fence was repaired or replaced as appropriate.
1997-03-26 | Drainage | Ditches | MAJOR WIDENING(O) | 6 | CAMPBELL | The widening of KY 32 caused a drainage problem where Ramp A intersected I-64. | A modified paved ditch was constructed and a Drop Box Inlet was lowered to facilitate proper drainage at this intersection.
1997-03-26 | Erosion Control Plan | Silt Fence | MAJOR WIDENING(O) | 6 | CAMPBELL | It was acknowledged that silt fence placed around the drainage boxes in the median did not perform as expected and failed. | Additional erosion control measures such as silt checks , silt fence , and silt fence modified (reinforced with straw bales) were added.
1997-03-26 | Maintenance of Traffic | Quantities | MAJOR WIDENING(O) | 6 | CAMPBELL | There were insufficient quantities of signage set up in the original plans to maintain and control traffic throughout the entire construction phase. | Additional Flashing Arrows Signs were added.
1997-03-26 | Drainage | Existing Pipe | MAJOR WIDENING(O) | 6 | CAMPBELL | Proposed work on an existing pipe on Ramp C would cause a significant disruption of traffic. | This pipe was plugged and abandoned in place. This action did not impact drainage because the new construction provided for alternative drainage on Ramp C.
1997-03-26 | Construction | Inspection | MAJOR WIDENING(O) | 6 | CAMPBELL | Concrete at the pier columns and endbents of westbound Triplett Bridge substructure was found to be grossly deteriorated upon inspection. No work item had been set up for this on the original plans. | A Change Order was established to repair the concrete at the pier columns and endbents.
1997-03-26 | Traffic | Omission | MAJOR WIDENING(O) | 6 | CAMPBELL | A Junction Box Type B was shown on the Lighting Plans but not set up on the bid items summary sheet. | This item was added via Change Order.
1997-03-26 | Pavement | Shoulders | MAJOR WIDENING(O) | 6 | CAMPBELL | Approximately 2000 ft. of the westbound shoulder where traffic was shifted during Phase I of the project experienced rutting and potholes in the pavement appeared due to subgrade failure. The rapid deterioration of this pavement was in part attributed to | A Change Order was approved to repair the numerous rutted areas and potholes.
1997-03-26 | Pavement | Repair | MAJOR WIDENING(O) | 6 | CAMPBELL | An existing layer of Latex was encountered on the Bridge over Bullfork Road where the plans called for Machine Preparation of Existing Slab for the new overlay. | Machine Preparation of Existing Slab was changed to complete removal of the existing overlay in order to prepare for the new overlay.
1997-03-26 | Traffic | Lighting | MAJOR WIDENING(O) | 6 | CAMPBELL | The original lighting layout required the lighting cable to be run through rock. | The Contractor installed #1/3 C Ducted Cable in lieu of the planned #2/3 C lighting cable in order to avoid the rock by using a longer route.
1997-03-26 | Drainage | Error | MAJOR WIDENING(O) | 6 | CAMPBELL | It became necessary to perform underdrain work parallel to I-64 in a sequence other than what was stated in the contract proposal. | This change resulted in extra work and materials and required excavation of a special trench to install the 4-inch underdrains.
1997-03-26 | Maintenance of Traffic | Safety | MAJOR WIDENING(O) | 6 | CAMPBELL | The traffic control plan required westbound I-64 traffic to be placed in the eastbound speed lanes thereby reducing lane widths to an unsafe level. | The concrete guardrail block-outs on the bridges were removed to enhance safety and provide maximum allowable lane widths.
1997-03-26 | Design | Slopes | MAJOR WIDENING(O) | 6 | CAMPBELL | An existing 15-inch culvert in the median at Bullfork Bridge prevented construction of the minimum 12:1 slope required at the end of the Crash Cushion Type IX-A. | The existing 15-inch culvert in the median at Bullfork Bridge was extended.
1997-03-26 | Construction | Delays | MAJOR WIDENING(O) | 6 | CAMPBELL | All construction activities were halted during the winter months of 1997 due to unfavorable weather conditions. | Temporary erosion control measures were placed on the project during the shut down.
1996-12-13 | Design | Special Note |  |  |  | The special note concerning the use of MTV's is the most confusing note associated with asphalt. | The note should be clarified to prescribe whether or not MTV's should be utilized rather than leaving this decision to the Contractor's discretion. In general , all new roadway construction should require it.
1996-12-13 | Construction | Inspection |  |  |  | Erosion control items were included on the plans in accordance with current design policy. However , grade work for the roadway was being performed on a separate contract that was still ongoing , which caused a duplication of erosion control items. Co | Specifications indicate that erosion control items are to be measured for payment. There should have been no redundant cost associated with these items unless the Contractor was simply paid by plan quantity , in which case improved oversight by the Cabi
1996-12-13 | Design | Specifications |  |  |  | The original plans specified construction of asphalt wedge curb on this project but the Contractor had subcontracted someone that primarily specialized in concrete applications. | It was requested and approved to use Concrete Wedge Curb in lieu of Asphalt Wedge Curb at same unit bid price. This substitution of materials may have provided some benefit since some consider concrete to be cleaner , faster , and have a longer life.
1996-12-13 | Construction | Ride Quality |  |  |  | The plans were designed for surfacing on a new route with twelve foot driving lanes and ten foot shoulders. There were concerns about segregation , especially end of load segregation , on the asphalt base and surface courses impacting the ride quality | An item for Asphalt Placement with MTV was added via Change Order. A suggestion was made that all new roadway construction involving asphalt should require the use of MTV's.
1996-12-13 | Construction | Inspection |  |  |  | Final dressing Class B was included on the plans in accordance with current design policy. However , grade work for the roadway was being performed on a separate contract that was still ongoing , which made this item unneeded. At the time the plans we | Specifications indicate that final dressing Class B is to be measured for payment. There should have been no redundant cost associated with this item unless the Contractor was simply paid by plan quantity , in which case improved oversight by the Cabine
1996-12-10 | Maintenance of Traffic | Safety |  |  |  | Variable message signs were requisitioned for traffic control measures. | A change order was approved for variable message signs.
1996-12-10 | Materials | Asphalt Mixtures |  |  |  | Asphalt content needed to be adjusted. | A change order was approved for Asphalt content adjustment.
1996-12-10 | Design | Borrow/Waste |  |  |  | The excavated rock was not suitable for channel lining. | Channel Lining Class III and Class IV (MOD) were used.
1996-12-10 | Pavement | Design |  |  |  | During the removal of existing concrete pavement , cracks appeared to occur randomly in the slabs adjacent to the slabs which were removed by the specified method , which was braking and removal. | Full depth sawing was used at 1-65 ramp tie-in locations.
1996-12-10 | Maintenance of Traffic | Safety |  |  |  | The work zone surrounding the bridge piers needed more protection. | Traffic control plans were altered with usage of concrete barrier walls to protect the work zone.
1996-12-10 | Maintenance of Traffic | Signage |  |  |  | Signing was not included in this contract. | It was determined to let temporary signing for the project during the construction so the ramp portion of the project could be opened to traffic.
1996-12-10 | Structures | Approaches |  |  |  | Due to the large amount of settlement anticipated for the embankment , the District recommended eliminating the approach slabs for this project. | The approach slabs were eliminated.
1996-12-10 | Maintenance of Traffic | Safety |  |  |  | The review team feels that most of the items in this change order could have been prevented if a plans-in-hand inspection had been made after the structural plans were available. | A plans-in-hand inspection should have been made after the structural plans were available.
1996-12-10 | Maintenance of Traffic | Safety |  |  |  | Temporary crash cushion Type VI was recommended to protect the end of the temporary concrete median barrier wall being used for traffic control. | Upon the completion of the rest of the roadway , this cushion was to be removed.
1996-12-10 | Pavement | Striping |  |  |  | A more durable pavement striping was requested instead of painted pavement striping. | 6 thermoplastic striping was used instead of painted pavement striping.
1996-12-10 | Pavement | Design |  |  |  | To provide a smoother transition on the ramp tie-in areas with 1-65 , District Four recommended using 11 non-reinforced PCC pavement instead of bituminous pavement. PCC pavement was recommended because it better matches the existing and new pavements. | Based on District Four's recommendation , 11 non-reinforced PCC pavement was substituted for bituminous pavement.
1996-12-10 | Drainage | Headwalls | PAVEMENT REHAB-INT(P) | 99 | BARREN | Unanticipated wet conditions were encountered for the rock subgrade to clay interface. | Four additional sections of perforated pipe and four additional perforated pipe headwalls were installed in order to provide the necessary drainage.
1996-12-10 | Pavement | Design | PAVEMENT REHAB-INT(P) | 99 | BARREN | The contractor requested that the Department apply the requirements of the most current gradation charts and deduction tables for crushed stone base on the project. | The most current gradation charts and deduction tables were applied to this project.
1996-12-10 | Drainage | Ponding | PAVEMENT REHAB-INT(P) | 99 | BARREN | Water was ponding near a curb and gutter section of roadway used to divert traffic during construction. | The decision was made to install a bituminous wedge next to the curb to minimize the above risks. Before the final surface course was installed , the wedge had to be removed by milling and texturing.
1996-12-10 | Design | Alignments | PAVEMENT REHAB-INT(P) | 99 | BARREN | An entrance approach did not align with the property owners existing entrance and fence gate. | At the property owners request the entrance was relocated.
1996-12-10 | Drainage | Ponding | PAVEMENT REHAB-INT(P) | 99 | BARREN | A culvert pipe needed to be installed to prevent pounded water from overtopping a temporary connector. | A change order was approved for culvert pipe installation.
1996-12-10 | Environmental | Stream Mitigation | PAVEMENT REHAB-INT(P) | 99 | BARREN | Environmental issues were encountered with the proposed extension of an existing box culvert and channel change. | The need for a large channel change was eliminated by doweling into the existing box culvert instead of removing concrete masonry and splicing to the existing reinforcement.
1996-12-10 | Geotechnical | Sinkhole | PAVEMENT REHAB-INT(P) | 99 | BARREN | Additional sinkholes were found during construction. | The sinkholes were filled and capped in accordance with the requirements for the treatment of open sinkholes.
1996-12-10 | Design | Entrance | PAVEMENT REHAB-INT(P) | 99 | BARREN | An entrance was added by permit on this project. | The property owner furnished the required twenty-eight linear feet of fifteen inch entrance pipe and the contractor installed the pipe for the property owner at no expense. The property owner issued a check for the additional embankment material.
1996-12-10 | Environmental | Underground Tank | PAVEMENT REHAB-INT(P) | 99 | BARREN | The original bid for removal of underground storage tanks included the contaminated soil around it; however , at the time of construction , the soil was determined to be uncontaminated. | The uncontaminated soil was used as embankment-in-place thus providing savings to the Department.
1996-12-10 | Design | Slopes | PAVEMENT REHAB-INT(P) | 99 | BARREN | A disabled property owner felt very uncomfortable mowing the proposed 3:1 slope with his riding mower. | Work to flatten the slope was approved on a cost plus basis.
1996-12-10 | Pavement | Type | PAVEMENT REHAB-INT(P) | 99 | BARREN | The Job Mix Formula asphalt content differed from the target asphalt content. | This change order provided for adjustment in the unit bid price for bituminous concrete materials when the J.M.F. asphalt content differed from the target asphalt content.
1996-12-10 | Design | Entrance | PAVEMENT REHAB-INT(P) | 99 | BARREN | The radius of the proposed commercial entrance did not allow proper turning movements for vehicles with heavy equipment trailers. | The radius was increased to 50 feet.
1996-12-10 | Design | Omission | PAVEMENT REHAB-INT(P) | 99 | BARREN | Two existing entrances were not shown on the plans. | This change order included the work necessary to install entrance pipes for the two existing locations.
1996-12-10 | Drainage | Pipe Sizing | PAVEMENT REHAB-INT(P) | 99 | BARREN | The original design routed flow from two sources , an eighteen inch culvert and a fifteen inch culvert , into a single fifteen inch entrance pipe. | An additional entrance pipe was added.
1996-12-10 | Utilities | Existing Utilities | PAVEMENT REHAB-INT(P) | 99 | BARREN | The contractor encountered two gas service lines that were not shown on the plans. | The lines had to be relocated because of the lowered ditch grade.
1996-12-10 | Design | Omission | PAVEMENT REHAB-INT(P) | 99 | BARREN | An existing field entrance was omitted from the roadway plans. | An entrance approach was constructed in the same location as the existing one.
1996-12-10 | Design | Granular Embankment | PAVEMENT REHAB-INT(P) | 99 | BARREN | The amount of embankment material necessary to construct an entrance was omitted from the quantities. | The contractor requested to install the fill material on a cost plus basis.
1996-12-10 | Drainage | Elevation | PAVEMENT REHAB-INT(P) | 99 | BARREN | The outlet elevation of a cross-drain was too high to properly drain. | A portion of the parking lot on the right-of-way of the approach road was lowered in order to allow proper drainage.
1996-12-10 | Drainage | Existing Pipe | PAVEMENT REHAB-INT(P) | 99 | BARREN | Entrances were designed to leave the existing entrance pipes in place. However , elevation checks indicated that the pipes were approximately six inches high and must be replaced to allow for proper roadway ditch drainage. | A change order was approved for entrance pipe replacement.
1996-12-06 | Design | Entrance |  |  |  | The Commissioner of Highways granted approval to add an entrance for a property owner. | This was not a CAP.
1996-12-06 | Geotechnical | Subsurface |  |  |  | A sandy cut slope required stabilization with crushed aggregate. | Include bid Item for a small quantity of crushed aggregate.
1996-12-06 | Maintenance of Traffic | Timing |  |  |  | Lapse time between contracts combined with the projectÖs erodible material and steep slopes would cause the finished grade on entrances to deteriorate before surfacing. | Four-inch stone was used to hold entrances in place.
1996-12-06 | Structures | Omission |  |  |  | Settlement Platforms were not included in the bridge design plans. | At end of Geotech Report ô add £Bid Items Affected¥.
1996-12-06 | Structures | Omission |  |  |  | An island header curb for bridge end drainage was omitted. | Constructability Review. Clarification of items needs to be addressed where roadway and bridges meet ô whose item is it?
1996-12-04 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The plans showed using a Type A bridge connector for the guardrail that connects with the bridge in the Eastbound lane at the end of the project. However , this bridge had the old type barrier wall with curbs and the connectors would not work with this | A Type C bridge connector was used instead.
1996-12-04 | Design | Guardrail | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The plans showed using a Type A bridge connector for the guardrail that connects with the bridge in the Eastbound lane at the end of the project. However , this bridge had the old type barrier wall with curbs and the connectors would not work with this | A Type C bridge connector was used instead.
1996-12-04 | Structures | Quantities | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | The bridge decks were set up for hydrodemolition. In the process of cleaning the decks , more deteriorated concrete was encountered than anticipated. | Additional latex overlay was needed to bring the decks back up to original grade.
1996-12-04 | Structures | Masonry Coating | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | This project involved structural overlays and bridge rehabs on four bridges of the Wendell Ford Parkway. Despite the fact that these bridges are an extremely visible part of the parkway system that are exposed to heavy applications of salt spray during t | It was determined that Masonry Coating would be more beneficial.
1996-12-04 | Structures | Rehab | PAVEMENT REHAB-PRK(P) | 99 | HOPKINS | Existing concrete pavement was overlayed with 7.5 inches of asphalt material. There were two steel girder bridges with concrete decks over KY 112 that had to be raised to match the elevation of the pavement overlay. The bridges originally had fixed supp | It was decided to build metal stands to hold the girders that were to be encased in concrete at Abutment 1. The expansion rockers from this abutment were used to replace the worst ones on Pier 2 and Abutment 2. The bolts that held the existing plates th
1996-12-03 | Drainage | Pipe Sizing |  |  |  | New pipe was placed according to plans , but when a heavy rain event occurred the pipe could not carry the water. | An additional pipe was placed adjacent to the other new pipe. Review drainage design to size culvert openings.
1996-12-03 | Geotechnical | Subsurface |  |  |  | Soft areas were spotted during construction phase. The Geotechnical Report had suggested some of the areas but not all were covered. Weighing upfront cost (geotech) vs. back end cost (construction). | The consensus from the group was that so long as Bid Items are set up for stabilization , i.e. , Stabilized Aggregate Base and Fabric-Geotextile Type III.
1996-12-03 | Erosion Control Plan | Slope Protection |  |  |  | Several areas with 2:1 slopes or less had unsuitable soils to hold seed and erosion occurred on the banks. | Erosion control blankets were used along with other methods to establish some type of growth. Serecia Lespedizia , invasive grasses were used in various areas. Other ideas: either a note to make this pay item incidental to the project or a provision on
1996-12-03 | Design | Quantities |  |  |  | Quantities were not considered for crossovers and turning lanes. | Review quantities during final calculations for Bid Items. Have a checklist of items to consider.
1996-11-21 | Geotechnical | Unsuitable Material |  |  |  | There were areas that were undercut due to unstable material and additional items were needed to refill them. | Additional quantities of Granular Embankment were established.
1996-11-21 | Maintenance of Traffic | Quantities |  |  |  | The reconstruction of KY 92 was performed under traffic but there were insufficient plans quantities to allow ongoing maintenance of the existing approach roads and mainline traffic. | Additional quantities of traffic bound base were added via change order.
1996-11-21 | Construction | Revisions |  |  |  | Construction Revision #1 added an auxiliary lane from Station 645+00 to Station 682+66.99 which required widening the proposed fill slope by five feet at the location of two manholes RT Station 667+33.8 and Station 668+68. The manholes were part of the p | The two Type C Manhole lids were modified to match the revised fill slope.
1996-11-21 | Utilities | Omission |  |  |  | The existing sanitary sewer line in the entrance RT Station 643+00 was inadvertently omitted from the original contract. | Additional funds had to be set up to relocate the existing sanitary sewer line.
1996-11-21 | Construction | Revisions |  |  |  | The decision was made to add an additional lane from the Interstate to the Water Park. | Funding for this revision , which was basically just asphalt costs , was approved through change order.
1996-11-21 | Utilities | Conflicting Information |  |  |  | Changes were necessary due to site conditions differing from the plans and conflicts with utilities. | These modifications included the addition of header curb where necessary and minor rerouting of storm sewer and public utilities due to plan omissions or conflicting locations.
1996-11-21 | Maintenance of Traffic | Striping |  |  |  | The decision was made to use temporary pavement striping paint in lieu of temporary removable tape due to the number and length of diversion tapers and temperature limitations associated with using removable tape. | It was necessary to procure funding to remove the temporary pavement striping used on temporary traffic diversions.
1996-11-21 | Design | Omission |  |  |  | Proposed disturb limits involved removing the existing standard curb and gutter in business parking lots LT and RT Stations 670+00 to 682+66.99 , but the original contract did not specify replacing said curb. | It was requested to encumber funding to place standard header curb near cut/fill slopes adjacent to existing business parking.
1996-11-21 | Maintenance of Traffic | Entrances |  |  |  | There were insufficient quantities of traffic bound base to maintain entrances on the project. | Additional traffic bound base was added.
1996-11-21 | Construction | Contracts |  |  |  | An existing retaining wall that had no footing , collapsed due to construction of a proposed roadway ditch along the base of the wall. The existing wall was on a proposed construction easement. | It was requested to establish contract items to place approximately 150 feet of non-reinforced gravity wall LT Station 680+60 to Station 682+50. The property owners were contacted and gave consent for construction of a new gravity retaining wall. The av
1996-11-21 | Construction | Coordination |  |  |  | The Contractor and the Department agreed to delay the placement of final surfacing and pavement markings until anticipated hauling to an adjacent highway project was completed in order to reduce exposure of the new surface to excessive wear. | The Department gave the Contractor written notice to start final surfacing. No work days were charged from April 1 , 2007 to fourteen days after the written notice. It was requested to establish a contract item for additional Maintain and Control Traff
1996-11-21 | Maintenance of Traffic | Phasing |  |  |  | The proposed template reduced the rate of super-elevation by approximately 4% less than existing KY 92 from Station 665+00 to Station 680+00. To do so required asphalt pavement depths of up to 24 inches on the low side of the super-elevated curve in orde | It was requested to encumber funds for additional temporary pavement striping. This addition was required due to revisions to the traffic control plan needed for the construction of proposed roadway template from Station 645+00 to Station 682+66.99. The
1996-11-21 | Design | Drainage |  |  |  | Excessive water was bleeding through the newly placed asphalt base from Station 668+00 to Station 670+30 , creating an unsafe condition. | It was requested to establish contract items to place an asphalt fin drain along the RT edge of existing pavement Station 668+00 to Station 670+30 +/-. The drain now empties into a Type I Perforated Pipe Headwall LT Station 670+30.
1996-11-21 | Utilities | Existing Utilities |  |  |  | The proposed storm sewer line LT Station 670+00 to Station 675+50 was to be placed adjacent to an existing 10' water main. Conflicting alignments and grades between the proposed storm sewer and water main prevented construction as specified in the origin | The proposed storm sewer was modified by shifting the main storm sewer line approximately 10' toward centerline. This shift required the modification of the proposed TY 11 DBI's and the addition of three junction boxes.
1996-11-21 | Drainage | Coordination |  |  |  | Existing drop box inlets did not match the proposed curb and gutter at various locations. | It was requested to encumber funding to modify existing drop box inlets LT Station 680+00 and RT Station 678+35 to match the proposed curb and gutter at each location.
1996-11-21 | Construction | Revisions |  |  |  | The decision was made to construct an additional right turn lane , that was not included in the original design plans , from LT Station 643+46.86 to LT Station 682+66.99. | Additional funding was procured to widen the proposed KY 92 to include an additional right turn lane. A Construction Revision included the revised typical section , cross-sections , drainage , and quantity modifications.
1996-11-19 | Design | Guardrail | CONGESTION MITIGTN(O) | 7 | FAYETTE | There were problems with an end treatment set up in the plans. | The Type 7 end treatment was replaced with Type 4A end treatment through Change Order.
1996-11-19 | Construction | ROW | SAFETY | 7 | FAYETTE | The project called for construction of a new box culver that was supposed to tie into an existing dry laid stone channel that ran under a building. The plans showed the culver top butting up to the brick veneer of the building , but when the existing cu | The Contractor braced the remaining brick and removed loose materials , along with a broken window to prevent any danger to the workers. The Contractor replaced the brick and window at completion of work on culvert.
1996-11-19 | Utilities | Inaccurate Location | CONGESTION MITIGTN(O) | 7 | FAYETTE | The water line for the City of Ferguson was at a different location than shown on the plans and was exposed during the relocation of Murphy Avenue. | A Change Order was established to relocate the water feed to the City of Ferguson.
1996-11-19 | Utilities | Delays | CONGESTION MITIGTN(O) | 7 | FAYETTE | The Prime Contractor experienced delay costs due to the shut down of project until overhead utilities were located. | An agreed upon lump sum payment was made to the Prime Contractor for their delay costs. The Contractor was also reimbursed for escalation costs for petroleum , geotextiles , blasting materials , etc. An adjustment for steel products was also approved
1996-11-19 | Design | Guardrail | SAFETY | 7 | FAYETTE | There were problems with an end treatment set up in the plans. | The Type 7 end treatment was replaced with Type 4A end treatment through Change Order.
1996-11-19 | Design | Guardrail | SAFETY | 7 | FAYETTE | There were problems with an end treatment set up in the plans. | The Type 7 end treatment was replaced with Type 4A end treatment through Change Order.
1996-11-19 | Design | Guardrail | CONGESTION MITIGTN(O) | 7 | FAYETTE | There were problems with an end treatment set up in the plans. | The Type 7 end treatment was replaced with Type 4A end treatment through Change Order.
1996-11-19 | Construction | ROW | CONGESTION MITIGTN(O) | 7 | FAYETTE | The project called for construction of a new box culver that was supposed to tie into an existing dry laid stone channel that ran under a building. The plans showed the culver top butting up to the brick veneer of the building , but when the existing cu | The Contractor braced the remaining brick and removed loose materials , along with a broken window to prevent any danger to the workers. The Contractor replaced the brick and window at completion of work on culvert.
1996-11-19 | Utilities | Delays | SAFETY | 7 | FAYETTE | The Prime Contractor experienced delay costs due to the shut down of project until overhead utilities were located. | An agreed upon lump sum payment was made to the Prime Contractor for their delay costs. The Contractor was also reimbursed for escalation costs for petroleum , geotextiles , blasting materials , etc. An adjustment for steel products was also approved
1996-11-19 | Utilities | Stacked Utilities | CONGESTION MITIGTN(O) | 7 | FAYETTE | A water line right of Station 72+60 on South Richardson Drive conflicted with the installation of a 15-inch storm sewer. The water line was not part of the utilities to be relocated on the project. | The water line had to be lowered for the installation of 15-inch storm sewer.
1996-11-19 | Maintenance of Traffic | Changes | CONGESTION MITIGTN(O) | 7 | FAYETTE | There were concerns about traffic interruptions on Dearl Whitaker Lane while paving over the existing pavement and necessary drainage revisions were being made. | Drainage revisions were needed to change the grade on Dearl Whitaker Lane in order to minimize traffic interruptions. An existing curb box inlet was changed to a modified box using Type 13 grates bolted into box. Also , the grade of the curb had to be
1996-11-19 | Utilities | Inaccurate Location | SAFETY | 7 | FAYETTE | A gravity sanitary sewer line that was not at elevation shown on plans interfered with installation of storm sewer pipe. | The storm sewer pipe was adjusted to avoid the gravity sanitary sewer line by changing the curb box inlet and junction box.
1996-11-19 | Utilities | Inaccurate Location | SAFETY | 7 | FAYETTE | The water line for the City of Ferguson was at a different location than shown on the plans and was exposed during the relocation of Murphy Avenue. | A Change Order was established to relocate the water feed to the City of Ferguson.
1996-11-19 | Utilities | Stacked Utilities | SAFETY | 7 | FAYETTE | A water line right of Station 72+60 on South Richardson Drive conflicted with the installation of a 15-inch storm sewer. The water line was not part of the utilities to be relocated on the project. | The water line had to be lowered for the installation of 15-inch storm sewer.
1996-11-19 | Utilities | Delays | CONGESTION MITIGTN(O) | 7 | FAYETTE | Additional cost involving the mechanically stabilized earth (MSE) retaining wall were incurred due to utility relocation delays. The project was let to bid with overhead utilities anticipated to be clear by the end of August 2004. The utilities , howev | An agreed upon lump sum amount compensated the subcontractor for direct delay costs associated with MSE wall based on contractorÖs/manufacturerÖs documented material escalation costs for the original wall quantity and also for escalation and engineering c
1996-11-19 | Utilities | Delays | SAFETY | 7 | FAYETTE | Additional cost involving the mechanically stabilized earth (MSE) retaining wall were incurred due to utility relocation delays. The project was let to bid with overhead utilities anticipated to be clear by the end of August 2004. The utilities , howev | An agreed upon lump sum amount compensated the subcontractor for direct delay costs associated with MSE wall based on contractorÖs/manufacturerÖs documented material escalation costs for the original wall quantity and also for escalation and engineering c
1996-11-19 | Utilities | Inaccurate Location | CONGESTION MITIGTN(O) | 7 | FAYETTE | A gravity sanitary sewer line that was not at elevation shown on plans interfered with installation of storm sewer pipe. | The storm sewer pipe was adjusted to avoid the gravity sanitary sewer line by changing the curb box inlet and junction box.
1996-11-19 | Maintenance of Traffic | Changes | SAFETY | 7 | FAYETTE | There were concerns about traffic interruptions on Dearl Whitaker Lane while paving over the existing pavement and necessary drainage revisions were being made. | Drainage revisions were needed to change the grade on Dearl Whitaker Lane in order to minimize traffic interruptions. An existing curb box inlet was changed to a modified box using Type 13 grates bolted into box. Also , the grade of the curb had to be
1996-11-19 | Utilities | New Utilities | SAFETY | 7 | FAYETTE | The project called for a curb box inlet and storm sewer at the intersection of Griffin and Eckstein Street. However , Eckstein Street already had underground utility lines with concrete kickers on water lines in the area where storm sewer was to be inst | The grade of pavement and curb through area was adjusted to drain water across the street where the existing gutter line would carry water to curb box inlet , thus eliminating the need for the new storm sewer.
1996-11-19 | Utilities | New Utilities | CONGESTION MITIGTN(O) | 7 | FAYETTE | The project called for a curb box inlet and storm sewer at the intersection of Griffin and Eckstein Street. However , Eckstein Street already had underground utility lines with concrete kickers on water lines in the area where storm sewer was to be inst | The grade of pavement and curb through area was adjusted to drain water across the street where the existing gutter line would carry water to curb box inlet , thus eliminating the need for the new storm sewer.
1996-11-19 | Utilities | Delays | SAFETY | 7 | FAYETTE | The Bridge Subcontractor experienced delay costs due to shut down of project until overhead utilities had been relocated. | Payment of the Bridge SubcontractorÖs delay costs were paid by an agreed upon lump sum for this item.
1996-11-19 | Utilities | Delays | CONGESTION MITIGTN(O) | 7 | FAYETTE | The Bridge Subcontractor experienced delay costs due to shut down of project until overhead utilities had been relocated. | Payment of the Bridge SubcontractorÖs delay costs were paid by an agreed upon lump sum for this item.
1996-11-19 | Utilities | Relocation | SAFETY | 7 | FAYETTE | The existing clay sewer line along Main Street and Bourne Avenue was located at the bottom of the Rock Refill line of the Subgrade , but the plans did not address this situation. | The existing clay sewer line was relocated and replaced with a PVC line by Change Order.
1996-11-19 | Utilities | Relocation | CONGESTION MITIGTN(O) | 7 | FAYETTE | The existing clay sewer line along Main Street and Bourne Avenue was located at the bottom of the Rock Refill line of the Subgrade , but the plans did not address this situation. | The existing clay sewer line was relocated and replaced with a PVC line by Change Order.
1996-11-19 | Maintenance of Traffic | Moving Traffic | SAFETY | 7 | FAYETTE | There were concerns about traffic during construction at the Oak Hill/Monticello Street intersection area. | Due to traffic considerations in the Oak Hill/Monticello Street intersection area , some existing pavement was left in place and milled in selective areas to match pavement grades.
1996-11-19 | Maintenance of Traffic | Moving Traffic | CONGESTION MITIGTN(O) | 7 | FAYETTE | There were concerns about traffic during construction at the Oak Hill/Monticello Street intersection area. | Due to traffic considerations in the Oak Hill/Monticello Street intersection area , some existing pavement was left in place and milled in selective areas to match pavement grades.
1996-11-19 | Design | Coordination | SAFETY | 7 | FAYETTE | The project plans showed a Guardrail barricade blocking entrance to the railroad underpass. However , the city had a cast iron water line running through the tunnel and recommended guardrail not be used because it's vibration could break the water line | The contractor used a concrete block (landscape type) retaining wall instead.
1996-11-19 | Design | Coordination | CONGESTION MITIGTN(O) | 7 | FAYETTE | The project plans showed a Guardrail barricade blocking entrance to the railroad underpass. However , the city had a cast iron water line running through the tunnel and recommended guardrail not be used because it's vibration could break the water line | The contractor used a concrete block (landscape type) retaining wall instead.
1996-11-19 | Traffic | Lighting | CONGESTION MITIGTN(O) | 7 | FAYETTE | The project called for ornamental street lights to match existing City lighting. However , the plans did not include circuit design or size wire to carry loads for lighting. The lights also needed photocell controls to automatically control the lights. | These changes were recommended by Central Office Division of Traffic and implemented via Change Order.
1996-11-19 | Traffic | Lighting | SAFETY | 7 | FAYETTE | The project called for ornamental street lights to match existing City lighting. However , the plans did not include circuit design or size wire to carry loads for lighting. The lights also needed photocell controls to automatically control the lights. | These changes were recommended by Central Office Division of Traffic and implemented via Change Order.
1996-11-19 | Structures | Handrail | SAFETY | 7 | FAYETTE | There were insufficient handrail quantities and the incorrect type were set up. | Handrail quantities needed to be increased and used to change handrail type from Type A1 to Type A.
1996-11-19 | Construction | Revisions | SAFETY | 7 | FAYETTE | The sidewalk at the corner of Freeman Avenue did not meet ADA requirements. | Two sidewalk ramps were added with pavers at the corner of Freeman Avenue for wheelchair accessibility. This work included removal of some existing concrete.
1996-11-19 | Utilities | Relocation | CONGESTION MITIGTN(O) | 7 | FAYETTE | The existing 6-inch water line from the 12-inch cast iron Main Station 500+95 to Jacksboro Street would have been located just beneath the rock refill line. | The water line was relocated to the sidewalk on the north side of South Main.
1996-11-19 | Utilities | Relocation | SAFETY | 7 | FAYETTE | The existing 6-inch water line from the 12-inch cast iron Main Station 500+95 to Jacksboro Street would have been located just beneath the rock refill line. | The water line was relocated to the sidewalk on the north side of South Main.
1996-11-19 | Geotechnical | Subsurface | SAFETY | 7 | FAYETTE | When the footer for Abutment #2 was excavated there were several mud seams and a hole where an existing sewer manhole was located. | These areas were cleaned out and filled with mass concrete. The price for this item was calculated in accordance with the specifications (Section 601.05) at twice the delivered cost of the concrete.
1996-11-19 | Structures | Handrail | CONGESTION MITIGTN(O) | 7 | FAYETTE | There were insufficient handrail quantities and the incorrect type were set up. | Handrail quantities needed to be increased and used to change handrail type from Type A1 to Type A.
1996-11-19 | Construction | Revisions | CONGESTION MITIGTN(O) | 7 | FAYETTE | The sidewalk at the corner of Freeman Avenue did not meet ADA requirements. | Two sidewalk ramps were added with pavers at the corner of Freeman Avenue for wheelchair accessibility. This work included removal of some existing concrete.
1996-11-19 | Geotechnical | Subsurface | CONGESTION MITIGTN(O) | 7 | FAYETTE | When the footer for Abutment #2 was excavated there were several mud seams and a hole where an existing sewer manhole was located. | These areas were cleaned out and filled with mass concrete. The price for this item was calculated in accordance with the specifications (Section 601.05) at twice the delivered cost of the concrete.
1996-11-19 | Utilities | Omission | CONGESTION MITIGTN(O) | 7 | FAYETTE | Additional items were needed to reconnect water services throughout the project. | A copper service line was added to reconnect water services.
1996-11-19 | Utilities | Omission | SAFETY | 7 | FAYETTE | Additional items were needed to reconnect water services throughout the project. | A copper service line was added to reconnect water services.
1996-11-15 | Design | Entrance |  |  |  | Additional work was needed in order to tie an existing sidewalk into the new driveway and to the grade of the front yard of Parcel #61. | A rock wall had to be modified in order to tie the existing sidewalk into the new driveway and grade of the front yard.
1996-11-15 | Maintenance of Traffic | Quantities |  |  |  | An insufficient quantity of traffic bound base was set up in the original contract. | Additional quantities were added via Change Order.
1996-11-15 | Drainage | Ditches |  |  |  | There was desire to eliminate an unsightly ditch and make maintenance more manageable in the front yards of several residences. | Drainage structures had to be installed beginning at Sta 153+50 and tied into the existing underground drainage at Sta 156+20.
1996-11-15 | Utilities | Relocation |  |  |  | The location of ten water meters conflicted with Detour #2. | The water meters had to be relocated due to the location of Detour #2.
1996-11-15 | Drainage | Headwalls |  |  |  | A headwall which was previously installed on this contract conflicted with the proposed wingwall on the northwest corner of the box beam bridge on existing Hopeful Road. | To alleviate the conflict , the headwall was removed and the 54 inch pipe was extended through the new wingwall of the bridge , which also was extended.
1996-11-15 | Environmental | Wells |  |  |  | There was a gas well under the roadway fill that was still active. This item was shown on the plans but was not addressed. | An item of Supplemental Agreement was needed to plug the well and the work was performed as a lump sum.
1996-11-15 | Pavement | Repair |  |  |  | Additional items were needed due to the replacement of failed pavement sections. | Additional quantities of Bituminous Concrete Base Class I had to be set up.
1996-11-15 | Drainage | Culvert |  |  |  | The inlet headwall of a 72x48 box culvert at Sta 165+15 Rt of Centerline presented a drop off hazard. Also , the same culvert on the outlet end would not allow a gravel drive to be constructed over the same grade bench under the new PCI bridge at Sta 16 | The inlet headwall the 72x48 box culvert was converted into a Drop Box with a Type 3 grate , the new and existing storm pipes were tied into the box , and re-grading was performed in order to eliminate the drop off hazard. The same culvert was also ext
1996-11-15 | Traffic | Lighting |  |  |  | A quantity of interconnect wire was not used because the existing interconnect wire was recently installed and was in good condition. | The unused portions of wire were purchased by the Department and delivered to the Boone Co. Traffic Barn.
1996-11-15 | Pavement | Approaches |  |  |  | Additional items were needed at all locations where the new PCC pavement tied into the existing pavement. There were no items set up originally. | Hook bolts and expansion anchors were added for these locations.
1996-11-15 | Right-of-Way | Omission |  |  |  | Additional items were needed to upgrade Hopeful Road to fulfill an agreement with the City of Florence before the city would take over maintenance of the road. | A Change Order was established to upgrade Hopeful Road.
1996-11-15 | Construction | Revisions |  |  |  | It was desired that an additional lane on KY 18 westbound be added to allow traffic to be channeled into two turning lanes into Mall Road , two through lanes , and a single lane drop into K-Mart. | A Change Order added the additional quantities needed for this work.
1996-11-15 | Design | Omission |  |  |  | An item for Controlled Density Backfill was omitted from the original plans. | A new item was established for Controlled Density Backfill due to it being omitted from the original plans.
1996-11-15 | Maintenance of Traffic | Omission |  |  |  | Detour number 3 had to be built over an existing ditch. | The ditch material had to be excavated and backfilled with suitable material before the detour pavement could be applied.
1996-11-15 | Pavement | Design |  |  |  | There was a high volume of traffic and stopping and turning actions at the intersection of US 42 and Hopeful Road as well as the intersection of KY 18 and Hopeful Road. | District Construction Personnel decided to use PMAC in the Bituminous Concrete Surface because of its rut resistance properties.
1996-11-15 | Pavement | Design |  |  |  | There were failures in the section of pavement constructed according to plan and already carrying traffic from Sta 150+00 to Sta 160+00. | It was decided based upon recommendations from Central Office Pavement Design and Geotechnical Sections that the pavement design should be modified. The new pavement consisted of the following items: Geotextile fabric Type III on the soil , 6 inches of
1996-11-15 | Environmental | Stream Mitigation |  |  |  | A natural spring was encountered at Sta 235+35. | District Office Personnel recommended installation of a spring box to drain the area so that the water did not saturate the fill. A 15 inch culvert pipe was also used to connect the spring box to a 60 inch headwall right of Sta 236+65.
1996-11-15 | Pavement | Repair |  |  |  | There was a section of pavement that rutted severely from Rt Sta 150+00 to Sta 159+00 of Hopeful Road. | Additional quantities of Bituminous Concrete Base Class Cl w/PMAC were set up. It was decided by District Construction Personnel to mill out the two thin lifts of material (1.5 of Binder and 2.25 Base) and replace it with one thick 4 inch lift of base wi
1996-11-15 | Structures | Omission |  |  |  | There were no provisions made pertaining to the removal of an existing bridge at Sta 10+65 existing Hopeful Road. | Provisions for this work were added through Change Order.
1996-11-15 | Utilities | Relocation |  |  |  | An electrical service conflicted with the proposed slope grade from Sta 202+25 to Sta 203+25. | The electrical service had to be relocated.
1996-11-15 | Utilities | Relocation |  |  |  | A 12 inch force main conflicted with the location of a proposed bridge footing. | The main had to be relocated by Change Order.
1996-11-15 | Maintenance of Traffic | Striping |  |  |  | There was a shifting of traffic throughout the project. Striping was needed for four separate detours and in areas of milling. | Additional striping had to be performed through Change Order.
1996-11-15 | Design | Quantities |  |  |  | An insufficient quantity of concrete was set up in the contract. | Additional quantities of concrete were added.
1996-11-15 | Maintenance of Traffic | Entrances |  |  |  | It was necessary to maintain passable drives for the residences throughout the various construction phases and wet seasons. | The quantity of Traffic Bound Base and Geotextile Fabric Type III had to be increased.
1996-11-15 | Erosion Control Plan | Quantities |  |  |  | Additional erosion control was needed. | Additional erosion control was added at a cost of $2.00 per lineal foot.
1996-11-15 | Structures | Reinforcement Steel |  |  |  | There were concerns about the proposed epoxy steel reinforcement spacing. | The epoxy steel reinforcement spacing was increased on both the top and bottom mats as directed by Central Office Construction.
1996-11-15 | Utilities | Quantities |  |  |  | There was an insufficient quantity of gate valves set up in the contract. | The quantity of gate valves was increased via Change Order.
1996-11-15 | Utilities | Relocation |  |  |  | The locations of several water meters interfered with the construction of Detour #2. | These water meters needed to be relocated for Detour #2 construction.
1996-11-15 | Utilities | Communication |  |  |  | The Florence Sewer Commission was informed about the proposed roadway construction yet made no effort to respond about a possible relocation of an existing sewer line. Once construction began , the Florence Sewer Commission informed the department that | The pavement typical section had to be modified to avoid a 20 inch sanitary sewer force main in the area.
1996-11-15 | Maintenance of Traffic | Signage |  |  |  | Due to the confined work areas , the Contractor requested permission to use Big Foot vertical panel channelizers in addition to the channelization devices permitted by the standard drawings. These devices would be used in areas where vertical panels as | Permission to use these items was given. These devices provided additional lane width and in the event of disturbance by traffic , they are less likely to become an obstacle in the driving lane. Since this was an option proposed by the Contractor , th
1996-11-15 | Utilities | Quantities |  |  |  | There were insufficient quantities for fire hydrant installation set up in the contract. | Quantities for fire hydrant installation were increased as directed by the District Utility Department.
1996-11-15 | Pavement | Quantities |  |  |  | Areas of bituminous concrete pavement , PCC Base , and Concrete Entrance Pavement all exceeded original quantities. | Additional quantities of DGA Base had to be set up because it was used as a base for the items previously mentioned.
1996-11-15 | Utilities | Relocation |  |  |  | A water line conflicted with the construction of an abutment footing. | The water line was relocated by Change Order.
1996-11-15 | Geotechnical | Unsuitable Material |  |  |  | There were soft and yielding areas encountered throughout the project. | An increase in roadway excavation was necessary.
1996-11-15 | Erosion Control Plan | Silt Checks |  |  |  | Additional items were needed throughout the project for erosion control. | Additional silt checks were established.
1996-11-15 | Pavement | Quantities |  |  |  | There were insufficient plan quantities of PCC Base - 9 inch and Cement Concrete Entrance Pavement - 8 inch. | Additional quantities had to be set up due to the insufficient plan quantities.
1996-11-15 | Environmental | Pollution |  |  |  | There were a large number of old tires discovered after the excavation of two ponds on the project. | An item of Supplemental Agreement was needed to properly dispose of them and a lump sum price was established.
1996-11-15 | Environmental | Underground Tank |  |  |  | A septic tank was discovered on Parcel 96 and it was not properly taken care of with the original demolition contract. | A Supplemental Agreement was needed and lump sum compensation was established via Change Order.
1996-11-15 | Right-of-Way | CAP |  |  |  | Much of the leech field on Parcel No. 81 was destroyed by construction excavation. | A sanitary sewer line had to be extended in order to tie Parcel No. 81 into the sewer system since. This was also made as a right-of-way agreement.
1996-10-29 | Maintenance of Traffic | Striping | BRIDGE REPLACEMENT(P) | 10 | PERRY | While realigning the driving lanes for Phase 1 , the existing lines were removed by grinding. At night , the areas of the existing deck that had been grinded appeared to be skip lines , which caused considerable confusion to motorists. | Contrary to plans , which called for paint to be used for temporary pavement marking , Removable Lane tape was utilized for all phases. This caused an overrun in quantities for Removable Lane Tape.
1996-10-29 | Maintenance of Traffic | Safety | BRIDGE REPLACEMENT(P) | 10 | PERRY | The Contractor had safety concerns about using plastic drums or barricades. The Contractor was worried that if struck , these devices would roll into traffic or become airborne and that they might move under normal wind conditions caused by high speed t | The Contractor requested using the BIGFOOT vertical panel barricade in lieu of plastic drums or barricades. The advantages of this device are the ability to separate from the base and lie flat when struck and a reduction in movement under normal wind con
1996-10-29 | Structures | Reinforcement Steel | BRIDGE REPLACEMENT(P) | 10 | PERRY | Approximately 304 linear feet of existing median barrier was removed north of Bent 13 to accommodate MOT. The existing wall had a cast in place glare screen , which the plans did not account for when they specified the Concrete Median Barrier Type 12D. | It was agreed to replace the glare screen on the relocated Median Barrier , but the standards indicated a minimum embedment of 5.75 inches for reinforcing bars. When the Contractor began drilling these holes , he repeatedly drilled through the deck at
1996-10-29 | Construction | Safety | BRIDGE REPLACEMENT(P) | 10 | PERRY | Upon review of Northbound I-65 through the work zone , it was apparent that the excessive speed of traffic was contributing to the accident rate. Standard Reduced Speed Ahead and Speed Limit 40 MPH signs were ineffective. | To reduce the excessive speed of traffic , it was agreed to utilize off duty police officers and their vehicles to enforce the posted speed limit. The accident rate , injury rate , and traffic speed decreased significantly compared to conditions prior
1996-10-29 | Traffic | Omission | BRIDGE REPLACEMENT(P) | 10 | PERRY | No type of pavement marker was specified on plans. | There should have been some type of pavement markers specified on the job.
1996-10-29 | Structures | Expansion Joints | BRIDGE REPLACEMENT(P) | 10 | PERRY | If grinding is going to occur , but the slab being placed is not thick enough , it can cause issues at the finger dams. | It was suggested that a thicker slab be placed if grinding is needed. This will help at the finger dam locations.
1996-10-29 | Construction | Specifications | BRIDGE REPLACEMENT(P) | 10 | PERRY | Prohibition of concrete placement during winter months by specifications would have halted progression of the project. | Contrary to Section 609.05 of the specification manual , concrete placement was allowed during January and February. It was agreed that all requirements of Section 601.17 Part C would be strictly followed. Concrete slab temperatures were monitored by i
1996-10-29 | Structures | Expansion Joints | BRIDGE REPLACEMENT(P) | 10 | PERRY | The bearing devices for the finger dams at L23 and L23' were either badly worn or missing. The finger dams had dropped approximately 3/4 - 1 inch. | A jacking plan was developed and implemented to resolve the issue and resulted in a Change Order.
1996-10-29 | Structures | Expansion Joints | BRIDGE REPLACEMENT(P) | 10 | PERRY | The contract plans and approved shop drawings for the finger joint extensions did not indicate that the driving surface of the dams should have anti-skid studs. | Since the existing finger dams had the studs , it was agreed to add the anti-skid studs to the finger dam extension.
1996-10-29 | Construction | Revisions | BRIDGE REPLACEMENT(P) | 10 | PERRY | Division of Operations requested a weather monitoring station to be installed on this project to provide information related to dispatching crews to apply de-icing chemicals on this section of I-65. | A weather monitoring station was installed on project as requested and required a Change Order.
1996-10-29 | Construction | Method/Innovation | BRIDGE REPLACEMENT(P) | 10 | PERRY | Due to the configuration of the steel reinforcement in the barrier wall on the bridge , the slip form method was considered an alternative method of installation. | The Contractor was given the option to slip form and placed a 200 foot test section prior to completing the wall to ensure conformance with appropriate specifications. This method resulted in a credit of $6.58 per linear foot to the department.
1996-10-29 | Structures | Expansion Joints | BRIDGE REPLACEMENT(P) | 10 | PERRY | A one part silicon formulation was inadequate to properly seal the expansion joints , considering the large amount of dynamic movement and expansion/contraction on the bridge. | A two part system such as Dow Corning 902 or an approved equivalent was chosen as the preferred solution. The one part seals were removed and replaced.
1996-10-29 | Traffic | Lighting | BRIDGE REPLACEMENT(P) | 10 | PERRY | After work began on the installation of the new lighting control equipment and the new 2400 volt feed , it was discovered that existing equipment essential to the proper functioning of the lighting at the Kennedy Bridge and approach was severely deterior | After consultation with the District Office and Division of Traffic , it was determined the deficient items would be replaced.
1996-10-29 | Maintenance of Traffic | Phasing | BRIDGE REPLACEMENT(P) | 10 | PERRY | The Contractor proposed a modification of the Traffic Phasing that allowed Ramp WN to remain open during Revised Phase 1. | This modification was reviewed by the Task Force and approved as part of Traffic Revision No. 1. It was agreed to pay the incentive for 13 of the 15 Calendar Days established. It was agreed that the two Calendar Days remaining represent the inconvenienc
1996-10-29 | Construction | Ride Quality | BRIDGE REPLACEMENT(P) | 10 | PERRY | There were concerns about rideability on the bridge. | It was suggested that in the future , plans should specify rideability on long bridges.
1996-10-29 | Construction | Revisions | BRIDGE REPLACEMENT(P) | 10 | PERRY | The bridge abutment wall in the gore area of SB I-65 and I-64 was protected by an array of sand filled crash barrels , which were struck regularly. Once hit , there was little protection remaining in this area and the barrels were difficult to maintain | It was agreed to install a React 350 Attenuator specifically designed for the gore area.
1996-10-29 | Maintenance of Traffic | Communication | BRIDGE REPLACEMENT(P) | 10 | PERRY | After work began it was discovered that one Highway Advisory Radio (HAR) was inadequate to properly advise the traveling public of construction activity. The stated range of a mobile unit , the speed of traffic , and possible message length did not giv | In discussions with the Indiana DOT , it was decided to use two HAR's (one for each State involved). Each HAR was installed at sites completely controlled by the respective Departments to allow for the long term security of the units and to ensure suffi
1996-10-29 | Design | Communication | BRIDGE REPLACEMENT(P) | 10 | PERRY | There were concerns that construction personnel were not informed about the status of the project. | Construction personnel should be given opportunities to review plans and proposals prior to letting.
1996-10-29 | Structures | Quantities | BRIDGE REPLACEMENT(P) | 10 | PERRY | On the Kentucky approach , the plans indicated an existing overlay thickness of 1.75 inches; however , the actual thickness was 2.25 inches. Latex quantities for the approach included 15% for partial depth , but the actual quantities approached 34%. | Considering field conditions , it was apparent that the plan quantity for Concrete Overlay - Latex was insufficient. The overrun formula was used to calculate a new unit price. Plan quantity was adjusted via change order.
1995-12-05 | Geotechnical | Slides | RELOCATION(O) | 10 | MORGAN | Estimated quantities for geotechnical fabric used to repair slide damage were insufficient. | A change order was approved to increase the quantity of geotechnical fabric.
1995-12-05 | Materials | Asphalt Mixtures | RELOCATION(O) | 10 | MORGAN | An adjustment needed to be made for the asphalt cement content. | A change order was approved for the asphalt cement content adjustment.
1995-12-05 | Drainage | Omission | RELOCATION(O) | 10 | MORGAN | An entrance pipe for a cemetery entrance was omitted from the plans. | A change order for the entrance pipe was approved.
1995-12-05 | Utilities | Gas Well | RELOCATION(O) | 10 | MORGAN | Two wells were discovered in a disturbed area which had to be plugged. | A change order was approved for plugging the wells.
1995-12-05 | Geotechnical | Soils | RELOCATION(O) | 10 | MORGAN | Areas along the mainline had to be undercut to remove silty runoff deposits from strip mining. | A change order was approved to remove silty runoff deposits
1995-12-05 | Design | Evaluations | RELOCATION(O) | 10 | MORGAN | Additional excavation was required due to an incorrect ground elevation in the plans. | A change order was approved for the additional excavation.
1995-12-05 | Environmental | Landscaping | RELOCATION(O) | 10 | MORGAN | The unavailability of plants shown in the plans necessitated the use of alternate plants. | A change order was approved for the alternate plants.
1995-12-05 | Geotechnical | Slides | RELOCATION(O) | 10 | MORGAN | The pavement on both ends of the corrected section had to be milled and redone due to damages suffered during the correction and rebuilding of the embankment at the failed section. This change order could be contributed to the slide correction. | A change order was approved for the pavement repair.
1995-12-05 | Drainage | Diversion Drainage | RELOCATION(O) | 10 | MORGAN | More channel lining was deemed necessary because of highly erodible embankment material. | A change order was approved for additional channel lining.
1995-12-05 | Pavement | Striping | RELOCATION(O) | 10 | MORGAN | Temporary Pavement Striping was omitted from the plans. | The contractor was compensated for Temporary Pavement Striping
1995-12-05 | Geotechnical | Slides | RELOCATION(O) | 10 | MORGAN | After the completion of the project, a major slide occurred. About 500 feet of mainline section sank approximately 6 to 8 inches. Geotechnical representatives explained that a coal seam and clay material present under the massive embankment caused this failure; an extensive sub-surface exploration might not have predicted this event. | Corrective measures for this situation were to excavate the failed material and rebuild the embankment on a drainage blanket with more extensive drainage allowances.
1995-12-05 | Geotechnical | Subsurface | RELOCATION(O) | 10 | MORGAN | Unstable material was encountered which had be to removed. | Undercutting and stabilization were performed.
1995-12-05 | Geotechnical | Subsurface | RELOCATION(O) | 10 | MORGAN | Construction personnel recommended adding guardrail to protect a drop-off area which had been cleared during construction and utility relocation. | A change order was approved for the guardrail.
1995-12-05 | Drainage | Channel Change | RELOCATION(O) | 10 | MORGAN | A channel change had overhanging rocks which needed to be removed to prevent filling the new channel. | A change order was approved to remove overhanging rocks.
1995-12-05 | Geotechnical | Slides | RELOCATION(O) | 10 | MORGAN | Several "pop" slides were found at various locations. | Several "pop" slides were found at various locations.