## Slide 1
SUE
Finding
Buried
Treasure

## Slide 2: SUE-Subsurface Utility Engineering
Level D
Level C
Level B
Level A

## Slide 3: Statewide Survey Contract
Patrick Perry
  502-782-4925
  patrick.perry@ky.gov
QK4
Palmer
GRW

## Slide 4: SUE Request
Project Number
County
What Level needed and Where(Provide Plan Sheet)
Word or Excel Sheet
Coordinate Control Sheet
Deliverables
  Reasonable date for completion (typically month)
  DGN in current KYTC CADD Standard

## Slide 5: SUE Request
Quality Level A 5-159.00 |  |  |  |  |  |  | Quality Level B 5-159.00 |  |  |  | 
 | Station | Offset | RT / LT | Facility Type | Surface Type |  |  | Start Station | End Station | Offset | Facility
1 | 588+08 | 102 | Lt | 24" Gas Main | Earth/grass |  | 1 | 575+00 +/- | 601+00 +/- | edge of WB lane to R/W (~158.74ft LT) | AT&T buried cable
2 | 590+96 | 106 | Lt | 12" DIW Water Main - possibly in 24" Casing pipe | Earth/grass |  |  |  |  |  | 
3 | 600+52 | 110 | Lt | 12" DIW Water Main - possibly in 24" Casing pipe | Earth/grass |  |  |  |  |  | 
4 | 604+81 | 110 | Lt | 36" Sanitary Sewer | Earth/grass |  |  |  |  |  | 
5 | 606+46 | 110 | Lt | 36" Sanitary Sewer | Earth/grass |  |  |  |  |  | 
6 | 629+91 | 97 | Lt | 24" Sanitary Sewer | Earth |  |  |  |  |  | 
7 | 648+00 | 85 | LT | UG electric in 3 1/2" conduit | Earth |  |  |  |  |  | 
8 | 139+20 | 25 | Rt | 8" DI Water Main - possibly in 12" Casing | Earth/Rip Rap |  |  |  |  |  | 
9 | 139+64 | 19 | Rt | 8" Gas Main | Earth/Rip Rap |  |  |  |  |  | 
10 | TBD | 109 | Lt | AT&T UG cable | Earth/grass |  |  |  |  |  | 
11 | TBD | 93 | Lt | AT&T UG cable | Earth |  |  |  |  |  | 

## Slide 7: SUE Request

## Slide 10: SUE Deliverables
Point | Utility & Size | Station | Offset | Project Northing | Project Easting | Ground Elevation | Depth | Top of Util. Elev. | Surface | Comment
LWC |  |  |  |  |  |  |  |  |  | 
1087 | Level "B" | 590+72.31 | 74.64' LT | 266915.98 | 1239806.68 | 515.46 |  |  | Grass | Level "B"
1088 | 12" Steel | 590+73.13 | 104.47' LT | 266942.44 | 1239792.88 | 513.86 | -4.50 | 509.36 | Grass | TH #2
1084 | Level "B" | 590+73.56 | 134.22' LT | 266968.63 | 1239778.77 | 514.00 |  |  | Grass | Level "B"
 | See comment | 600+52 | 110' LT |  |  |  |  |  |  | TH #3: No signal, could not locate
 | See comment | 139+20 | 25' RT |  |  |  |  |  |  | TH #8: No signal, could not locate
MSD |  |  |  |  |  |  |  |  |  | 
1010 |  | 603+27.72 | 105.77' LT | 267554.43 | 1240888.08 | 517.92 |  | 507.89 | Grass | Sanitary MH
1014 | 36" Sanitary | 604+88.01 | 106.14' LT | 267632.79 | 1241027.91 | 518.43 | -10.23 | 508.20 | Grass | TH #4: Calculated from MH pipe
1013 | 36" Sanitary | 606+48.81 | 107.88' LT | 267712.60 | 1241167.51 | 518.41 | -9.89 | 508.52 | Grass | TH #5: Calculated from MH pipe
1012 |  | 607+98.76 | 111.05' LT | 267788.38 | 1241296.95 | 519.32 |  | 508.81 | Grass | Sanitary MH
1078 |  | 627+23.28 | 331.31' LT | 269010.09 | 1242782.26 | 515.99 |  | 504.59 | Grass | Sanitary MH
1080 | 24" Sanitary | 629+90.55 | 97.06' LT | 268964.62 | 1243134.73 | 516.11 | -9.75 | 506.36 | Grass | TH #6: Calculated from MH pipe
1079 |  | 632+56.50 | 136.17' RT | 268919.27 | 1243485.55 | 518.45 |  | 508.13 | Grass | Sanitary MH
Electric |  |  |  |  |  |  |  |  |  | 
1097 | Level "B" | 647+75.37 | 95.33' LT | 269958.22 | 1244617.42 | 524.33 |  |  | Grass | Level "B"
1098 | 2" Iron | 647+93.96 | 95.01' LT | 269968.32 | 1244633.02 | 524.48 | -1.41 | 523.07 | Grass | TH #7: between hwy lamps
1099 | Level "B" | 648+22.36 | 94.84' LT | 269983.83 | 1244656.39 | 524.43 |  |  | Grass | Level "B"
AT&T |  |  |  |  |  |  |  |  |  | 
1232 | Level "B" | 602+76.56 | 128.2' LT | 267549.11 | 1240832.48 | 519.76 |  |  | Grass | Level "B"
1230 | Concrete Cap | 602+80.26 | 109.06' LT | 267534.19 | 1240845.02 | 517.08 | -4.73 | 512.35 | Grass | TH #10: Probe to resistance
1229 | Concrete Cap | 602+82.53 | 101.27' LT | 267528.49 | 1240850.80 | 515.93 | -3.71 | 512.22 | Grass | TH @ Flow Line
1227 | See comment | 602+82.81 | 94.95' LT | 267523.10 | 1240854.12 | 517.63 |  |  | Grass | TH #11: Sensor reading 6.5' to utility
1225 | Level "B" | 602+84.49 | 80.93' LT | 267511.68 | 1240862.41 | 520.13 |  |  | Grass | Level "B"

## Slide 11: SUE Deliverables
Point | Utility & Size | Station | Offset | Project Northing | Project Easting | Ground Elevation | Depth | Top of Util. Elev. | Surface | Comment
LWC |  |  |  |  |  |  |  |  |  | 
1087 | Level "B" | 590+72.31 | 74.64' LT | 266915.98 | 1239806.68 | 515.46 |  |  | Grass | Level "B"
1088 | 12" Steel | 590+73.13 | 104.47' LT | 266942.44 | 1239792.88 | 513.86 | -4.50 | 509.36 | Grass | TH #2
1084 | Level "B" | 590+73.56 | 134.22' LT | 266968.63 | 1239778.77 | 514.00 |  |  | Grass | Level "B"
 | See comment | 600+52 | 110' LT |  |  |  |  |  |  | TH #3: No signal, could not locate
 | See comment | 139+20 | 25' RT |  |  |  |  |  |  | TH #8: No signal, could not locate
MSD |  |  |  |  |  |  |  |  |  | 
1010 |  | 603+27.72 | 105.77' LT | 267554.43 | 1240888.08 | 517.92 |  | 507.89 | Grass | Sanitary MH
1014 | 36" Sanitary | 604+88.01 | 106.14' LT | 267632.79 | 1241027.91 | 518.43 | -10.23 | 508.20 | Grass | TH #4: Calculated from MH pipe
1013 | 36" Sanitary | 606+48.81 | 107.88' LT | 267712.60 | 1241167.51 | 518.41 | -9.89 | 508.52 | Grass | TH #5: Calculated from MH pipe
1012 |  | 607+98.76 | 111.05' LT | 267788.38 | 1241296.95 | 519.32 |  | 508.81 | Grass | Sanitary MH
1078 |  | 627+23.28 | 331.31' LT | 269010.09 | 1242782.26 | 515.99 |  | 504.59 | Grass | Sanitary MH
1080 | 24" Sanitary | 629+90.55 | 97.06' LT | 268964.62 | 1243134.73 | 516.11 | -9.75 | 506.36 | Grass | TH #6: Calculated from MH pipe
1079 |  | 632+56.50 | 136.17' RT | 268919.27 | 1243485.55 | 518.45 |  | 508.13 | Grass | Sanitary MH
Electric |  |  |  |  |  |  |  |  |  | 
1097 | Level "B" | 647+75.37 | 95.33' LT | 269958.22 | 1244617.42 | 524.33 |  |  | Grass | Level "B"
1098 | 2" Iron | 647+93.96 | 95.01' LT | 269968.32 | 1244633.02 | 524.48 | -1.41 | 523.07 | Grass | TH #7: between hwy lamps
1099 | Level "B" | 648+22.36 | 94.84' LT | 269983.83 | 1244656.39 | 524.43 |  |  | Grass | Level "B"
AT&T |  |  |  |  |  |  |  |  |  | 
1232 | Level "B" | 602+76.56 | 128.2' LT | 267549.11 | 1240832.48 | 519.76 |  |  | Grass | Level "B"
1230 | Concrete Cap | 602+80.26 | 109.06' LT | 267534.19 | 1240845.02 | 517.08 | -4.73 | 512.35 | Grass | TH #10: Probe to resistance
1229 | Concrete Cap | 602+82.53 | 101.27' LT | 267528.49 | 1240850.80 | 515.93 | -3.71 | 512.22 | Grass | TH @ Flow Line
1227 | See comment | 602+82.81 | 94.95' LT | 267523.10 | 1240854.12 | 517.63 |  |  | Grass | TH #11: Sensor reading 6.5' to utility
1225 | Level "B" | 602+84.49 | 80.93' LT | 267511.68 | 1240862.41 | 520.13 |  |  | Grass | Level "B"

## Slide 12: Finding the Booty
Maps are a Pirate’s Best Friend (Besides his Hook)
  Utility Contacts – As-Builts
  GIS Information
  Line & Grade – Potential Conflict Areas to dig (Cuts, Ditches, Proposed Pipes, Critical Utility Systems)
  Google Earth / Street View / Open Source Maps
Evidence in the Field
  Valves / Meters / Signs / Markers / Manholes / Pedestals / Drop Poles
  Trench Warfare
  BUD Markings
  Exposed Pipes

## Slide 14: Know What’s Below
BUD 811 Utility Locates
  811 Call Center / Web Ticket Entry Dig, Design or Damaged
  Utility Locators
  Consolidated Locating Services (USIC)
  Private Locating Consultants
Electromagnetic Induction Tracing
What about GPR?
When in Doubt – Witch it Out
If I were a pirate…where would I hide my Booty…

## Slide 15: Imaging the Ground

## Slide 17: Digging for Gold (Knuckle Deep)
ASCE 38-02 Non-Mechanical Means
  Utility Probe
  Shovel
  Posthole Diggers
Vacuum Excavation
  Air Vac Systems
  Wet Vac Systems
The Mother of all Gold Diggers

## Slide 18: Dig – Rig’s
Air Vac
Wet Vac
Mega Vac

## Slide 19: Frustrations that make a Pirate want to…
Rocks for Backfill
No Tracer Wires
Hard Clay Soils
PVC Force Mains
Jefferson County USIC
Frozen Ground / Frozen Booty